Night Sky Radiant Cooling System Saves Energy

in a Commercial Building

This night-sky radiant cooling system enables downsizing of conventional cooling equipment and reduces annual energy costs by cooling water in a radiative and evaporative fashion. Water is sprayed over a flat or low-slope roof surface at night, filtered, stored, and delivered the following day for cooling. The system is comprised of a roof-spray assembly, a thermal-storage component, and a microprocessor control unit. The process is most applicable to arid climates where hot days are followed by cool nights with minimum temperatures below 18°C. The product was tested in a Los Angeles, California state government office building. Operationally, system storage water is sprayed over the low-slope single-ply membrane roof, which is divided by a north-south ridge. The spray water, typically chilled to 5-10°C below the minimum night air temperature, from the east and west roof sections is collected at roof drains, filtered, and delivered to separate thermal storage locations. Water from the east roof section is stored in an underground tank north of the building. This tank water is delivered on thermostat demand to custom cooling coils added at rooftop HVAC units, serving a large open plan section of the building. The water chilled on the west roof slope is also filtered, and then circulated through underfloor plastic tubing to store cooling in the concrete slab floors of rooms located along the west and south walls. This passive radiant cooling from the floors provides first-stage cooling for these areas, with second-stage cooling provided by twelve small rooftop HVAC units. Annual cooling-energy consumption was reduced by more than 50%.

Technical Data

The system installed includes a copper and brass roof-spray assembly composed of piping, pumps, sand filters, and spray heads, an underground fibreglass storage tank (56.9 m3), plastic under-floor tubing (approx. 2,700 m), and four chilled-water coils. Typical capacities are 3.4 MJ/m2 of roof surface in peak conditions. For buildings with peak loads exceeding this amount, WhiteCap™ allows for significant downsizing of conventional cooling equipment.

Energy Data

Conventional cooling-energy consumption was over 70% lower with WhiteCap™ operation in September than without WhiteCap™ in July. Adjusting for WhiteCap™ pump energy use and climate changes, net annual cooling-energy savings are over 50% (over 74.4 GJ saved annually).

Economic Data

Simple payback period is less than 2.5 years. The cost of the WhiteCap™ system totalled USD 10,100, with annual savings of USD 4,400.

Contacts:

| 5401 Associates, L.P. K Brunk 2901 Ocean Park Boulevard, Suite 117 Santa Monica, CA 310-396-4161 310-396-8910 (Fax) | Roof Science Corporation M. Best 123 C Street Davis, CA 95616 916-753-4844 916-753-4125 (Fax) |
| --- | --- |
| Davis Energy Group D. Springer 123 C Street Davis, CA 95616 916-753-1100 916-753-4125 (Fax) |  |

See also: 	“Nightsky” System Cools Roof Tops

NightSky natural cooling system saves energy

WhiteCap™ Roof Spray Cooling

# Text boxes

The Crenshaw Boulevard Employment Development Department office in Los Angeles,California.