## Savings Estimate_New
DOE Priority Rulemaking: EPACT Update to Fluorescent Lamps
| Baseline: | Business as usual, standards in place do not change
| Scenario 1: | Fluorescent lamp standard raised to FEMP recommended level (hold lumen output constant and use higher efficacious lamp)
| Scenario 2: | Fluorescent lamp standard raised to FEMP Best Available (hold lumen output constant and use higher efficacious lamp)
[9 empty] | Baseline | Scenario 1 | Scenario 2
| Sector | Phase 1 Energy Use (TWh/yr) | Baseline Efficacy (average, lowest first-cost lamp) | Baseline lumen service (lowest first-cost lamp) | Baseline System Wattage per Lamp | Scenario 1: FEMP Recommended, Normalized Watts | Scenario 2: FEMP Best Available, Normalized Watts | Scenario 3: T12 Electronic to T8 Electronic | Annual Quads PEC | Annual Quads PEC | Annual Quads PEC
4-Foot Linear (T8) | Com / Ind | 43.7181 | 80.9 | 2710 | 29.8 | 30.3 | 28.6 |  | 0.48046 | 0.48046 | 0.46111
4-Foot Linear (T12) | Com / Ind | 97.5497 | 57 | 2312.5 | 35.7 | 32.8 | 31.7 |  | 1.0721 | 0.98497 | 0.95194
U-tube lamps (T8 and T12) | Com / Ind | 6.5302 | 61.7 | 2283.75 | 35.7 | 31.6 | 29 |  | 0.071766 | 0.063524 | 0.058297
8-Foot Linear (T8) | Com / Ind | 0.16954 | 89 | 5250 | 56.9412 | 50.7 | 48 |  | 0.0018632 | 0.001659 | 0.0015706
8-Foot Linear (T12) | Com / Ind | 17.3165 | 68.5 | 4905 | 63.05 | 60 | 54.8 |  | 0.19031 | 0.1811 | 0.1654
Total |  | 141.2678 | [6 empty] | 1.8165 | 1.7117 | 1.6383
[9 empty] | Savings over Baseline in one year (Quads PEC) | 0.10474 | 0.17813
[9 empty] | Savings over Baseline in one year (percent) | 5.766% | 9.806%
365.25 | Days per year | [7 empty] | Cumulative savings over Baseline 2008-2030 for Fluorescent (Quads PEC) | 1.2569 | 2.1375
20 | Assumed lifespan of a fixture, regardless of light technology (years)
3.22 | 1998 Site to Source conversion to Quads PEC (BTS Core Databook, 2000)
292.997 | Units conversion, Terawatt-hrs per Quad
Note on D7: ADL: Lowest first cost lamp efficacy. Costing from www.bulbs.com Efficacy from manufacturer catalogues, 2001.
Note on E7: Lumen Output: Lumen output of the lowest first-cost fluorescent tubes is held constant to determine energy savings potential. Source: Manufacturer Catalogues, 2001. Www.bulbs.com, 2001.
Note on J17: Note: This assumes no changed in installed base, a 20 year fixture lifespan and no change in site to source PEC ratio.
Note on A11: ADL: Because the ADL inventory only accounts for T8 and T12 greater than 4 feet, an assumption is made that 50% of lamps greater than 4 feet are 8 foot lamps and are thus are subject to EPACT regulation.
Note on A12: ADL: Because the ADL inventory only accounts for T8 and T12 greater than 4 feet, an assumption is made that 50% of lamps greater than 4 feet are 8 foot lamps and are thus are subject to EPACT regulation.

## Lamps_New
T-12 Baseline (Note: these lamps were selected by choosing the lowest first cost 34W T-12 on www.bulbs.com, and identifying the equivalent models from the manufacturer catalogues.)
Brand | Watts | Size | Len. (in) | Description | Catalogue # | Model | Life (hrs) | CRI | Color Temp (K) | Initial Lumens | Mean Lumens | Ratio I/M | Initial Efficacy | Mean Efficacy | Price
General Electric | 34 | T-12 | 48 | Warm White, rapid start | 13821 | F40WW/RS/WM 30PK | 20000 | 52 | 3000 | 2700 | 2320 | 1.1638 | 79.4 | 68.2
Philips | 34 | T-12 | 48 | Warm White, rapid start | 256867 | F40WW/RS/EW ALTO | 20000 | 53 | 3000 | 2700 | 2350 | 1.1489 | 79.4 | 69.1 | $1.92 ea. for 30
Osram Sylvania | 34 | T-12 | 48 | Warm White, rapid start | 24595 | F40/WW/SS | 20000+ |  |  | 2750 |  |  | 80.9
General Electric | 34 | T-12 | 48 | Cool White, rapid start | 13803 | F40CW/RS/WM | 20000 | 60 | 4100 | 2650 | 2280 | 1.1623 | 77.9 | 67.1
Philips | 34 | T-12 | 48 | Cool White, rapid start | 244707 | F40/CW/RS/EW ALTO | 20000 | 62 | 4100 | 2650 | 2300 | 1.1522 | 77.9 | 67.6 | $1.56 ea. for 30
Osram Sylvania | 34 | T-12 | 48 | Cool White, rapid start | 24594 | F40CW/SS/ECO | 20000+ |  |  | 2700 |  |  | 79.4
Best Available Technology
Brand | Watts | Size | Len. (in) | Description | Catalogue # | Model | Life (hrs) | CRI | Color Temp (K) | Initial Lumens | Mean Lumens |  | Initial Efficacy | Mean Efficacy | Price
General Electric | 34 | T-12 | 48 | Rapid Start Lamp | 14627 | F40SPX30/RS/WM | 20000 | 82 | 3000 | 2900 | 2610 | 1.1111 | 85.3 | 76.8
Philips | 34 | T-12 | 48 | Ultralume, RS Fluorescent | 237818 | F40/30U/RS/EW/ALTO | 20000 | 85 | 3000 | 2900 | 2600 | 1.1154 | 85.3 | 76.5
Osram Sylvania | 34 | T-12 | 48 | Supersaver RS Lamps | 24589 | F40/D830/SS | 20000+ |  | 3000 | 2900 |  |  | 85.3
General Electric | 34 | T-12 | 48 | ECOLUX lamps - TCLP compliant | 23159 | F40SPX30/RS/WM/ECO | 20000 | 82 | 4100 | 2900 | 2610 | 1.1111 | 85.3 | 76.8
Philips | 34 | T-12 | 48 | Ultralume, RS Fluorescent | 237842 | F40/41U/RS/EW/ALTO | 20000 | 85 | 4100 | 2900 | 2600 | 1.1154 | 85.3 | 76.5
Osram Sylvania | 34 | T-12 | 48 | Supersaver RS Lamps | 24586 | F40/D841/SS | 20000+ |  | 4100 | 2900 |  |  | 85.3
Wattages if lumens held constant |  |  |  |  | BF | System Watts | lumens | lm/W
General Electric | 31.653 |  |  |  | 0.88 | 35.7 | 2312.5 | 57.0028 | Baseline - lowest first cost (Manufacturer Catalogues, 2001)
Philips | 31.653 | [5 empty] | 2520 | 62.1176 | FEMP recommended (Dec 2000), 2800 Initial Lumens
Osram Sylvania | 32.2392 | [5 empty] | 2605 | 64.2129 | FEMP Best Available (Dec 2000), 2900 Initial Lumens
General Electric | 31.0668 | [5 empty] | 2605 | 64.2129 | Catalogue Best Available (Manufacturer Catalogues, 2001)
Philips | 31.0668
Osram Sylvania | 31.653 |  | Average: | 31.6 | Watts
T-8 Baseline
Brand | Watts | Size | Len. (in) | Description | Catalogue # | Model | Life (hrs) | CRI | Color Temp (K) | Initial Lumens | Mean Lumens |  | Initial Efficacy | Mean Efficacy | Price
General Electric | 32 | T-8 | 48 | Med. bi-pin, rapid start | 15949 | F32T8/SP41 | 20000 | 78 | 4100 | 2850 | 2710 |  | 89.1 | 84.7
Philips | 32 | T-8 | 48 | Med. bi-pin, rapid start | 272484 | F32T8/TL741/ALTO | 20000 | 78 | 4100 | 2850 | 2710 |  | 89.1 | 84.7 | $2.34 ea. for 25
Osram Sylvania | 32 | T-8 | 48 | Med. bi-pin, rapid start | 21824 | FO32/741 | 20000 | 75 | 4100 | 2800 |  |  | 87.5
General Electric | 32 | T-8 | 48 | Med. bi-pin, rapid start | 15947 | F32T8/SP35 | 20000 | 78 | 3500 | 2850 | 2710 |  | 89.1 | 84.7
Philips | 32 | T-8 | 48 | Med. bi-pin, rapid start | 272492 | F32T8/TL735/ALTO | 20000 | 78 | 3500 | 2850 | 2710 |  | 89.1 | 84.7 | $2.34 ea. for 25
Osram Sylvania | 32 | T-8 | 48 | Med. bi-pin, rapid start | 21823 | FO32/735 | 20000 | 75 | 3500 | 2800 |  |  | 87.5
Best Available Technology
Brand | Watts | Size | Len. (in) | Description | Catalogue # | Model | Life (hrs) | CRI | Color Temp (K) | Initial Lumens | Mean Lumens |  | Initial Efficacy | Mean Efficacy | Price
General Electric | 32 | T-8 | 48 | StarCoat T8 Lamps | 22655 | F32T8/SPX30 | 20000 | 86 | 3000 | 2950 | 2800 |  | 92.2 | 87.5
Philips | 32 | T-8 | 48 | Advantage RS Ultimate Performance | 270652 | F32T8/ADV835/ALTO | 24000 | 86 | 3500 | 3100 | 2950 |  | 96.9 | 92.2
Osram Sylvania | 32 | T-8 | 48 | Extended Performance - 800 series | 21760 | FO32/830/XP | 24000 | 85 | 3000 | 3000 | 2820 |  | 93.8 | 88.1
General Electric | 32 | T-8 | 48 | EcoLux Lamps - TCLP Compliant | 25613 | F32T8/SPX30/ECO | 20000 | 86 | 4100 | 2950 | 2800 |  | 92.2 | 87.5
Philips | 32 | T-8 | 48 | Advantage RS Ultimate Performance | 270660 | F32T8/ADV841/ALTO | 24000 | 86 | 4100 | 3100 | 2950 |  | 96.9 | 92.2
Osram Sylvania | 32 | T-8 | 48 | Extended Performance - 800 series | 21762 | FO32/841/XP | 24000 | 85 | 4100 | 3000 | 2820 |  | 93.8 | 88.1
Wattages if lumens held constant |  |  |  |  | BF | System Watts | lumens | lm/W
General Electric | 30.9111 |  |  |  | 0.89 | 29.8 | 2710 | 80.9362 | Baseline - lowest first cost (Manufacturer Catalogues, 2001)
Philips | 29.4118 | [5 empty] | 2662.4561 | 79.5163 | FEMP recommended (Dec 2000), 2800 Initial Lumens
Osram Sylvania | 29.8507 | [5 empty] | 2820 | 84.2215 | FEMP Best Available (Dec 2000), 3000 Initial Lumens
General Electric | 30.9111 | [5 empty] | 2856.6667 | 85.3166 | Catalogue Best Available (Manufacturer Catalogues, 2001)
Philips | 29.4118
Osram Sylvania | 29.8507 |  | Average: | 30.1 | Watts
U-type Baseline
Brand | Watts | Size | Len. (in) | Description | Catalogue # | Model | Life (hrs) | CRI | Color Temp (K) | Initial Lumens | Mean Lumens |  | Initial Efficacy | Mean Efficacy | Price
General Electric | 32 | T-8 | 22.4375 | RE730 Phosphor, 6" spacing between legs | 10479 | F32T8/SP30/U/6 | 20000 | 75 | 3000 | 2700 | 2565 |  | 84.4 | 80.2
Philips | 32 | T-8 | 22.4375 | Med bi-pin, rapid start, 3000K | 340737 | FB32T8/TL730/6 | 20000 | 75 | 3000 | 2650 | 2370 |  | 82.8 | 74.1 | $8.00 ea for 20
Osram Sylvania | 32 | T-8 | 22.4375 | Octron Curvalume 700 series | 21967 | FBO32/730/6 | 20000 | 75 | 3000 | 2750 |  |  | 85.9 | 0
General Electric | 35 | T-12 | 22.4375 | Warm White, Watt-Miser, 6" spacing between legs | 12207 | F40/WW/U/6/WM | 14000 | 52 | 3000 | 2350 | 2150 |  | 67.1 | 61.4
Philips | 34 | T-12 | 22.4375 | Warm White, Medium bi-pin | 378620 | FB40WW/6/EW ALTO | 18000 | 53 | 3000 | 2400 | 2050 |  | 70.6 | 60.3 | $6.50 ea for 20
Osram Sylvania | 34 | T-12 | 22.4375 | Curvalume Rapid Start Lamps | 24047 | FB40/WW/6/SS | 18000 |  |  | 2650 |  |  | 77.9 | 0
Best Available Technology
Brand | Watts | Size | Len. (in) | Description | Catalogue # | Model | Life (hrs) | CRI | Color Temp (K) | Initial Lumens | Mean Lumens |  | Initial Efficacy | Mean Efficacy | Price
General Electric | 32 | T-8 | 22.4375 | RE 830 Phosphor, 6" spacing between legs | 10483 | F32T8/SPX30/U/6 | 20000 | 84 | 3000 | 2800 | 2630 |  | 87.5 | 82.2
Philips | 32 | T-8 | 22.4375 | U-bent, rapid start lamps | 340802 | F32T8/TL830/6 | 20000 | 85 | 3000 | 2800 | 2535 |  | 87.5 | 79.2
Osram Sylvania | 32 | T-8 | 22.4375 | Octron Curvalume 800 series | 21970 | FBO32/830/6 | 20000 | 82 | 3000 | 2850 |  |  | 89.1 | 0
General Electric | 40 | T-12 | 22.4375 | RE 830 Phosphor, 6" spacing between legs | 14816 | F40SPX30/U/6 | 14000 | 82 | 3000 | 3100 | 2820 |  | 77.5 | 70.5
Philips | 34 | T-12 | 22.4375 | SPEC, 3000K | 33092-8 | F40/SPEC30/6/EW | 18000 | 70 | 3000 | 2760 | 2500 |  | 81.2 | 73.5
Osram Sylvania | 34 | T-12 | 22.4375 | Curvalume Rapid Start | 24063 | FB40/D30/6/SS | 18000 |  | 3000 | 2730 |  |  | 80.3 | 0
Wattages if lumens held constant |  |  |  |  | BF | System Watts | lumens | lm/W
General Electric | 30.8571 |  |  |  | 0.885 | 32.75 | 2283.75 | 61.7135 | Baseline - lowest first cost (Manufacturer Catalogues, 2001)
Philips | 30.2857 | [5 empty] | 2370 | 64.0443 | FEMP recommended (Dec 2000), 2650 initial lumens
Osram Sylvania | 30.8642 | [5 empty] | 2582.5 | 69.7866 | FEMP Best Available (Dec 2000), 2800 initial lumens
General Electric | 30.3226 | [5 empty] | 2621.25 | 70.8338 | Catalogue Best Available (Manufacturer Catalogues, 2001)
Philips | 29.5567
Osram Sylvania | 33.0012 |  | Average: | 30.8 | Watts
Eight foot fluorescent lamp baselines (T8 and T12)
Brand | Watts | Size | Len. (in) | Description | Catalogue # | Model | Life (hrs) | CRI | Color Temp (K) | Initial Lumens | Mean Lumens |  | Initial Efficacy | Mean Efficacy | Price
General Electric | 59 | T-8 | 96 | RE 730 Phosphor | 23407 | F96T8/SP30 | 15000 | 75 | 3000 | 5800 | 5310 |  | 98.3 | 90
Philips | 59 | T-8 | 96 | T-8 Cool White | 344531 | F96T8/TL730 | 15000 | 75 | 3000 | 5700 | 5190 |  | 96.6 | 88 | $8.16 ea for 48
Osram Sylvania | 59 | T-8 | 96 | Octron 700 series | 21854 | FO96/730 | 15000 | 75 | 3000 | 5700 |  |  | 96.6 | 0
General Electric | 60 | T-12 | 96 |  | 13729 | F96T12/CW/WM/ECO | 12000 | 60 | 4100 | 5500 | 5060 |  | 91.7 | 84.3
Philips | 60 | T-12 | 96 | T-12 Cool White | 258400 | F96T12/CW/EW ALTO | 12000 | 62 | 4100 | 5400 | 4750 |  | 90 | 79.2 | $3.64 ea for 45
Osram Sylvania | 60 | T-12 | 96 | Single Pin base | 29815 | F96T12/CW/SS/ECO | 12000 |  |  | 5300 |  |  | 88.3 | 0
Best Available Technology
Brand | Watts | Size | Len. (in) | Description | Catalogue # | Model | Life (hrs) | CRI | Color Temp (K) | Initial Lumens | Mean Lumens |  | Initial Efficacy | Mean Efficacy | Price
General Electric | 59 | T-8 | 96 | RE 830 Phosphor | 23414 | F96T8/SPX30 | 15000 | 84 | 3000 | 5950 | 5440 |  | 100.8 | 92.2
Philips | 59 | T-8 | 96 | Instant Start Fluorescent Lamps | 344572 | F96T8/TL830 | 15000 | 85 | 3000 | 5900 | 5490 |  | 100 | 93.1
Osram Sylvania | 59 | T-8 | 96 | Octron 800 Series | 21897 | FO96/830 | 15000 | 82 | 3000 | 5900 |  |  | 100 | 0
General Electric | 60 | T-12 | 96 | RE 841 Phosphor | 15340 | F96T12/SPX41/WM 15 PK | 12000 | 80 | 4100 | 6000 | 5640 |  | 100 | 94
Philips | 60 | T-12 | 96 | Ultralume | 342071 | F96T12/41U/EW | 12000 | 85 | 4100 | 5900 | 5550 |  | 98.3 | 92.5
Osram Sylvania | 60 | T-12 | 96 | Designer 800 Supersaver | 29812 | F96T12/D841/SS | 12000 |  | 4100 | 5800 |  |  | 96.7 | 0
Wattages if lumens held constant |  |  |  |  | BF | System Watts | lumens | lm/W
General Electric | 57.5397 |  |  |  | 0.85 | 56.9412 | 5250 | 88.9831 | T-8 Baseline - lowest first cost (Manufacturer Catalogues, 2001)
Philips | 57 | [5 empty] | 5190 | 87.9661 | FEMP recommended T-8 (Dec 2000), 5700 initial lumens
Osram Sylvania | 57 |  | T-8 Average: | 57.2 | Watts |  | 5488.2627 | 93.0214 | FEMP Best Available T-8 (Dec 2000), 5950 initial lumens
General Electric | 55 | [5 empty] | 5465 | 92.6271 | T-8 Best Available (Manufacturer Catalogues, 2001)
Philips | 54.9339 | [5 empty] | 4905 | 68.46 | T-12 Baseline - lowest first cost (Manufacturer Catalogues, 2001)
Osram Sylvania | 54.8087 |  | T-12 Average: | 54.9 | Watts |  | 5152 | 71.9074 | FEMP recommended T-12 (Dec 2000), 5600 initial lumens
[5 empty] | BF | System Watts | 5640 | 78.7185 | FEMP Best Available T-12 (Dec 2000), 6000 initial lumens
[5 empty] | 0.88 | 63.05 | 5595 | 78.0904 | T-12 Best Available (Manufacturer Catalogues, 2001)
Note on H21: BA: LBNL Ballast Analysis, weightee avergae watts/lamp, 4 foot fixtures, F40T2/ES with magnetic ballast.
Note on I22: BA: Philips F40SPEC35/RS/EW, 3 color temperatures
Note on H48: BA: LBNL Ballast Analysis, weightee avergae watts/lamp, 4 foot fixtures, F32T8/RE70 with electronic rapid start ballast.
Note on I49: BA: Calculated by multiplying baseline mean lumens by ratio of initial lumens of FEMP lamp / initial lumens of baseline lamp.
Note on I50: BA: From Best Available table lamps with 3000 initial lumens.
Note on H76: BA: Average of T12 and T8 values (assumes 50% each, with no basis…)
Note on G76: BA: Average of T12 and T8 values (assumes 50% each, with no basis…)
Note on I77: From lamp with 2650 initial lumens in Baseline table
Note on I78: BA: Average of 2 lamps with 2800 initial lumens in Best Available table.
Note on I105: BA: From baseline table lamp with 5700 lumens
Note on I106: BA: Average of lamps in Best Available table with 5950 or 5900 lumens, adjusting mean lumens of lamp with 5900 initial lumens by ratio of 5950/5900.
Note on I110: BA: Lamp in Best Available table with 6000 initial lumens
Note on I109: BA: Mean lumens of lamp with 5500 initial lumens, adjusted by 5600/5500
Note on H111: BA: Watts per lamp (from 2-lamp system), LBNL Ballast Standards Analysis
Note on H104: BA: Advanca Ballast Selection Guide, April 2000, 2-lamp ballast = 110 W/2 = 55 W, normalized by ratio of ballast factor to baseline ballast (this is a different normalization of wattage than that for fixture spacing; it assumes that a ballast could be built at this wattage with the same BF as the baseline ballast. We did this normalization in the LBNL ballast analysis with stakeholder input).