Natural resources conservation service
conservation practice sPECIFICATION

well
material specification

introduction

The materials covered by this specification are as referred to by Conservation Practice Standard and Conservation Practice Specification 642- Well.

Casing

Casing materials may be pipe made of steel, cooper, plastic, fiberglass, asbestos-cement, concrete, or other similar materials of equivalent strength and durability.

Steel pipe, copper, asbestos-cement pipe, reinforced plastic mortar, plastic or fiberglass pipe may be used for well casings in drilled wells.  Only steel pipe shall be used for driven wells.

Steel

Steel well casings shall equal or exceed the requirements specified in ASTM-A-589.  Steel pipe manufactured for other purposes can be used if the quality of the pipe equals or exceeds that specified in ASTM-A-589.

Used steel pipe may be used for well casing provided that it is of good quality and has a wall thickness equal to greater than Schedule 40, and greater than the thickness shown in Table 5 of the standard.

Plastic

If the water will be used for human consumption, plastic casings for transporting portable water must be approved by NSF.  Plastic casings shall be made of acrylonitrilebutadiene-styrene (ABS), polyvinyl chloride (PUC), or styrene-rubber (SR) and shall conform to the requirements specified in ASTM-F-480.  Plastic pipe manufactured for water or irrigation pipelines can be used if the quality of the pipe equal or exceeds that specified in ASTM-F-480.

Acrolonitrile-butadiene-styrene  (ABS)

ABS casing pipe material shall meet or exceed the requirements of ASTM Specification 
D-4673, cell classification 434 or 533.  ABS well casing pipe, couplings and screen plastics shall be virgin plastic produced by the original compounder without extenders.  It shall contain polymers, blends or polymers, or both in which the minimum butadiene content is 6 percent; the minimum acrylonitrile content is 15 percent, the minimum styrene or substituted styrene content, or both, is 15 percent; the maximum content of other monomers is 5 percent; and lubricants, stabilizers, and colorants.

Polyvinyl-chloride (PVC)

PVC casing pipe material shall meet or exceed the requirements of ASTM Specification D-1784, a cell classification 12454-A,-B,-C or 14222-A,-B,-C,-D.  PVC casing pipe, couplings and screen plastics shall be made of virgin plastic produced by the original compounder without extenders.  It shall contain polyvinyl chloride homopolymer, and such additives--stabilizers, lubricants, processing aids, impact improvers and colorants--as needed to provide the required processing and toughness characteristics.

Styrene-rubber (SR)

SR casing pipe material shall meet or exceed the requirements of ASTM Specification D-1892, cell classification 4434-A.  SR well casing pipe, couplings and screen plastics shall be made of virgin plastic produced by the original compounder with materials such as antioxidants and lubricants.  It may contain as much as 15 percent acrylonitrile, combined in the styrene plastics, rubbers, or both.  The rubbers shall be of polybutadiene, butadiene styrene type, or both, with a maximum stryrene content of 25 percent or nitrile type, or both. The combined styrene plastic and rubber content shall not be less than 90 percent.

Concrete

Concrete well casings shall be reinforced and shall meet or exceed the requirements of ASTM-C-76.  The minimum 28-day compressive strength shall be 4,000 lbs./in.

Fiberglass

Fiberglass casings can be used if tests indicate that:

1.	The material meet the requirements specified in ASTM-D-2996, tests for long-term cyclic pressure strength, long-term static pressure strength, and short-term rupture strength as required in ASTM-D-2996 are not needed because the pipes are to be used for well casings.

2.	The points meet the requirements specified in Section 3.8, ASTM-F-480.

3.	The modulus of elasticity is certified for use in determining maximum depth.

Reinforced Plastic MortAr

Reinforced plastic mortar casings should equal or exceed the requirements specified in ASTM-D-3517.

Table 1 - Maximum depth of installation for plastic (SDR-PR) pipe

| SDR | Material |
| --- | --- |
|  | PVC | ABS | SR |
|  | Modulus of elasticity (E) |
|  | 400,000 | 320,000 | 250,000 | 300,000 |
| 13.5 | 985 | 785 | 615 | 735 |
| 17 | 475 | 380 | 295 | 355 |
| 21 | 245 | 200 | 150 | 185 |
| 26 | 130 | 100 | 80 | 95 |
| 32.5 | 65 | 50 | 40 | 50 |

Table 2 - Dimension and maximum depth of installation for Schedules 40 and 80 PVC plastic pipe

| Nom. dia. in. | Out dia. in. | Schedule 40 | Schedule 80 |
| --- | --- | --- | --- |
|  |  | Min. wall in. | SDR | Max. depth ft. | Min. wall in. | SDR | Max. depth ft. |
| 2 | 2.375 | 0.154 | 15.4 | 650 | 0.218 | 10.9 | 1,.960 |
| 2.5 | 2.875 | 0.203 | 14.2 | 840 | 0.275 | 10.4 | 2,260 |
| 3 | 3.500 | 0.216 | 16.2 | 550 | 0.30 | 11.7 | 1,550 |
| 3.5 | 4.00 | 0.226 | 17.7 | 420 | 0.318 | 12.6 | 1,220 |
| 4 | 4.50 | 0.237 | 19.0 | 340 | 0.337 | 13.4 | 1,010 |
| 5 | 5.563 | 0.258 | 21.6 | 230 | 0.375 | 14.8 | 740 |
| 6 | 6.625 | 0.280 | 23.7 | 170 | 0.432 | 15.3 | 660 |
| 8 | 8.625 | 0.322 | 26.8 | 120 | 0.50 | 17.3 | 450 |
| 10 | 10.75 | 0.365 | 29.5 | 90 | 0.593 | 18.1 | 390 |
| 12 | 12.75 | 0.406 | 31.4 | 70 | 0.687 | 18.6 | 360 |

Note: Table is for PVC Schedule pipe made of material having a modulus of elasticity of 400,000 lb/in2.
For PVC pipe having a modulus of elasticity of 360,000, multiply the depth by a factor of 0.9.
For PVC pipe having a modulus of elasticity of 320,000, multiply the depth by a factor of 0.8.
A factor of 0.625 can be used for ABS Schedules 40 and 80 pipe having a modulus of elasticity of 250,000
lbs/in2.

Table 3 - Dimensions and depth limitations for reinforced plastic mortar well casings.

| Dia (in) | Maximum depth (ft) |
| --- | --- |
|  | 20 | 60 | 100 | 200 | 300 | 400 | 500 | 750 | 1,000 |
|  | Minimum wall thickness (in.) |
| 8 | 0.17 | 0.17 | 0.23 | 0.23 | 0.23 | 0.29 | 0.29 | 0.33 | 0.33 |
| 10 | .17 | .17 | .28 | 28 | .28 | .36 | .37 | .41 | .41 |
| 12 | .18 | .19 | .34 | .34 | .34 | .43 | .43 | .46 | .46 |
| 14 | .19 | .22 | .32 | .40 | .40 | .43 | .46 | .46 | .46 |
| 15 | .19 | .24 | .34 | .34 | .46 | .46 | .46 | .46 | .46 |
| 16 | .20 | .25 | .36 | .36 | .46 | .46 | .46 | .46 | .46 |
| 18 | .21 | .28 | .40 | 40 | 45 | .45 | .45 | .52 | .42 |
| 20 | .21 | .31 | .42 | .42 | .45 | .45 | .45 | .54 | .54 |
| 21 | .21 | .33 | .48 | .48 | .48 | .48 | .48 | .57 | .57 |
| 24 | .24 | .38 | .48 | .48 | .57 | .57 | 57 | .57 | .57 |
| 27 | .26 | .40 | .49 | .49 | .49 | .62 | .62 | .62 | .62 |
| 30 | .29 | .44 | .49 | .49 | .49 | .68 | .68 | .68 | .68 |
| 33 | .32 | .44 | .60 | .60 | .60 | .75 | .75 | .75 | .75 |
| 36 | .35 | .48 | .65 | .65 | .65 | .82 | .82 | .82 | .82 |

Table 4 - Minimum thickness of metal casings for wells

| Dia. in | Minimum wall thickness (in.) |
| --- | --- |
|  | Steel casing | lightweight galv.casing |
| 1.0 | 0.133 | -- |
| 1.5 | .145 | -- |
| 2.0 | .154 | -- |
| 2.5 | .203 | -- |
| 3.0 | .216 | -- |
| 3.5 | .226 | -- |
| 4.0 | .060 | 0.0322 |
| 4.5 | .060 | .0322 |
| 5.0 | .075 | .0382 |
| 6.0 | .105 | .0382 |
| 8.0 | .105 | .0486 |
| 10.0 | .105 | .0486 |

Lightweight galvanized casings shall be used only in areas where local experience has proved them to be satisfactory.
Diameters 1" to 3.5" are for driven or drilled wells.

Table 5 - Maximum depth of installation for steel casings (ft.)

| Wall Uncoated Thickness (in.) | Casing size (in.) |
| --- | --- |
|  | 4 | 5 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 24 |
|  | Outside diameter (in.) |
|  | 4.5 | 5.563 | 6.625 | 8.625 | 10.75 | 12.75 | 14.0 | 16.0 | 18.0 | 24.0 |
| 0.036 | 80 | 40 | 25 | - |  |  |  |  |  |  |
| 0.048 |  | 180 | 100 | 50 | 25 |  |  |  |  |  |
| 0.060 |  | 370 | 190 | 110 | 50 | 25 | -- |  |  |  |
| 0.075 |  | 720 | 380 | 220 | 100 | 50 | 30 | 20 | -- |  |
| 0.105 |  | 2030 | 1060 | 620 | 280 | 140 | 80 | 60 | 40 | -- |
| 0.135 | -- | -- | 1340 | 600 | 310 | 180 | 130 | 90 | 60 |  |
| 0.164 | -- | -- | -- | 1080 | 550 | 330 | 250 | 160 | 110 | -- |
| 0.179 | -- | -- | -- | 1410 | 720 | 430 | 320 | 210 | 150 | - |
| 0.188 | -- | -- | -- | 1650 | 840 | 500 | 370 | 250 | 170 | 70 |
| 0.219 | -- | -- | -- | -- | 1340 | 800 | 600 | 400 | 280 | 110 |
| 0.250 | -- | -- | -- | -- | -- | 1190 | 890 | 600 | 420 | 170 |
| 0.281 | -- | -- | -- | -- | -- | -- | 1280 | 850 | 590 | 250 |
| 0.312 | -- | -- | --- | -- | -- | -- | -- | 1170 | 820 | 340 |
| 0.344 | -- | -- | -- | -- | -- | -- | -- | -- | 1100 | 460 |
| 0.375 | -- | - | -- | -- | -- | -- | --- | -- | -- | 600 |
| 0.438 | - | - | -- | -- | -- | -- | -- | -- | -- | 960 |

Note: Based on the Cleindeinst Equation for Critical Collapse Pressure, using Poisson's ratio (u) of 0.30 and a modulus of elasticity (E) of 30,000,000 lbs/in2.
	D=   2E    x   2.31	
	    1-u2        SDR (SDR-1)2