Air-Cooled Chillers

In accordance with the Energy Policy Act of 2005, the Federal Acquisition Regulations Section 23, and Presidential Executive Order 13123 the vendor shall provide air-cooled chillers that meet or exceed the latest Federal Energy Management Program (FEMP) energy-efficiency purchasing specifications.  Refer to the FEMP Web site at www.eere.energy.gov/femp/procurement/ to obtain proper sizing and cost-effectiveness data, operating tips and other important information.

| Performance Recommendation for Air-Cooled Chillers – Effective11/2003 |
| --- |
| Part Load Optimized Chillers |
| Compressor Type and Capacity | Recommended IPLV (kW/ton) |
| Scroll (30 to 60 ton) | 0.86 kW/ton or less |
| Reciprocating (30 to 150 ton) | 0.90 kW/ton or less |
| Screw (70 to 200 ton) | 0.98 kW/ton or less |
| Full Load Optimized Chillers |
| Compressor Type and Capacity | Recommended Full Load |
| Scroll (30 to 60 ton) | 1.23 kW/ton or less |
| Reciprocating (30 to 150 ton) | 1.23 kW/ton or less |
| Screw (70 to 200 ton) | 1.23 kW/ton or less |