Water-Cooled Chillers

In accordance with the Energy Policy Act of 2005, the Federal Acquisition Regulations Section 23, and Presidential Executive Order 13123 the vendor shall provide water-cooled chillers that meet or exceed the latest Federal Energy Management Program (FEMP) energy-efficiency purchasing specifications. Refer to the FEMP Web site at www.eere.energy.gov/femp/procurement/ to obtain proper sizing and cost-effectiveness data, operating tips and other important information.

| Performance Recommendation for Water-Cooled Chillers – Effective 11/2003 |
| --- |
| Part Load Optimized Chillers |
| Compressor Type and Capacity | Recommended IPLV (kW/ton) |
| Centrifugal (150 to 200 ton) | 0.52 kW/ton or less |
| Centrifugal (300 to 2,000 ton) | 0.45 kW/ton or less |
| Rotary Screw (≥ 300 ton) | 0.49 kW/ton or less |
| Full Load Optimized Chillers |
| Compressor Type and Capacity | Recommended Full Load |
| Centrifugal (150 to 200 ton) | 0.59 kW/ton or less |
| Centrifugal (300 to 2,000 ton) | 0.56 kW/ton or less |
| Rotary Screw (≥ 300 ton) | 0.64 kW/ton or less |