SPILL PREVENTION, CONTROL, AND COUNTER MEASURE PLAN

NATIONAL WEATHER SERVICE

WFO/RDA

7950 Airport Road

Santa Teresa, New Mexico  88008

Original Date of Plan:			February 2005

Date of Last Plan Review:			February 2005

Date of Last Amendment			February 2005

And P.E. Certification:

Designated Person Responsible for Spill Prevention:

Michael D. Teer, Electronic Technician

Telephone: (505) 589-4088 x260

CERTIFICATION

I hereby certify that I have examined the facility, and being familiar with the provisions of Title 40 of the Code of Federal Regulations Part 112, I attest that this Spill Prevention, Control, and Countermeasure (SPCC) plan has been prepared in accordance with good engineering practices.

John Chase, P.E.

Printed Name of Professional Registered Engineer

______________________________Date:_______

Signature of Registered Professional Engineer

Registration No. _______________	State:_______

REVIEW DOCUMENTATION AND MANAGEMENT APPROVAL PAGE

REVIEW DOCUMENTATION

In accordance with Title 40 of the Code of Federal Regulations (40 CFR) Part 112.5(b), a review and evaluation of this SPCC plan will be conducted at least once every 5 years.  As a result of this review and evaluation, the National Weather Service will amend the SPCC plan within 6 months of the review to include more effective prevention and control technology if the following both apply:

.	Such technology will significantly reduce the likelihood of a spill event from the facility

.	If such technology has been field-proven at the time of review

In accordance with 40 CFR §112.1 and §112.3 any amendment to the SPCC plan shall be certified by a Professional Engineer within 6 months after a change in the facility design, construction, operation, or maintenance occurs which materially affects the facility’s potential for a discharge of oil “…in quantities that may be harmful... into or upon the navigable waters of the United States or adjoining shorelines or waters of the contiguous zone... or that may affect natural resources...”

| Review Date | Signature of Designated Person | Amended (Yes or No)? |
| --- | --- | --- |

MANAGEMENT APPROVAL

The National Weather Service is committed to the prevention of discharges of oil to navigable waters and the environment.  We maintain the highest standards for SPCC through regular review, updating and implementation of this SPCC plan for the National Weather Service Facility located at 7950 Airport Road, Santa Teresa, New Mexico, 88008.

_________________________________________

Printed Name and Title of Meteorologist In Charge

_____________________________________

Signature and Date

TABLE OF CONTENTS

PART I - GENERAL INFORMATION	1

A.	GENERAL	1

1.	Name	1

2.	Type	1

3.	Date of Initial Operation	1

4.	Location	1

5.	Name and Address of Operator	1

6.	Facility Contacts	1

B.	SITE DESCRIPTION AND OPERATIONS	2

1.	Facility Location, Layout, and Operations	2

2. 	Facility Storage	2

3. 	Drainage Pathway and Distance to Navigable Waters	3

4.	Spill History	4

5.	Spill Potential, Volumes, and Rates	4

6. 	Discussion of Facility Conformance with 40 CFR 112	4

7.  	Type of Oil and Storage Capacity	5

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES FOR SPILL PREVENTION AND CONTROL	6

A.	TANK AND SYSTEM DESIGN FOR SPILL PREVENTION	6

1.	Aboveground Storage Tanks (AST)	6

2.	Tank Refueling and Truck Unloading Operations	6

3.	Inspections and Records	7

4. 	Site Security	8

5. 	Training	8

B. 	SPILL CONTROL	8

1.	Secondary Containment Designs, Construction Material, and Volume	8

2.	Spill Kits Type and Location	9

3. 	Drain Inlet Cover	9

4.	Personal Protective Equipment (PPE)	9

PART III - SPILL COUNTERMEASURES AND REPORTING SPILL COUNTERMEASURES	10

A. 	SPILL COUNTERMEASURES	10

1.	SWIMS	10

B. 	SPILL REPORTING	10

1.	General Notification Procedures for All Spills	11

2.	Federal Notifications	11

3.	State Notifications	12

4.	Local Contacts and Notifications:	12

5. 	Cleanup Contractor Notification	12

PART IV - RECOMMENDED IMPROVEMENTS	13

A.	PHYSICAL UPGRADES	13

B.	PROCEDURAL CHANGES	13

1.	Inspections and Preventative Maintenance	14

APPENDIX

A-1	TANK ULLAGE AND FUELING LOG

A-2	FUEL UNLOADING PROCEDURE CHECKLIST

B-1	MONTHLY INSPECTION CHECKLIST

B-2	ANNUAL INSPECTION CHECKLIST

C-1	TRAINING OUTLINE

C-2	TRAINING RECORD

D-1	SPILL RESPONSE EXERCISE RECORD

D-2	SPILL REPORTING FORM

E	CROSS REFERENCE OF THE REQUIREMENTS OF TITLE 40 OF THE CODE OF FEDERAL

REGULATIONS, SECTION 112 WITH THIS PLAN

F	MATERIAL SAFETY DATA SHEET (MSDS)

G	SPILL CLEANUP KIT INFORMATION

H	PERMITS

I	PHOTOGRAPHIC LOG AND PHOTOGRAPHS

J	FIGURES

1.	MAP OF AREA

2.	SITE DRAWING

3.	WFO AST AND GENERATOR DIAGRAM

4.	RDA SPACE DIAGRAM

5.	TOPOGRAPHIC MAP & DISTANCE TO THE RIO GRANDE

ATTACHMENT 1	40 CFR 112

PART I - GENERAL INFORMATION

A.	GENERAL

This section of the Spill Prevention, Control, and Countermeasure (SPCC) plan provides general information about the facility and a description of the site and its operations.

NOTE: A complete copy of this SPCC plan shall be maintained and kept available at the El Paso Weather Forecast Office, Santa Teresa, New Mexico.

1.	Name

National Weather Service (NWS) - El Paso Weather Forecast Office, Santa Teresa, New Mexico.

2.	Type

This facility is an onshore (non-production) facility that operates as a Weather Forecast Office (WFO).  The facility has a Radar Data Acquisition (RDA) building at the NEXRAD radar system.

3.	Date of Initial Operation

The WFO relocated from El Paso, Texas, to a new facility at Santa Teresa, New Mexico, in September 1995.  The new installation included an emergency generator and associated fuel systems.  In March 1996, the RDA was installed, and it also included its own emergency generator and fuel tanks.

4.	Location

National Weather Service		Latitude:	31° 52΄ 20˝ N

Weather Forecast Office		Longitude:	106° 41΄ 52˝ W

7950 Airport Road			Elevation:	4109 ft.

Santa Teresa, New Mexico  88008

(505) 589-4088

5.	Name and Address of Operator

National Oceanic and Atmospheric Administration

National Weather Service - Southern Region Headquarters

819 Taylor Street

Room 10A06

Fort Worth, Texas  76102

(817) 978-2367

6.	Facility Contacts

Name				Title		Telephone Number

Main Number/WFO				(505) 589-4088 (24-hours)

William Alexander		MIC		(915) 309-8903 (off hours)

Michael Teer			ET		(505) 522-5111 (off hours)

B.	SITE DESCRIPTION AND OPERATIONS

This section describes the site and its operations.

1.	Facility Location, Layout, and Operations

The facility is located in Santa Teresa, New Mexico, adjacent to, and south of, the Santa Teresa International Airport.  The property is owned by NOAA.  The facility is on a privately maintained drive at 7950 Airport Road, approximately 1.2 miles west of the intersection of Airport Road and Artcraft Road.  Figure 1 is a map the local Santa Teresa area.  Figure 2 (a site drawing from prior to the installation of the RDA) shows the facility layout.

The facility has two separate emergency generators with associated above-ground diesel fuel storage tanks (AST).  One 175 kW generator, which supplies emergency power to the WFO, has a 1,000 gal. AST plus a 72 gal. day tank (calculated from outside measurements).  There is also an 80 kW generator that supplies emergency power to the RDA and has two ASTs, each having a capacity of 229.8 gallons.  Both generators utilize #2 diesel fuel.

The estimated fuel usage is approximately 60 gallons per month.  This estimate is based on extrapolation from recent fuel orders.  The generators are tested once per week for 60 minutes.  The generators are also activated in advance of potential power outages during severe weather conditions.  Obviously, fuel consumption would increase based on the duration of any power outages.

The WFO AST is not enclosed in fenced area; however, the facility is staffed 24-hours a day, 365 days a year and there are security cameras strategically placed around the facility.  All buildings are kept locked.  The RDA and associated buildings are in a fenced compound which is also kept locked.  The exterior of the entire facility is lighted at night.

2. 	Facility Storage

The generator for the WFO is located just to the northeast of the WFO in a brick building which is approximately 225 square feet (ft²).  Its associated above-ground storage tank (AST), which has a capacity of 1,000 gallons, is located adjacent and to the north of the structure.  The AST is mounted on a concrete pad, is rectangular, and is of double-walled, steel construction (Joaquin Manufacturing).  Figure 3 is a schematic of the WFO emergency generator and fuel tank.  The AST’s fill port is located on the top of the tank and is situated in an overfill well below the grade of the top of the tank.  The well has a capacity of approximately 7-8 gal.  Piping from the AST leads into the generator building and into the day tank.  The day tank has a capacity of 72 gallons (calculated) and feeds directly to the Marathon/Caterpillar generator.  The day tank, located directly below the generator sits in a steel, open-topped spill pan which provides secondary containment.  The spill pan holds approximately 192 gal. (calculated).  The tank is connected to the generator via 37 ft. of 1in. (outside diameter) black steel pipe.  All of the joints are threaded.  The piping is single-walled; however, the pipe outside the building that leads from the AST to the building is sheathed in a PVC pipe.  Flexible hosing connects the steel pipe from the floor of the space to the engine as a safeguard against rupture from vibration when the generator is running.

The AST has a high level audible alarm at the tank.  The AST also has an audible alarm in the event of interstitial leakage (secondary containment) around the tank.

The generator and fuel tanks for the RDA are located in a pre-fabricated building (manufactured by Fibrebond) to the north of the WFO (See Figure 4).  The Kohler/John Deere generator is located in the center of the 130 ft² building.  The twin 229.8 gal. diesel tanks (manufactured by IFH Group Inc.) are rectangular in shape and mounted next to the north wall of the building.  They are constructed of steel and are single-walled.  The fueling port is located outside the north wall of the building.  The building is designed to be the secondary containment for this system.  The watertight containment measures 9 in. from the floor to the door sill.  The secondary containment for the building is calculated to be in excess of 700 gallons.

The ASTs are connected to each other via two lateral pipes (one high, one low) and allow for diesel to move from one tank to the other.  The tanks are connected to the generator via 13 ft. of ½ in. black steel pipe and all joints are threaded.  Flexible hosing connects the steel pipe to the engine, again, for protection against vibration.

The ASTs are not fitted with any audible alarm systems.  There is a low-level indicator which sends a signal to a computer in the WFO indicating when the tanks need to be refueled.

Table 1 in Section 7 summarizes the diesel storage capacities at WFO El Paso.

3. 	Drainage Pathway and Distance to Navigable Waters

The terrain at the El Paso NWS facility is relatively flat.  There is very little change in grade around the WFO, WFO emergency generator, or RDA complex.  Much of the area is covered with gravel.  Areas not covered in gravel consist mostly of tightly packed, fine-grained sand.  Diesel fuel, being a light fuel, will easily penetrate the gravel and can penetrate sand with some success.  However, it is not anticipated that spilled fuel would travel far from the site of the spill, nor would it have any potential to impact any surface waters.  There is basically no water in the immediate vicinity of the facility.  The only navigable water in the region is the Rio Grande, which is approximately 5 miles to the east at its closest approach (See Figure 5).

Cleanup options for any significant spill that was not contained at this site would most likely be to remove the contaminated sediment and replace.

Three-spill kits containing absorbent boom, pads and pillows, and drain seals, are located at the main generator.  Two are stationed outside and adjacent to the 1,000 gal AST, and another kit is located inside the WFO generator building.

Oil spilled from the 1,000 gallon AST would spill onto the concrete pad and then onto the surrounding gravel.  Any oil spilled in the main generator room, that exceeded the secondary containment, would spill onto the floor of the space and out the doorway which faces east.  Oil spilled from the RDA ASTs would spill onto the floor of the building and if this secondary containment were to be exceeded, out the doorway which also faces east.  Fueling trucks –for both generator systems– park on the graveled areas adjacent to the fueling ports.  The trucks that supply fuel to WFO El Paso typically have a 1,600 gal. capacity and are constructed with 3 or 4 separate compartments.  In most cases the trucks utilize automatic shutoff nozzles (similar to the types used at gas stations) to prevent overfilling.

4.	Spill History

Reportable spill events from 1994 to present (date on cover of this plan):

None.

5.	Spill Potential, Volumes, and Rates

The most likely causes of spills from the ASTs are from overfilling or a ruptured hose during refueling, a failure of one of the compartments of the fuel truck, failure of the structural integrity of the AST, or a ruptured fuel line.

If conducted according to plan and with good management practices, large spills from fueling operations are not likely.

For the ASTs, a large spill caused by loss of structural integrity or vehicle collisions are low probability events owing to alarm systems, weekly testing of the generators and daily observations by NWS personnel.

Table 2 summarizes the potential type of spills, volumes, and rates.

6. 	Discussion of Facility Conformance with 40 CFR 112

Every effort has been made by the NWS to ensure that this facility fully conforms to the applicable provisions of 40 CFR 112.  The following is a brief summary of the applicable characteristics of the facility:

a. 	The facility is staffed 24-hours a day, 365 days a year.  The generators are tested monthly, and on a daily basis NWS personnel are working near and around both generator systems decreasing the likelihood of a large spill incident.  The facility is located near the Santa Teresa International Airport and the city of El Paso, Texas, where rapid response is available in the event of a fuel spill.

b. 	The 1,000 gallon AST has an overfill alarm as well as an interstitial alarm.  The day tank for the main generator is contained in an overfill catch basin.  The ASTs for the RDA generator are in a building which has been designed to provide ample secondary containment.

c. 	The SPCC Plan:

i.	Has the full approval of the appropriate NWS managers.

ii.	Has been prepared and certified by a Professional Engineer.

iii.	Provides for prevention efforts to ensure that fuel oil discharges will not occur.

iv.	Provides a vehicle to ensure that personnel training is accomplished.

v.	Provides for appropriate reporting of oil discharges.

vi.	Provides for appropriate mitigating actions to be taken if an oil discharge should occur.

7.  	Type of Oil and Storage Capacity

Table 1.  Descriptive Inventory of Facility Storage

| Tank | Nominal Capacity (Gallons) | Product Stored | Type | Double Walled? |
| --- | --- | --- | --- | --- |
| WFO AST | 1,000 | #2 Diesel | Rectangular Steel | Yes |
| WFO Day Tank | ~75 | #2 Diesel | Rectangular Steel | No* |
| RDA ASTs (2) | 229.8 each | #2 Diesel | Rectangular Steel | No* |

*  These ASTs have been provided with external secondary containment.

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES FOR SPILL PREVENTION AND CONTROL

This section describes the design components and operating procedures that have been or will be implemented at the facility to prevent oil spills. The facility will review the design and operational procedures contained in this section and implement those that are not currently in place.

A.	TANK AND SYSTEM DESIGN FOR SPILL PREVENTION

This section describes components and operating procedures that will be implemented at the facility to prevent oil spills.

1.	Aboveground Storage Tanks (AST)

WFO AST:  The AST construction will be compatible with the #2 diesel fuel held by the tank.  The AST will have secondary containment around the primary tank shell.  A level gauge or dip-stick will indicate the fuel level (from empty to full).

An automatic shut-off valve on the fill spout will be set to close at 90 percent of capacity (900 gallons).  The AST also will have an audible high-level alarm set at 85 percent of capacity (850 gallons) and interstitial monitoring device between the primary and secondary tanks that is connected to the audible alarm system.  A seven-gallon capacity spill container will surround the fill spout.

Day Tank:  This tank will have an open top spill pan (rupture basin) designed to hold 110 percent of the tank volume.  It will have a liquid level gauge to indicate the amount of fuel in the tank (empty to full) and a high-level float switch connected to the audible alarm to warn of overfilling.   The rupture basin will have a float switch designed to detect fuel that has spilled or leaked.  The float switch will be connected to an audible alarm system in the office.

Piping:  An anti siphoning valve will be located between the AST and the pump to prevent unwanted fuel from being siphoned from the AST.

2.	Tank Refueling and Truck Unloading Operations

All delivery drivers will have U.S. Department of Transportation hazardous material transportation training as required by Federal law.

The remainder of this section discusses the procedures that will be used during unloading of fuel from the tank truck into the AST to prevent spills.  This procedure will be documented every time refueling occurs using the appropriate form (See Appendix A).  Copies of these forms will be kept for 5 years.

a. 	The following procedure will be used before fuel delivery and unloading:

(See Appendix A-2)

- If applicable, place a magnetic, urethane spill cover over the storm drain catch basin inlet.

- The Designated Person or his designated representative should determine the available capacity (ullage) of the AST by converting the reading on the fuel gauge to gallons (see Appendix A).  This ullage is communicated to the fuel supply contractor and marked in the fueling log.

- Move spill containment equipment such as booms, spill barriers or spill kits into the unloading area.

- Block the tank truck wheels.

- Place drip pans under all pump hose fittings (if applicable) before unloading.

- The Designated Person or his designated representative and the delivery driver will ensure the fill nozzle is placed in the appropriate AST filling port.

b. 	The following procedure will be used during the fuel unloading period:

(Appendix A-2)

i.  		The Designated Person or his/her designated representative and the delivery driver will remain with or near the vehicle and the fuel tanks at all times during unloading.  Gauges on the AST and the truck, as well as the fueling nozzle, will be continuously monitored to ensure the ullage is not exceeded.  If the audible high-level alarm sounds, stop the unloading procedure immediately to ensure fuel ullage is not exceeded.

c.	The following procedure will be used after fuel unloading is completed:

(Appendix A-2)

- Record the amount of fuel transferred to the AST in the log (Appendix A-1).

- Drain the fill hose and then ensure that all drain valves are closed (if applicable) before removal of the hose from the tank.

- Pour any uncontaminated fuel in the drip pans, tank truck containment pool, or spill pipe spill bucket container into the AST (if it has the capacity) or dispose of appropriately.

- Inspect the tank truck before removing the blocks to ensure the lines have been disconnected from the tank.

- Remove the blocks from truck wheels.

- Place a copy of the completed fuel-unloading checklist in the SPCC.

3.	Inspections and Records

Inspection and Maintenance of Tanks:  The AST and day tank will be inspected, each time a maintenance technician visits the site, as well as the regularly scheduled monthly inspections, for any fuel leaks, especially at the tank seams (including the underside of the tank).  The outside of exposed piping will also be inspected.  Monthly and annual inspections will follow the checklists shown in Appendix B-1 and B-2.  Monthly and annual inspection forms will be completed by the staff.

Integrity Testing:  Integrity testing of the ASTs is required under the new regulations put forth by the U.S Environmental Protection Agency (EPA).  However manufacturers of shop-built tanks have stated that integrity testing of their tanks is not necessary and that best management practices should be employed instead.  The EPA has stated, “ for certain smaller, shop-built containers in which internal corrosion poses minimal risk of failure; which are inspected at least monthly; and, for which all sides are visible (i.e., the container has no contact with the ground), visual inspection alone might suffice, subject to good engineering practice.”

To comply with §112.8.c.6, WFO El Paso will continue to make observations during generator tests, conduct regular monthly and annual inspections, and recommend integrity testing only when it is warranted, e.g. noticeable leakage or corrosion.  Testing will also be conducted if the structural integrity comes into question as a result of a fire, earthquake or other similar event.

Record Keeping:  The Environmental/Safety Focal Point or Maintenance Technician, (person designated for spill prevention at the facility) will be responsible for completing (i) the Ullage Logs and documentation of Fuel Unloading Procedures, (ii) the Records of Inspections, (iii) the Training Record, and (iv) the Spill Response Exercise Record.  These records will be maintained for at least 5 years from the time of the recorded action.

4. 	Site Security

The WFO AST is not enclosed in fenced area; however, the facility is staffed 24-hours a day, 365 days a year, and there are security cameras strategically placed around the facility.  All buildings are kept locked.  The RDA and associated buildings are in a fenced compound which is also kept locked.  The exterior of the entire facility is lighted at night.

Signs are posted on and around the ASTs warning of the presence of a combustible liquid, the combustible liquid is diesel fuel, and that smoking is prohibited near the AST.  Fire extinguishers are located in the generator buildings.  There is no vehicular traffic near the ASTs.

5. 	Training

As a minimum, the Environmental/Safety focal point, an alternate, and the responsible manager (MIC, HIC, or OIC) are trained in the intent of applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in the previous paragraph.  Spill control and countermeasure is included in the training.  An outline for the training is found in Appendix C.

Training is repeated once per year.  All new personnel responsible for implementing this SPCC plan are properly trained before beginning work at the new position.  A record of who is trained when, and by whom (Appendix C) is filed with this SPCC plan and kept for a period of 5 years.

B. 	SPILL CONTROL

This section describes control measures that have been implemented to prevent any spilled oil from entering navigable waters or adjoining shorelines.

1.	Secondary Containment Designs, Construction Material, and Volume

The AST for the WFO’s generator is fitted with secondary containment.  The secondary containment consists of a 0.25-in. Styrofoam shell which is encased in a polypropylene jacket.  At the bottom of the polypropylene jacket is a moisture sensor (interstitial alarm) which if activated triggers an audible alarm at the tank.  Surrounding the polypropylene jacket is a 6 in. layer of concrete.

The secondary containment for the WFO generator’s day tank is a steel catch basin mounted under the day tank.  The volume of the catch basin is calculated to be approximately 200 gal.

The secondary containment for the RDA ASTs is the pre-fabricated housing itself and provides for approximately 150 percent of the volume of the storage tanks.

2.	Spill Kits Type and Location

The Pig 202 spill kits or equivalent will be located in the generator room or in the Generator Building near the respective ASTs.  The spill kits are designed to absorb up to 60-gallons each of diesel fuel and to divert a spill from navigable waters.  The kits include oil absorbent socks and mats in a polyethylene container that doubles as a disposal container.

3. 	Drain Inlet Cover

If applicable, magnetic, urethane will cover will be placed over the storm drain catch basin inlet prior to any fuel transfer.

4.	Personal Protective Equipment (PPE)

If a leak or spill were to occur, it might be necessary for NWS personnel to conduct initial emergency procedures to minimize the impact of the spill, control the spill, or secure the area.  In order for them to employ the SWIMS procedure (see Part III.A of this plan) it may be necessary for them to come into contact with the diesel fuel.  If this were to occur, NWS personnel must use proper PPE.  Proper PPE for diesel fuel is specified in the MSDS (Appendix F).

    - Eye protection is accomplished by the use of Chemical Goggles or a Full Face Shield.  An Eyewash Station should be provided in the area.

    - Hand protection is accomplished by the use of Nitril Gloves and will be worn at all times when handling this material.  If there is a likelihood of skin exposure then impervious clothing such as Tyvek should be worn.

    - Other clothing & equipment - if contaminated - must be removed and laundered before reuse.  Items that cannot be laundered should be discarded.

PART III - SPILL COUNTERMEASURES AND REPORTING SPILL COUNTERMEASURES

A. 	SPILL COUNTERMEASURES

This section presents countermeasures to contain, clean up, and mitigate the effects of any oil spills at this site.

1.	SWIMS

A spill containment and cleanup activity will never take precedence over the safety of personnel.  No countermeasures will be undertaken until conditions are safe for workers.  The SWIMS procedure should be implemented as countermeasures:

S  -	Stop the leak and eliminate ignition sources.

a. 	Attempt to seal or some how stop leak if it can be done safely.

b. 	Attempt to divert flow away from any drainage ditch, storm sewer or sanitary sewer with a spill barrier or the contents of spill kit.  The spill kit is located in the Generator Building.

c. 	Eliminate all ignition sources in the immediate area.

W  -	Warn others.

a.  	Yell out “SPILL”.  Inform the person in-charge at your facility.

b. 	Account for all personnel and ensure their safety.

c. 	Notify contacts and emergency response contractor as described in the following section for assistance in control and cleanup.

I  -	Isolate the area.

a. 	Rope off the area

M  -	Minimize your exposure to the spilled material by use of appropriate clothing and protective equipment.  If possible, remain upwind of the spilled material.

S  -	Standby to assist the emergency response contractor.

B. 	SPILL REPORTING

This section discusses the reporting procedures for spills of diesel fuel at the facility.  The people and organizations that are notified vary, based on the quantity of the spill, whether it reaches navigable waters or adjoining shorelines, the frequency and history of spills and the potential impacts which the spill may have on people, property, or the environment.

A spill report form that requests the information to be reported to all agencies in writing (to the extent known) is included in Appendix D.  Copies of the completed form should be sent to the NWS Environmental Compliance Officer and the National Oceanic and Atmospheric Administration (NOAA) Mountain Regional Compliance Officer (see next section).

1.	General Notification Procedures for All Spills

- First, call 911 (or the local emergency agency) if there is an immediate emergency.

- Next, notify the appropriate persons within the NWS and NOAA:

  - Terry Brisbin, Regional Env/Safety Coord.	817-978-2644 x139

  - Mark George, RECO for the Mountain Region	303-497-3064

  - Mike Jacob, NWS Env. Compl. Officer		301-713-1838 x165

  - Olga Kebis, NWS Safety Officer			301-713-1838 x173

2.	Federal Notifications

The Federal Clean Water Act as described in 40 Part 110.6, requires notifying the EPA National Response Center or the U.S. Coast Guard (USCG) as soon as anyone has knowledge of any discharge of oil in quantities that “may be harmful,” 40 CFR 110.3 defines “may be harmful” as a discharge if either of the following applies:

Violates applicable water quality standards.

Or

Causes a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or cause sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines.

If either of these criteria is met, contact the following:

The National Response Center    		800-424-8802

EPA Region 6				866-372-7745

Additionally, under the SPCC regulations under 40 CFR 112.4(a), if either of the two spill criteria (listed below) occurs, a report must be submitted to the EPA Regional Administrator within 60 days:

- A discharge of more than 1,000 gallons of oil into or upon navigable waters or adjoining shore lines in a single event.

- Two spill events that cause discharge of more than 42 gallons in each event, within any 12 month period.

Please refer to 40 CRR 112.4(a) for instructions on the required contents of the report and proper reporting procedures.

Diesel fuel is not listed as a hazardous substance under the Comprehensive Environmental Response Compensation, and Liability Act (CERCLA); therefore, no other notification to the EPA is required for discharges of diesel fuel other than those listed previously.

3.	State Notifications

The ASTs at WFO El Paso are not regulated by the State of New Mexico’s Petroleum Storage Tank Bureau (i.e., the tanks to not exceed 1,319 gal. and are “associated with an emergency generator system.”), however, the state does require that prompt notification be made when there is a spill or release of “any material in such quantity as may with reasonable probability injure or be detrimental to human health, animal or plant life, or property, or may unreasonably interfere with the public welfare or the use of property.”

In this instance notification should be made to the New Mexico Dispatch Office who will then in turn contact the New Mexico Environment Department:

- NM Environment Dept. (via Main Dispatch)     505-827-9329

Note:  New Mexico has not established reportable quantity thresholds.

If needed additional state assistance can be obtained from the New Mexico State Police.

- New Mexico State Police Dispatch		505-827-9126

4.	Local Contacts and Notifications:

    - Santa Teresa Volunteer Fire Dept.		911 or 800-260-0911

    - Dona Ana County Emerg. Management		505-527-8741

    - Local Emerg. Planning Comm.			505-524-6300

5. 	Cleanup Contractor Notification

The following cleanup and environmental consulting contractors have been identified in the Santa Teresa area that would be able to assist WFO El Paso in the event of a spill emergency:

D&H Pump Services, Inc. (Spill Cleanup)

1221 Tower Trail

El Paso, Texas  79907

915-859-8150 or 915-859-8111

Rhino Environmental Services, Inc. (Spill Cleanup)

350 Valley Chile Road

Vinton, Texas  79821

915-886-4355 or 888-461-1894 (Pager)

ENCON Environmental Services, Inc. (Environmental Consulting)

7307 Remcon Circle

Suite 101

El Paso, Texas  79912

915-833-3740

PART IV - RECOMMENDED IMPROVEMENTS

In accordance with 40 CFR 112.7, this section presents physical upgrades or procedural changes that are not yet fully operational but are called for in the plan.

A.	PHYSICAL UPGRADES

The ASTs, piping system, alarm system, and spill response equipment satisfy all current Federal and State of New Mexico requirements and are in good operating condition.  However, the following changes and upgrades are recommended:

- Provide secondary containment for the refueling truck when practicable.  Until that time, employ best management practices (see below).  There are a number of secondary containment options available to the agency.  There are several types of temporary drive-on berm systems commercially available.  Another simple option might include installing asphalt berms at the fueling site with properly engineered, and controllable, drainage systems.  Obviously, any engineered system would require the approval of a licensed engineer.

Note: Currently industry has requested that EPA redefine the term ‘loading/unloading rack’ (§112.7 (h)).  It is possible that a change in this definition could exempt a facility from providing secondary containment for fuel trucks during fuel delivery for on-site consumption.

- Have the float switch for the WFO AST tested regularly.  Repair if necessary.

- Install secure fencing around WFO AST when practicable.  Until such time, continue to employ good security practices such as maintain lighting and security cameras.

- The catch basin for the day tank did not have a level indicator nor an alarm.  Nor was there one for the day tank.  In accordance with 40CFR §112.8(c).8 installing such a system for the day tank and/or the catch basin is recommended.

- It is not clear as to the purpose of the PVC sheathing on the black pipe leading from the WFO AST into the generator building.  The PVC sheathing is problematic in that it does not allow for routine inspections, and more than likely provides an environment around the black pipe that promotes corrosion.  If the sheathing was meant as secondary containment, then it should be removed and a more appropriate form of secondary containment installed, such as a lined catch basin.  If the sheathing was meant as a form of physical protection, then the solid PVC piping should be exchanged for a sheathing that provides physical protection and allows for visual inspection and drainage to reduce the risk of corrosion (e.g. PVC drainage piping).

B.	PROCEDURAL CHANGES

The following procedures and/or procedural changes are recommended:

- Owing to the lack of secondary containment for the fuel truck it is strongly recommended that proper procedures be diligently followed during refueling operations as prescribed in Part II, A.2 and Appendix A of this plan.

- Perform all inspections as outlined in Part II, A.3 and Appendix B of this plan.

- Maintain a training program for all relevant personnel on an annual basis and when new personnel report to the facility as prescribed in Part II, A.5 and Appendix C of this plan.

- Continue to conduct spill exercises annually as prescribed in Part II, A.5 and Appendix D of this plan.

1.	Inspections and Preventative Maintenance

The inspection checklists found in Appendix B should be followed.  The interstitial monitoring device in the AST is designed to monitor the integrity of the primary tank.  Visual inspections of the outside of the secondary wall of the AST and the primary wall of the day tank will serve to signal a potential problem with the tank integrity.

Table 2.  Potential Spill Sources and Volumes

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| WFO AST and Day-Tank NOTE: The Steel AST and the Steel Day Tanks are separated by about 20' and are interconnected via a fuel transfer pump. | Overfilling or a ruptured hose during fueling. | 0 to 40a | 80b | Into the surrounding gravel/sand substrate. Very little grade in this area. | Spills of this nature would largely be contained on the paved area or in the gravel and sand around the tank area. |
|  | Failure of fuel supply line to pump | * 0 to 1000 ** 0 to ~75 | Variable depending on the nature of the failure. | Same as above; except in the case of failure inside the generator room. A spill of this nature would go onto the floor of the space and then east out the doorway, then into the gravel/sand substrate. | Can be minimized through routine inspections especially during operations. |
|  | Structural Failure | * 0 to 1000 ** 0 to ~75 | Variable depending on the nature of the failure. | Same as above. | Low probability event that both primary and secondary containment would have to fail. |
|  | Vehicle Collision | * 0 to 1000 ** 0 to ~75 | Variable depending on the damage. | Same as above. | Very low probability. There is no vehicular traffic near the AST. |
|  | Overturn or puncture in an earthquake | * 0 to 1000 ** 0 to ~75 | Variable depending on the nature of the damage. | Same as above. | Low probability. Santa Teresa is in a moderate-risk earthquake zone. |
|  | Failure of the pump to shut down after filling the day-tank or failure of the line from pump to day tank. | 0 to 1000 | Variable depending on the nature of the failure. | Same as above. | Can be minimized through routine inspections and maintenance. A fuel return line is installed to allow fuel to return to the AST in the event that the transfer pump does not shut down. |
|  | Structural Failure or Vandalism | * 0 to 1000 ** 0 to ~75 | Variable, depending on the extent of damage. | Same as above. | Can be minimized through routine inspections, maintenance and by the adherence to good security practices. |

Notes:	a	Based on a maximum pumping rate of 80 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump.

b	Approximate maximum pumping rate of fill truck.

*  	Steel, 1000-gallon tank mounted outside on a concrete pad.

** One rectangular steel day tank mounted in a catch basin under the generator

Table 2.  Potential Spill Sources and Volumes (cont.)

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| RDA ASTs (2), 229.8 gal. each for a total of 459.6 gallons | Overfilling or a ruptured hose during fueling. | 0 to 40a | 80b | Into the surrounding gravel/sand substrate. Very little grade in this area. | Spills of this nature would largely remain in the gravel and sand around the tank area. |
|  | Structural Failure | 0-459.6 | Variable depending on the nature of the failure. | Into the secondary containment of the building. | Low probability event that both primary and secondary tank shells would fail. Can be minimized by routine inspections. |
|  | Earthquake damage. | 0-459.6 | Variable depending on the nature of the damage. | Into the secondary containment of the building. | Low probability. Santa Teresa is in a moderate-risk earthquake zone. However, in the event of severe earthquake damage the integrity of the secondary containment could be compromised. |
|  | Structural Failure or Vandalism | 0-459.6 | Variable, depending on the extent of damage. | Into the secondary containment of the building. | Can be minimized through routine inspections, maintenance and by the adherence to good security practices. |

Notes:	a	Based on a maximum pumping rate of 80 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump.

b	Approximate maximum pumping rate of fill truck.

APPENDIX A

A-1 TANK ULLAGE AND FUELING LOG

A-2 FUEL UNLOADING PROCEDURE CHECKLIST

Appendix A-1

Tank Ullage and Fueling Log

Station Name: ___________________________

Tank Capacity: __________________________ (gallons)

| Date | Initials | Gauge Reading | Initial Volume of Fuel in Tanka | Available Capacity or Ullageb (gallons) | Quantity Added (gallons) | Comments |
| --- | --- | --- | --- | --- | --- | --- |

Notes:	a      From gauge reading

b     Available capacity = tank capacity (900-gallons) – initial volume of fuel in tank

Appendix A-2

Fuel Unloading Procedure Checklist

Station Name: _________________________________________________________

Date: _________________________   	Tank:____________________________

NWS Rep: _____________________   	Supplier: _________________________

| X | Item | Description | Comments |
| --- | --- | --- | --- |
| The following six items must be completed before fuel unloading. |
|  | 1 | Ensure the audible high-level alarm system and automatic shutoff valve are functioning properly. |  |
|  | 2 | Determine the available capacity (ullage) of the above ground storage tanks (AST) by converting the reading on the fuel gauge to gallons (See Appendix A, Page A-1). This ullage should then be marked in the fueling log and communicated to the tank truck unloading contractor. |  |
|  | 3 | Move spill containment equipment such as booms or spill barriers into the unloading area. |  |
|  | 4 | Block the wheels of the tank truck. |  |
|  | 5 | Place drip pans under all pump hose fittings (if applicable) after the hose is hooked up to the AST and before unloading. |  |
|  | 6 | Ensure the fill nozzle is in place in the appropriate AST appurtenance. In this case, the fill nozzle is placed in the fill pipe connected to the round spill container. |  |
| The following two items must be completed during fuel unloading. |
|  | 7 | Ensure that the NWS representative and the tank truck operator remain with the vehicle at all times during unloading. |  |
|  | 8 | Monitor the gauges on the AST and the truck continuously to ensure the ullage is not exceeded. If the audible high-level alarm sounds, stop the unloading of fuel immediately. |  |
| The following six items must be completed after fuel unloading. |
|  | 9 | Record the amount of fuel unloaded in the log (Appendix 1, page A-1). |  |
|  | 10 | Before removing the fill hose from the AST, ensure that it is drained and that all drain valves are closed (if applicable). |  |
|  | 11 | Pour any fuel in the drip pans, tank truck containment pool, or spill container on the fill pipe into the AST (if it has the capacity) or dispose of appropriately (describe how it was disposed of, if applicable). |  |
|  | 12 | Inspect the tank truck before removing the blocks to ensure the lines have been disconnected from the AST. |  |
|  | 13 | Remove the blocks from the tank truck wheels. |  |
|  | 14 | Place a copy of this fuel-unloading checklist in the SPCC Plan folder. |  |

Additional Comments Below:

APPENDIX B

B-1 MONTHLY INSPECTION CHECKLIST

B-2 ANNUAL INSPECTION CHECKLIST

Appendix B-1

Monthly Inspection Checklist

| Site Name: | Tank Name or Number: |
| --- | --- |
| Date of Inspection: | Inspected by: |
| Date of Last Inspection: | Signature: |
| A. TANKS | YES | NO | NOTES |
| Are there any oil stains on the outside of the tank, including the underside? |  |  |  |
| Is there any oil on the ground, concrete, or asphalt around the tank? |  |  |  |
| Are there any visible cracks or indications of corrosion on the tank, at fittings, joints, or seals? (Such as paint peeling or rust spots) |  |  |  |
| Are there any raised spots, dents, or cracks on the tank? |  |  |  |
| Does it appear that the foundation has shifted or settled? |  |  |  |
| Is the fuel gauge working properly? |  |  |  |
| Are all vents clear so they may operate properly? |  |  |  |
| If rainwater is present in secondary containment area, does sufficient volume remain for spill control? (if applicable) |  |  |  |
| B. PIPING | YES | NO | NOTES |
| Is there any oil on the outside of or under any aboveground piping, hoses, fittings, or valves? |  |  |  |
| Are aboveground piping, hoses, fittings, or valves in good working condition? |  |  |  |
| C. SECURITY/SAFETY/SPILL COUNTERMEASURES | YES | NO | NOTES |
| Are lights working properly to detect a spill at night? |  |  |  |
| Are all locks in the “lock” position? |  |  |  |
| Are all warning signs properly posted and readable? |  |  |  |
| Are vehicle guard posts in place and properly secured? (if applicable) |  |  |  |
| Are spill kits easily accessible, protected from the weather, and complete? |  |  |  |

Corrective Actions Required (explain below):

Appendix B-2

Annual Inspection Checklist

| Site Name: | Tank Name or Number: |
| --- | --- |
| Date of Inspection: | Inspected by: |
| Date of Last Inspection: | Signature: |
| A. MONTHLY CHECKLIST | YES | NO | NOTES |
| Have Monthly Inspection checklists been completed? |  |  |  |
| B. TANKS |  |  |  |
| Are all alarms and automatic shutoff devices working properly? |  |  |  |
| Is interstitial monitor functioning properly? (if applicable) |  |  |  |
| C. OTHER |  |  |  |

Corrective Actions Required (explain below):

APPENDIX C

C-1 TRAINING OUTLINE

C-2 TRAINING RECORD

Appendix C-1

TRAINING OUTLINE:

SPILL PREVENTION, CONTROL AND COUNTERMEASURES

Training will be provided for facility personnel at the following times:

1.	System startup or whenever new equipment is installed

2.	Within the first week of employment for new personnel

- Annually

The training will include complete instruction in the elements of the facility’s Spill Prevention, Control, and Countermeasure Plan and will include the following:

1. 	Pollution control laws, rules, and regulations including a summary of Title 40 of the Code of Federal Regulations Part 112 “Oil Pollution Prevention” (see Attachment)

2. 	Fuel Storage System

- Purpose and application of the following system elements:

- Tanks

- Piping

- Pumps

- Accessory equipment

- Electronic monitors

B. 	Operation, maintenance, and inspection of system elements

3. 	Spill Prevention

A. 	Potential spill sources

B.	Spill flow direction and impact on navigable waters

C.	Procedures to prevent spills, especially during fuel unloading

4. 	Spill Control

A. 	Secondary containment

B.	Safety valves

C.	Pump and equipment shutoff switches

D.	Use of catch basin inlet covers or other diversionary devices

5. 	Spill Countermeasures

A.	 Location and use of emergency phone numbers

B.	 Location and use of fire extinguishers

C.	 Location and use of spill cleanup kit

D.	 Implementing SWIMS procedure

Appendix C-2

TRAINING RECORD

NOTE:  SPCC TRAINING IS REQUIRED ANNUALLY

Site name: ___________________________________________

| Date of Training | Employee Trained | Trainer | Remarks |
| --- | --- | --- | --- |

APPENDIX D

D-1 SPILL RESPONSE EXERCISE RECORD

D-2 SPILL REPORTING FORM

Appendix D-1

SPILL RESPONSE EXERCISE RECORD

NOTE: 	 A SPILL RESPONSE EXERCISE WILL BE CONDUCTED

ANNUALLY AND RECORDED BELOW.

Site name: ___________________________________________

| Date of Exercise | Signature of Environmental Focal Point | Remarks |
| --- | --- | --- |

Guidelines for conducting a “SPILL RESPONSE EXERCISE”:

- Review PART III (SPILL COUNTERMEASURES AND REPORTING) of this plan

- Review the information required on the “SPILL REPORTING FORM” (Page D-2)

- Verify the telephone numbers shown on the “SPILL REPORTING FORM” (Page D-2)

Record the Date of the Exercise and the Signature of the Environmental Focal Point

Appendix D-2

SPILL REPORTING FORM (Form Dated 02/05)

| 1. GENERAL |
| --- |
| Name of Facility: | Address: |
| Completed by: | Organization: National Weather Service |
| Position: | Phone: |
| 2. SPILL INFORMATION |
| Date: | Time: |
| Location at Facility: | Quantity: |
| Substance Spilled: | Other: |
| 3. OUTSIDE NOTIFICATIONS |
| Agencies | Recorder at Outside Agency | Date and Time |
| Call 911 (or the local emergency agency), if there is an immediate emergency. |  |  |
| NWS/NOAA: Mike Jacob, (301) 713-1838 ext. 165 Olga Kebis, (301) 713-1838 ext. 173 Terry Brisbin, (817) 978-2644 x139 Mark George, (303) 497-3064 |  |  |
| EPA National Response Center, or U.S. Coast Guard: (800) 424-8802 |  |  |
| List Additional State and Local Agencies below: |  |  |
| 4. INFORMATION ON SOURCE AND CAUSE: |
| 5. DESCRIPTION OF ENVIRONMENTAL DAMAGE: |
| 6. CLEANUP ACTION(S) TAKEN: |
| 7. CORRECTIVE ACTION(S) TO PREVENT FUTURE SPILLS: |

Note:  	-   All information must be filled in.  If something is unknown, write “unknown.”

-   Copies must be sent to the NWS/NOAA personnel listed above.

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS OF TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, SECTION 112 WITH THIS PLAN

Appendix E

Cross Reference of the Requirements of

40 CFR 112 and this plan

| CFR Citation | Item | Plan Location |
| --- | --- | --- |
| 112.1(d)(2)(ii) | Criteria for need of an SPCC Plan | Table 1 |
| 112.4(a) | Reporting of Spills – Federal Notifications | Part III, B |
| 112.4(c) | Reporting of Spills – State Notifications | Part III, B |
| 112.5(b) | SPCC Plan review and amendment requirements – 5 year max. | Page ii |
| 112.5(c) | PE Certification of Technical Amendments | Page i |
| 112.7 | SPCC Plan – full approval by management | Page i; Appendix E |
| 112.7(a)(1) | Discussion of Facility Conformance | Part I, B.6 |
| 112.7 (a) (3) | Facility Description and Diagrams | Part I, A and B; Appendix K |
| 112.7 (a) (3) (i) | Type of Oil and Storage Capacity | Part I, B.7; Table 1 |
| 112.7 (a) (3)(ii) | Discharge Prevention Measures | Part II |
| 112.7(a)(3)(iii) | Discharge and Drainage Controls | Parts II and III |
| 112.7 (a)(3)(iv) | Countermeasures for Discovery, Response and Cleanup | Part III |
| 112.7 (a)(3) (v) | Methods of Disposal | Part III, B.5 |
| 112.7 (a) (3)(vi) | Contact List and Phone Numbers | Part III, B; Appendix D-2 |
| 112.7 (a)(4) | Spill Reporting Form | Appendix D-2 |
| 112.7 (a)(5) | Procedures In Event of Discharge | Part III, A; Appendix D-2 |
| 112.7 (b) | Flow Prediction Information | Table 2 and Appendix K |
| 112.7 (c) | Secondary Containment | Part II, A.1 & and A.2 |
| 112.7(c)(1)(vii) | Sorbent Materials | Part III, B.2; Appendix G |
| 112.7(d) | Commitment of Manpower and Equipment | Part III, B |
| 112.7 (e) | Inspections, Tests and Records | Part II, A.2; Appendix B |
| 112.7(f) | Training | Part II, A.5; Appendix C |
| 112.7 (g)(5) | Lighting | Part III, A.4 |
| 112.7(j) | State Rules, Regulations and Guidelines | Part III, B |
| 112.8(c)(6) | Container Testing | Part II, A; Appendix B |

APPENDIX F

MATERIAL SAFETY DATA SHEET (MSDS)

ELECTRONIC VERSION OF MSDS TO BE INSERTED HERE

APPENDIX G

SPILL CLEANUP KIT INFORMATION

Product Data Sheet

Item Number: KITR202

Item Name: PIG® Spill Kit in a 95-gallon Overpak Salvage Drum - MRO refill

Absorbency

•61 gal./each (230.9 L/each)

| Options Available |
| --- |
| Item # | Size | Color | Misc. Features | Amount | Length | Width | Height | Depth | Int. Dia. | Ext. Dia. | Weight |
| KITR202 | — | — | — | 1 each | — | — | — | — | — | — | 89lbs. (40.4kg) |

Description Replacement contents for a container with a variety of absorbents for responding to spills of oils, coolants, solvents, and water.

Application To be used to replace components used in KIT202 and KIT224

Features and Benefits Prepackaged/Easy to replace the contents of the original 95 gallon (360 L) spill kit (KIT202) Variety of absorbents/An assortment of absorbent products to handle non-aggressive spills up to 61 gallons (231 L)

Composition PIG® BLUE Socks: polypropylene and magnesium aluminosilicate PIG® Pillows: polypropylene and cellulose fibers PIG® Mats: polypropylene

| Kit Components |
| --- |
| Qty. | Description | Component Refill Item Number |
| 16 | 48" PIG® BLUE Socks | 4048 |
| 10 | 10' PIG® BLUE Socks | PIG202 |
| 60 | PIG® Universal Mat Pads | MAT203 |
| 8 | PIG® Pillows | PIL201 |
| 50 | PIG® Wipers | WIP310 |
| 10 | Temporary Disposal Bags and Ties | BAG201-L |
| 1 | Emergency Response Guidebook | N/A |
| 1 | Instructions | N/A |
| 6 | Tamperproof Seals | N/A |

| This product helps you comply with: |
| --- |
| Regulatory Citation | Summary |
| 40 CFR 112.7(c)(1)(vii) | Spill Prevention Control and Countermeasures (SPCC) plans require facilities that have the potential to pollute waterways to have, "appropriate containment and / or diversionary structures or equipment to prevent discharge oil from reaching a navigable water course." |

APPENDIX H

PERMITS

THIS PAGE LEFT INTENTIONALLY BLANK

APPENDIX I

PHOTOGRAPH LOG AND PHOTOGRAPHS

Appendix I

Photographic Log

| Photo # | Date | Description |
| --- | --- | --- |
| 01 | 8/31/04 | WFO Main Generator. |
| 02 | 8/31/04 | WFO Main Generator’s Day Tank and Catch Basin. |
| 03 | 8/31/04 | Black pipe leading from the AST to the WFO Main Generator. |
| 04 | 8/31/04 | WFO AST with Spill Kits. |
| 05 | 8/31/04 | WFO AST. |
| 06 | 8/31/04 | WFO AST with PVC-sheathed pipe Leading to Generator (facing east). |
| 07 | 8/31/04 | High-Level and interstitial audible alarm system. |
| 08 | 8/31/04 | WFO Main Generator Building and AST. |
| 09 | 8/31/04 | RDA Generator Building within fenced compound. |
| 10 | 8/31/04 | RDA ASTs’ filling port. |
| 11 | 8/31/04 | RDA ASTs. |
| 12 | 8/31/04 | RDA ASTs’ filling port and ventilation ducts. |
| 13 | 8/31/04 | RDA Generator Building’s secondary containment. |
| 14 | 8/31/04 | Locked door to RDA generator space. |
| 15 | 8/31/04 | WFO AST’s filling port (inside of overfill basin). |
| 16 | 8/31/04 | WFO AST’s shutoff valve to the generator. |

Photo 01.  WFO Main Generator.

Photo 02. WFO Main Generator’s Day Tank and Catch Basin.

Photo 03. Black Pipe Leading from the AST to the WFO Main Generator.

Photo 04. WFO AST with Spill Kits.

Photo 05. WFO AST.

Photo 06.  WFO AST with PVC-Sheathed Pipe Leading to Generator (Facing East).

Photo 07. High-Level and Interstitial Audible Alarm System.

Photo 08. WFO Main Generator Building and AST (Photographed from NEXRAD Tower).

Photo 09. RDA Generator Building within Fenced Compound.

Photo 10. RDA ASTs Filling Port.

Photo 11. RDA ASTs (229.8 gallons each).

Photo 12. RDA Generator’s Filling Port and Ventilation Ducts.

Photo 13. RDA Generator Building’s Secondary Containment (9 inches from floor to sill).

Photo 14.  Locked Door to RDA Generator Space.

Photo 15. WFO AST’s Filling Port (w/overfill basin).

Photo 16. WFO AST’s Shutoff Valve to the Generator.

APPENDIX J

FIGURE 1	MAP OF AREA

FIGURE 2	SITE DRAWING

FIGURE 3	WFO AST AND GENERATOR DIAGRAM

FIGURE 4	RDA SPACE DIAGRAM

FIGURE 5	TOPOGRAPHIC MAP & DISTANCE TO THE RIO GRANDE

ELECTRONIC VERSIONS OF FIGURES TO BE INSERTED HERE

ATTACHMENTS

ATTACHMENT 1	40 CFR § 112

ELECTRONIC VERSION OF 40 CFR 112 TO BE INSERTED HERE

# Comments

Can you inspect the pipe through this PC sheathing?