Accident consequences analysis of the HYLIFE-II

# Inertial Fusion Energy Power Plant Design

S. Reyesa,b,*, J. F. Latkowskia, J. Gomez del Riob,and J. Sanzb

a Lawrence Livermore National Laboratory, P. O. Box 808, L-446, Livermore, CA 94550,

Tel: 925-424-5684 ( Fax: 925-422-7390

b Universidad Nacional de Educacion a Distancia, Escuela Tecnica Superior Ingenieros Industriales,

### Departamento Ingenieria Energetica, C/ Ciudad Universitaria, s/n, 28040 Madrid, Also: Instituto Fusion Nuclear, Madrid, Spain

Abstract

Previous studies of the safety and environmental (S&E) aspects of the HYLIFE-II inertial fusion energy (IFE) power plant design have used simplistic assumptions in order to estimate radioactivity releases under accident conditions. Conservatisms associated with these traditional analyses can mask the actual behavior of the plant and have revealed the need for more accurate modeling and analysis of accident conditions and radioactivity mobilization mechanisms. In the present work computer codes traditionally used for magnetic fusion safety analyses (CHEMCON, MELCOR) have been applied for simulating accident conditions in a simple model of the HYLIFE-II IFE design. Here we consider a severe loss of coolant accident (LOCA) in conjunction with simultaneous failures of the beam tubes (providing a pathway for radioactivity release from the vacuum vessel towards the confinement) and of the two barriers surrounding the chamber (inner shielding and confinement building it self). Even though confinement failure would be a very unlikely event it would be needed in order to produce significant off-site doses. CHEMCON code allows calculation of long-term temperature transients in the fusion reactor first wall, blanket, and shield structures resulting from decay heating. MELCOR is used to simulate a wide range of physical phenomena including thermal-hydraulics, heat transfer, aerosol physics and fusion product transport and release. The results of these calculations show that the estimated off-site dose is less than 5 mSv (0.5 rem), which is well below the value of 10 mSv (1 rem) given by the DOE Fusion Safety Standards for protection of the public from exposure to radiation during off-normal conditions.

Keywords: IFE safety analysis; Accident consequences; Off-site doses

* Corresponding author.

E-mail address: reyessuarez1@llnl.gov (S. Reyes)

1.	Introduction

The HYLIFE-II IFE power plant concept [1] sought to maximize its attractiveness by providing lifetime components, high availability, low cost of electricity and favorable S&E characteristics. During the original HYLIFE-II study, S&E goals included:

- low off-site dose from a severe accident

- avoidance of nuclear grade (N-stamp) for most components (requiring less than 0.25 Sv off-site dose in the event of failure of that component)

- working area dose rates less than 50 (Sv/hr for low occupational risk

- dose from routine atmospheric effluents less than 50 (Sv/yr.

Since that time, the nuclear community (fission and fusion) has reached a consensus and established more restrictive safety goals. The DOE Fusion Safety Standards [2] for public protection in case of accident give a limit off-site dose of 10 mSv (1 rem). This dose is a 50-year committed effective dose to the most exposed individual (MEI) at the site boundary (1 km) that only includes contributions from direct cloudshine and inhalation during plume passage, because they pose an immediate threat. This value is based upon a 1991 Environmental Protection Agency document that specifies the level at which sheltering and evacuation should be undertaken [3].

This work concentrates on severe accident analysis in order to compare off-site obtained doses to the values provided by DOE Fusion Safety Standards. The present work focuses on what has been considered to be one of the most severe possible accidents in the HYLIFE-II design. We assume a LOCA with loss of all the liquid flibe and simultaneous break of all the beam tubes, which provides a flow path from the target chamber to the confinement. In addition, breaks in both the inner shielding wall and the confinement building wall are assumed. These breaks provide a pathway for release of radioactive material to the environment.

In order to perform a consequences analysis, first we need to know the source term of radioactivity that is released to the environment. Neutron transport and activation, thermal transients, and aerosol transport calculations have been performed. Given the activity release and the specific dose of each isotope, which has been evaluated with the MACCS2 code [4], the accident dose may be calculated.

2.	Long-term thermal behavior

Prior to the calculation of radioactivity release fractions, one needs to know the time-temperature histories of the different reactor components during the accident. This is used to determine the activation products source term available for mobilization, which will later be used as input data for the MELCOR calculations [5].

In this case the only energy source is the radioactive decay heat from the activated material in the reactor components. Once the accident begins, it is conceivable that fusion reactions could continue to occur for a short period of time. Several factors must be considered: accelerator operation, target injection, and beam propagation through a varying environment. If accelerator operation and target injection both continue, then beam propagation ultimately will determine when ignition is no longer possible. We have assumed a complete loss of coolant accident combined with multiple breaks in the beam tubes, shielding, and confinement building. These breaks will allow air to enter the beam tubes and chamber, and this air will result in the inability to propagate the heavy ion beams to the target.

Langdon discusses the pressure of gas that is allowable for successful beam propagation [6]. For an unneutralized beam, a background pressure of more than 13 Pa (conservatively assuming lithium gas) guarantees that stripping and plasma instabilities will destroy the beam. For a fully neutralized beam, a pressure of about 2700 Pa will produce multiple scattering, which will destroy propagation. If we conservatively assume that the beams are fully neutralized, then fusion yield might continue until enough air enters the beam tube to raise the pressure to 2700 Pa.

To determine the time required to reach 2700 Pa within the beam tubes, a simple MELCOR calculation was performed. We see that 2700 Pa is reached within only 50 ms, and thus, a plant operating at 6.4 Hz will not be able to ignite the next target before beam propagation is halted due to air pressure.

Considering then that decay heat from activated materials is the only existing source available for heat transfer, a CHEMCON [7] calculation was developed using a simple 1-D cylindrical model. This model consists of four stainless steel shells that represent the tubes containing the flibe, first structural wall, blanket structure and vacuum vessel, a inner concrete shield and the confinement building wall. Conduction, convection and radiation heat transfer was calculated between these structures. The activation and decay heat results were obtained from the ACAB [8] activation code following 30 years of plant operation. Fluxes in structures were calculated with TART [9] Monte Carlo neutron transport code. Figure 1 shows the thermal transient in the different reactor components due to the decay heat from the activation products.

The first wall temperature, initially being 675 (C, displays a mild peak at 679 (C at about 15 minutes, after which it gradually falls. This indicates that the radioactive afterheat is low enough to avoid melting of the stainless steel structure (Tmelt ~ 1400 ºC) or any over-stress damage. This result eliminates the possibility of volatilization of the stainless steel structures during the accident, which would result in a significant increase in the radioactive mobilized mass.

In order to protect the first structural wall from direct neutron fluxes, the updated HYLIFE-II design considers a flibe pocket 60 cm thick, which is the value used in our final accident analysis. A parametric study was developed in order to evaluate the benefit of a thick liquid wall on the activation of the structures and accident temperatures. ACAB calculations were performed for different flibe pocket thickness and irradiation times of 3 and 30 years irradiation. Figure 2 shows the maximum accident temperatures obtained with CHEMCON for the different cases.

It can be observed that an unprotected wall would not reach the melting point either. This result is very important when accounting for the stainless steel mobilized masses. Figure 2 also shows the benefit of introducing a thick liquid protection. For example, note that for thickness > 15 cm, a 30-yr protected wall is better than a 3-yr unprotected wall in terms of maximum accident temperature.

3.	Activation products source term

There are four main sources of radioactivity that must be considered in HYLIFE-II. First, the x-rays from each target vaporize a maximum of 10 kg of flibe. Although we assume a total LOCA, our analyses conservatively include this flibe aerosol with its activation products.

Second, it is estimated that approximately 140 g of tritium would be trapped within the chamber, blanket, and piping [1]. We assume that entire tritium inventory is converted to the more radiotoxic HTO form. This yields a mass of HTO aerosol of 930 g, which we round up to 1 kg.

Third, we assume that the corrosion of type 304 stainless steel (SS304) by flibe within the chamber and blanket can be limited to 1 (m/y via corrosion control methods. Additionally, we assume that the flibe clean-up system can maintain the mobilizable inventory of corrosion products to a 1-y supply. Given a total surface area of 1040 m2, we obtain a corrosion product inventory of 8.3 kg in the total flibe volume.

Finally, we use data from oxidation-driven mobilization experiments on PCA performed at the Idaho National Engineering and Environmental Laboratory (INEEL) to calculate an additional 0.5 kg of SS304 (we assume that SS304 mobilization will be the same as that from PCA) that is mobilized under exposure to steam at the accident temperatures previously calculated [10,11]. Adding this 0.5 kg to the 8.3 kg of corrosion products, we have ~ 9 kg, which we round up to 10 kg of SS304. Considering that only about 5% of the flibe is present in the chamber at any given time, we end up getting 0.5 kg of SS304 as corrosion and oxidation products.

It is worth noting that we are being quite conservative in assuming that the corrosion products will be in an aerosol form and available for mobilization (one could make an argument that the corrosion products would leave with the flibe during the LOCA). Additionally, our assumption of steam oxidation driven mobilization is conservative – because the secondary system uses water, it is credible that some water could collect in low points of the plant, but the layout will be designed to avoid water anywhere near the flibe ducts. At temperatures of interest, oxidation-driven mobilization from PCA under exposure to air occurs at a rate that is ~ 900( lower than that under exposure to steam.

4.	Radioactivity release and off-site doses

To estimate release fractions, a MELCOR model of HYLIFE-II was developed. This model consists of four stainless steel shells, which represent the SS304 tubes, first wall, blanket structure and vacuum vessel, a concrete inner shield and the containment building. The beam tubes were also modeled, considering an updated HYLIFE-II version that includes 96 beams per side. Beam tubes and volumes within the vacuum vessel are assumed to be at vacuum. The SS304 shells are initially at their operating temperature of 675 ºC.

The radioactive source term described in the previous section is used as input data for the masses of activated material that is available for mobilization during the transient.

We have considered a severe accident consisting of a total LOCA, with loss of all the liquid flibe, with simultaneous failure of the beam tubes, the concrete inner shielding and the confinement. The total failure of the beam tubes (the area of the break is modeled as the calculated area of the total number of beams) means that the inner volumes are going to have a flow path towards the outer volumes, which are filled with air at atmospheric pressure. Both the inner shield and confinement walls are initially at an estimated temperature of 32 ºC.  Additionally, we assume a double failure of the inner shielding and concrete building  (each of these breaks is 1 m2 in area) that provides a pathway to the environment. This model is used by MELCOR to simulate the progression of the accident.

The MELCOR heat transfer package considers conduction, convection and radiation between the structures. The aerosol transport module treats SS304 and flibe aerosol nucleation and agglomeration, vapor condensation, gravity settling and gaseous/liquid transport. A new module introduced by INEEL allows simulation of HTO transport and condensation. Calculations of tritium migration from the stainless steel shells were also developed using TMAP (Tritium Migration Analysis Program) rather than assuming an instantaneous liberation from the structures. These calculations showed that at the operating temperature of 675 ºC, the tritium migration from the steel is fast enough (>90% in only 1.5 hour) that there is no difference when comparing with the results from the instantaneous migration assumption [12].

The transient is considered to be one month long. Table 1 shows the fraction of the source term masses that are released to the environment during the accident, so as the final doses. It can be noticed that from the initial 0.5 kg of SS304 that is mobilized, only 63 g are released to the environment. Approximately 1.1 kg (out of 10 kg) of flibe is released. Finally, due to partial condensation of the HTO on the colder walls of the building, we get a release fraction of 86% of the initial 1 kg mobilized.

With these data about the activity released in units of Bq, and the adequate dose conversion factors (DCF) in units of Sv/Bq, off-site doses can be obtained. Of the total inventory in the reactor at the moment of shutdown (just before the accident happening), all the radionuclides whose contribution to the radioactivity release was above 3.7 x 107 Bq (1 mCi) were considered for dose calculation purposes. The DCF library has been updated to include radionuclides that were missing from traditional (fission) libraries as some of these radionuclides maybe important for fusion doses. Data on DCF were obtained using the MACCS2 code in order to calculate early doses (defined as the equivalent effective doses with 50 years commitment, resulting from the first 7 days of exposure during the plume passage). In addition to direct cloudshine and inhalation during plume passage, our doses also consider contributions from groundshine, and inhalation of resuspended material. Typical weather conditions and ground level release were assumed as recommended by the Fusion Safety Standards.

With these assumptions, the results from Table 1 show that the dominant dose is from the tritium in HTO form, which gives a total of 4.6 mSv (460 mrem). Both the SS304 and the flibe make small contributions to the total dose, being 3.3 μSv (0.33 mrem) and 38 μSv (3.8 mrem), respectively. If conservative weather conditions are assumed instead of typical, then the calculated doses would be about 10( higher. On the other hand, assuming an elevated release in typical weather conditions would result in doses an order of magnitude lower than those calculated in the case of ground level release.

It should be pointed out that about 75% of the SS304 dose comes from 60Co, and for the flibe, 18F is the only contributor to the dose. From the total activity due to 18F at the moment of the reactor shutdown (1.26 x 1019 Bq = 340 MCi), only 8.6 x 1014 Bq (0.023 MCi) are vaporized and available for mobilization during the accident. The final quantity of activity from the 18F that is released to the environment is 1014 Bq (2.7 x 103 Ci).

The final result is that even with the various conservatisms introduced in the calculation, the off-site accident dose is under 5 mSv (0.5 rem). This is a relevant result given that it is below the limit of 10 mSv (1 rem) given in the DOE Fusion Safety Standards, which means no sheltering and evacuation are needed.

5.	Conclusions and future work

The primary goal of accident consequence analyses is to integrate the findings of the accident scenarios with the materials mobilization data and dust/aerosol transport modeling to estimate radiation doses under accident conditions. Doses and the consequences of those doses must be calculated to enable direct comparison of IFE hazards with those associated with fission and non-nuclear systems.

In the present work, accident doses have been analyzed for the HYLIFE-II IFE design. A severe LOCA with failure of the beam tubes, and double failure in the inner concrete shielding and confinement building has been simulated using fusion safety codes.

The long-term thermal study of the various reactor components has shown that the decay heat from activation products is low enough so that there is no melting of structures during the accident and temperatures reach a mild peak over the operational values before they start dropping.

The off-site dose released in this accident has been calculated to be less than 5 mSv (0.5 rem). This result is well below the limit given by the Fusion Safety Standards of 10 mSv (1 rem) during an off-normal event in order to avoid public sheltering and evacuation. We can conclude that the HYLIFE-II design has very favorable safety characteristics according to this analysis.

Additional work is needed to identify and simulate other accident scenarios in order to make a complete safety analysis for HYLIFE-II. Accidents that do not involve a total LOCA will have to make use of the equation of state of flibe, which will have to be introduced in MELCOR code. Also other IFE designs must be considered and analyzed in a similar way to have a wider perspective of the attractiveness of IFE designs from a safety and environment point of view.

## Acknowledgements

The authors would like to thank their colleagues at the INEEL for their assistance and recommendations that have been essential to the completion of the above work.

Work performed under the auspices of the U. S. Dept. of Energy by University of California Lawrence Livermore National Laboratory under Contract W-7405-Eng-48 and under support of scholarship from UNED, Madrid, Spain.

## References

[1]	R. W. Moir, et al., Fus. Technol. 25 (1994) 5-25.

[2]	"Safety of Magnetic Fusion Facilities: Guidance," DOE-STD-6003-96, U. S. Department of Energy, Washington, D. C. (1996).

[3]	"Manual of Protective Action Guides and Protective Action for Nuclear Incidents, "PB92-164763, U. S. Environmental Protection Agency, Washington, D. C. (1991).

[4]	D. Chanin and M. L. Young, NUREG/CR-6613, Vol. 1, SAND97-0594 (1998).

[5]	R. O. Gauntt, R. K. Cole, S. A. Hodge, S. B. Rodriguez, R. L. Sanders, R. C. Smith, D. S. Stuart, R. M. Summers and M. F. Young, NUREG/CR-6119, Vol. 1, Rev. 1, SAND97-2398 (1997).

[6]	A. B. Langdon, Particle Accelerators, 37 (1992) 175-180.

[7]	M. J. Gaeta and B. J. Merrill, Idaho National Engineering and Environmental Laboratory, INEL-95/0147 (1995).

[8]	J. SANZ, Universidad Nacional de Educacion a Distancia (UNED), Lawrence Livermore National Laboratory, UCRL-CR-133040 (1999).

[9]	D. E. CULLEN, Lawrence Livermore National Laboratory, UCRL-ID-126455, Rev. 2 (1998).

[10]	K. A. McCarthy, G. R. Smolik, D. L. Hagrman, and D. A. Petti, J. Nucl. Mater. 233-237 (1996) 1607-1611.

[11]	G. R. Smolik, W. J. Carmack, and K. Coates, Idaho National Engineering and Environmental Laboratory, ITER/US/97/TE/SA-25 (1997).

[12]	Rion Causey and Thomas Venhaus, personal communication (2000).

Figure 1

Figure 2

Fig. 1. Temperature evolution in the various reactor components during the first day following the accident.

Fig. 2. Maximum accident temperatures reached at the first structural wall for different flibe pocket thickness.

Table 1. Mobilized masses/activities, release fractions and off-site doses for the different considered radioactivity source terms.

| Radioactive source | Mobilized mass / activity | Release fraction | Off-site dose |
| --- | --- | --- | --- |
| SS304 corrosion / oxidation | 0.5 kg / 1.31 · 1012 Bq | 13% | 3.3 μSv / 0.33 mrem |
| Vaporized flibe | 10 kg / 7.06 · 1015 Bq | 11% | 38 μSv / 3.8 mrem |
| HTO trapped in steel | 1 kg / 4.99 · 1016 Bq | 86% | 4.6 mSv / 460 mrem |

# Text boxes

ThP.I-04