Statement Of Work

TDWR Site Investigation

And Technical Analysis Of

All FAA TDWR Sites

United States Of America

General:

This document covers the requirements of the Federal Aviation Administration (FAA) for a complete technical analysis of the condition of the HVAC systems serving all the TDWR installations throughout the continental United States.

Background:

The existing HVAC units are approximately 10 years old and in some cases older.  This places these units at or over their expected useful life expectancy.  In order to prioritize the systematic and efficient replacement of these aging units, a site survey is required to document the actual condition of the HVAC systems serving all the TDWR sites.  Since some units have already been replaced, and in some cases modifications may have been made, a site survey by a single contractor is necessary to establish a realistic schedule of replacement without defaulting to letting these units fail and replacing them on an emergency basis.

Location Of Project:

All Federal Aviation Administration TDWR Sites

Eastern Service Area Headquarters

1701 Columbia Avenue

College Park GA  30337

Project Description:

The work shall include, but not be limited to, furnishing all labor, materials, equipment, and services as may be necessary to do a technical and thorough analysis of the condition and configuration of the HVAC systems and their associated components, ancillaries, controls, etc.  The entire analysis consists of the following:

Examine the arrangement of the HVAC equipment inside and outside the TDWR building and compare to the drawings attached.  Note any discrepancies or changes from the drawings.

Take temperature readings of all airflows entering and leaving the evaporator and condenser coils.  Also, surface temperatures of the refrigerant lines at the condensers and compressors.

Record name plate data on all equipment.  This shall include motors and assembles, such as blower coils and condensing units.

Check the operation of all manual and motor operated dampers.

Take super-heat and sub-cooling readings on the refrigeration circuits.  Take pressure and temperature readings on the refrigeration circuits at each of the units.

Investigate the control systems and remote monitoring there of.

Note physical conditions of each system such as belt tensions, vibrations, presence of dirt, and presence of obstructions in ductwork or plenums and possible leakage from portions of the air distribution systems.

Take digital pictures of all HVAC components.

Take digital pictures of all related electrical and control equipment.

Assess the condition of each piece of TDWR HVAC equipment.

Prepare a written report for each site.  Report shall include all data mentioned above, nameplate data, pictures, field notes and assessment of condition.

After all sites have been visited, rank all sites from 1 to 47 for equipment replacement.  Indicate which sites fall into a critical category for immediate replacement.  Rank all others in order that replacement should occur.

PERFORMANCE TIME:

The Contractor shall complete the entire project including the 47 site investigations, condition determinations and the final report with recommended priorities within 18 months from the date of the notice to proceed.

SCHEDULE OF WORK:

All work, on each site, shall be performed during normal daytime hours of 7:30 AM to 4:00 PM unless otherwise approved by the local contact personnel or the Technical Contact.  Contractor shall submit a schedule of when each site will be visited, within 15 calendar days from award of contract, for review and approval by FAA.

DELIVERABLES:

The report shall consist of a narrative of all the findings, field notes, instrument readings and digital pictures of the HVAC systems and equipment at all 47 sites.  Each site should have a separate chapter in the final report for the 47 sites.  Arrange the narrative, in each chapter, into at least three parts.  Detailed system description, detailed evaluation of the condition, and detailed opinion of the performance of the system.  In a separate chapter, list the conclusions and recommendations.  An appendix should contain the field notes, instrument readings and summations of the data in chapter arrangement.  The report shall be in Word format.  Provide 6 pre-final hardbound copies for review and comment.  Provide 6 hard bound final copies and 3 copies of the source files on a CD-RW.

Attachments:

Drawings:

SO-D-101529-E01

SO-D-101529-E03

SO-D-101529-M01

List of TDWR sites

Directions to each site.

END OF DOCUMENT SOW