## Elev_Drop
Request | 5483
Requestor | C. Johnstone
Project | 2301
Task Mngr | Oshinowo
Crew | Crutcher,Teafoe,Wyatt, Jwilson
Date | Ides of March, 2007
ELEVATION TRANSFER AND FLOOR HEIGHT OBSERVTIONS PER REQUEST
ALL UNITS OF MEASUREMENT HEREIN ARE IN INCHES UNLESS OTHERWISE NOTED
40
16
MTA Enclosure Lower Level
32
21
LINAC Tunnel (Spur)
| Down Stream Tierod | [11 empty] | width 10.66'
198160
Up Stream tierod
198159
Shielding Blocks
The Mid points in the lower area are roughly 17 feet from the
up stream drop off into pit area
Lower Courtyard
Drop Tierod Outside in Lower Courtyard area between ladder & elevator
[5 empty] | 113332 | 226.811 | Meters | 8929.5499 | Inches | Hieght to top ot tierod
| Parking Area |  |  |  | Unadjusted height from run on the Ides of March, 2007
NOTE; THE OUTSIDE ELEV. RUN DID NOT CLOSE DUE TO WINDY CONDITIONS, THE CLOSURE ERROR WAS 0.060 INCHES, GOOD ENOUGH FOR THIS PROJECT HERE
Station | Plus |  |  |  | Instrument | Minus |  |  |  | Observed | Design | Delta | Comments
| Stick | Scale | Mic | Correction | Height | Stick | Scale | Mic | Correction | Height | Height
113332 | -15 | -11.6 | 0.04 | -0.872 | 8902.1179 | [5 empty] | 8929.5499 |  | (Tierod-Top) see comment above
TP#1 | [5 empty] | 44 | 14.2 | 0.067 | 0 | 8843.8509
| 44 | 14.9 | 0.048 | 0 | 8902.7989
TP#2 | [5 empty] | 44 | 14.8 | 0.072 | 0 | 8843.9269
| 44 | 15.4 | 0.015 | 0 | 8903.3419
198160 | Tierod Top |  |  |  |  | 0 | 8.3 | 0.421 | 0 | 8894.6209 |  |  | Dn.Stream Tierod MTA Enclosure
| 0 | 8.5 | 0.095 | 0 | 8903.2159
198159 | Tierod Top |  |  |  |  | 39 | 3.5 | 0.037 | 0 | 8860.6789 |  |  | Up Stream Tierod MTA Enclosure
| 39 | 2.8 | 0.021 | 0 | 8902.4999
198160 | Tierod Top |  |  |  |  | 0 | 7.8 | 0.079 | 0 | 8894.6209 | 8894.6209 | 0
| 0 | 7.6 | 0.064 | 0 | 8902.2849
TP#2 | [5 empty] | 44 | 14.3 | 0.059 | 0 | 8843.9259 | 8843.9269 | -0.001
| 44 | 13.7 | 0.034 | 0 | 8901.6599
TP#1 | [5 empty] | 44 | 13.8 | 0.012 | 0 | 8843.8479 | 8843.8509 | -0.003
| 44 | 13.3 | 0.013 | 0 | 8901.1609
113332 | [5 empty] | -15 | -12.6 | 0.085 | -0.872 | 8929.5479 | 8929.5499 | -0.002
Station | Plus |  |  |  | Instrument | Minus |  |  |  | Observed | Design | Delta | Comments
| Stick | Scale | Mic | Correction | Height | Stick | Scale | Mic | Correction | Height | Height
Floor Observations / Heights Upper Linac (Spur) Tunnel, pre-MTA Enclosure,
198159 | 44 | 16.9 | 0.046 | 0 | 8921.6249 | [5 empty] | 8860.6789 |  | From above elev. Run
Up Left | [5 empty] | 44 | 9.9 | 0.07 | 0 | 8867.6549 | Low spot in upper LINAC spur
Up Mid | [5 empty] | 44 | 9.7 | 0.06 | 0 | 8867.8649
Up Right | [5 empty] | 44 | 9.7 | 0.05 | 0 | 8867.8749
Mid Left | [5 empty] | 44 | 9.6 | 0 | 0 | 8868.0249 |  |  |  | feet
Mid Mid | [5 empty] | 44 | 9.5 | 0.08 | 0 | 8868.0449 |  | 8868.0437 | Averaged height Upper level MTA | 739.0036
Mid Right | [5 empty] | 44 | 9.5 | 0.08 | 0 | 8868.0449
Down Left | [5 empty] | 44 | 9 | 0.07 | 0 | 8868.5549 | High spot in upper LINAC spur
Down Mid | [5 empty] | 44 | 9.2 | 0.02 | 0 | 8868.4049
Down Right | [5 empty] | 44 | 9.7 | 0 | 0 | 8867.9249
198159 | [5 empty] | 44 | 16.9 | 0.046 | 0 | 8860.6789 | 8860.6789
Station | Plus |  |  |  | Instrument | Minus |  |  |  | Observed | Design | Delta | Comments
| Stick | Scale | Mic | Correction | Height | Stick | Scale | Mic | Correction | Height | Height
Floor Observations / Heights Lower Portion of MTA Enclosure,
198159 | 39 | 3.2 | 0.093 | 0 | 8902.9719 | [5 empty] | 8860.6789 |  | From above elev. Run
Up Left | [5 empty] | 51 | 14.3 | 0.05 | 0 | 8837.6219
Up Mid | [5 empty] | 51 | 14.4 | 0.06 | 0 | 8837.5119
Up Right | [5 empty] | 51 | 14.4 | 0.06 | 0 | 8837.5119
Mid Left | [5 empty] | 51 | 14.3 | 0.07 | 0 | 8837.6019 |  |  |  | feet
Mid Mid | [5 empty] | 51 | 14 | 0.02 | 0 | 8837.9519 |  | 8837.653 | Averaged height lower level MTA | 736.4711
Mid Right | [5 empty] | 51 | 14.2 | 0.01 | 0 | 8837.7619
Down Left | [5 empty] | 51 | 13.9 | 0 | 0 | 8838.0719 | high spot in down stream left corner
Down Mid | [5 empty] | 51 | 14.4 | 0 | 0 | 8837.5719
Down Right | [5 empty] | 51 | 14.7 | 0 | 0 | 8837.2719 | low spot in down-stream right corner
198160 | [5 empty] | 0 | 8.3 | 0.059 | 0 | 8894.6129 | 8894.6209 | -0.008 | From above elev. Run
[12 empty] | 30.3908 | Averaged delta upper to lower levels (inches)
[12 empty] | 2.5326 | Averaged delta upper to lower levels (feet)