## attributes
evaporative cooler
EvaporativeCoolerType | DirectEvaporativeRandomMediaAirCooler; DirectEvaporativeRigidMediaAirCooler; DirectEvaporativeSlingersPackagedAirCooler; DirectEvaporativePackagedRotaryAirCooler; DirectEvaporativeAirWasher; IndirectEvaporativePackageAirCooler; IndirectEvaporativeWetcoil; IndirectEvaporativeCoolingTowerOrCoilCooler; IndirectDirectCombination; | DirectEvaporativeAirCooler: cool the air stream by evaporating water into air stream directly; DirectEvaporativeRandomMediaAirCooler : coolers with evaporative pads, usually of aspen wood or plastic fiber/foam; DirectEvaporativeRigidMediaAirCooler: coolers with sheets of rigid, corrugated material as the wetted surface;DirectEvaporativeSlingersPackagedAirCooler: coolers with a water slinger in an evaporative cooling section and a fan section; DirectEvaporativePackagedRotaryAirCooler: coolers that wet and wash the evaporative pad by rotating it through a water bath; DirectEvaporativeAirWasher: coolers with spray-type air washer consist of a chamber or casing containing spray nozzles, and tank for collecting spray water, and an eliminator section for removing entrained drops of water from the air;IndirectEvaporativeAirCooler: coolers that cool air stream by evaporating water indirectly and without adding moisture into the air stream ; IndirectEvaporativePackageAirCooler: On one side of the heat exchanger, the secondary air stream is cooled by evaporation, while on the other side of heat exchanger, the primary air stream (conditioned air to be supplied to the room) is sensibly cooled by the heat exchanger surfaces; IndirectEvaporativeWetcoil: has water sprayed directly on the tubes of the heat exchanger where latent cooling takes place and the vaporization of the water on the outside of the heat exchanger tubes allows the simultaneous heat and mass transfer which removes heat from the supply air on the tube side; IndirectEvaporativeCoolingTowerOrCoilCooler: the combination of a cooling tower or other evaporative water cooler with a water-to-air heat exchanger coil and water circulating pump; IndirectDirectCombination: a two-stage cooler with a first-stage indirect evaporative cooler and second-stage direct evaporative cooler; | Enum
FlowArragementEnum | CounterFlow ,CrossFlow , ParallelFlow | CounterFlow: air and water flow enter in different directions, CrossFlow: air and water flow are perpendicular, ParallelFlow: air and water flow enter in same directions | Enum
HeatExchangeArea |  | heat exchange area | m2
HeatExchangerMediaMaterials | LINK to materials
OperationTempRange | Range(minimum, maximum) | Allowable operation ambient air temperature range | Range(oC)
size | link to size
weight | link to weight
sound | link to sound
WaterRequirement | LINK to water requirement
PUMP | LINK to PUMP
connectivities
PrimaryAirInlet
PrimaryAirOutlet
WaterInlet
WaterOutlet
Performance History
WaterSumpTemp |  | water sump temperature | oC
Effectiveness |  | ratio of the change in dry bulb temperature of the (primary) air stream to the difference between the entering dry bulb temperature of the (primary) air and the wet-bulb temperature of the (secondary) air
SenHeatTranRate |  | sensible heat transfer rate to primary air flow | kW
LatHeatTranRate |  | latent heat transfer rate to primary air flow | kW
TotHeatTranRate |  | total heat transfer rate to primary air flow | kW
EffectivenessTable | link to polynomial | total heat transfer effectiveness curve as a function of the primary air flow rate
AirPressDropCurves | LINK to polynomial | air pressure drop as function of air flow rate | Pa
WaterPressDropCurves | LINK to polynomial | water pressure drop as function of water flow rate | Pa
connections
pump electricity supply (internal pump)
Subtypes
IndirectEvaporCooler
SecondaryAirInlet |  | (comments: these are ports that can be assigned with component optionally)
SecondaryAirOutlet

## Sheet3
evaprate cooler
| direct evaporative air cooler |  | cool the air stream by evaporating water into air stream directly
|  | random-media air cooler | coolers with evaporative pads, usually of aspen wood or plastic fiber/foam
|  | rigid-media air cooler | coolers with sheets of rigid, corrugated material as the wetted surface
|  | slingers packaged air cooler | coolers with a water slinger in an evaporative cooling section and a fan section
|  | packaged rotary air cooler | coolers that wet and wash the evaporative pad by rotating it through a water abth
|  | air washer | coolers with spray-type air washer consist of a chamber or casing containing spray nozzles, and tank for collecting spray water, and an eliminator sectionfor removing enterined drops of water from the air
| indirect evaporative air cooler |  | coolers that cool air stream by evaporating water indirectly and without adding mositure into the air stream
|  | indirect package air cooler | On one side of the heat exchanger, the secondary air stream is cooled by evaporation, while on the other side of heat exchanger, the primary air stream (conditioned air to be supplied to the room) is sensibly cooled by the heat exchanger sufraces
|  | cooling tower/coil cooler | the combination of a cooling tower or other evaporative water cooler with a water-to-air heat exchanger coil and water circulating pump
| indirect/direct combination |  | a two-stage cooler with a first-stage indrecit evaporative cooler and second-stage direct evaporative cooler
| effectiveness |  | the extent to wthich the leaving air temperature from a cooler aproaches the tehermodynamic wet-bulb temperature of the entering air temperature
connections
fan