|  | Department of the Interior Bureau of Land Management |  |
| --- | --- | --- |

COMMUNICATIONS SITE PLAN

CAMPBELL TRACT

ANCHORAGE FIELD OFFICE

Prepared by the United States Bureau of Land Management

Anchorage Field Office

State of Alaska

Approved: _____/s/ Mile Zaidlicz__________________________    __June 6, 2006______

Field Manager						Date

CAMPBELL TRACT COMMUNICATIONS

SITE PLAN

I.	INTRODUCTION	3

A.	Terms and Definitions	3

B.	Purpose	4

C.	Site Description	4

D.	Area Served	4

E.	Access	5

F.	Site History and Development	5

G.	Goals and Objectives of Site Management Plan	6

II.	AUTHORITY AND DIRECTION	6

A.	Authority	7

B.	Relationship to Communications Site Lease	7

III.	GENERAL RESPONSIBILITIES	7

A.	The Bureau of Land Management	7

B.	Facility Owners and Facility Managers	7

C.	FCC and NTIA/IRAC	9

IV.	AUTHORIZED USES AND USERS WITHIN A FACILITY	9

A.	Exclusive Use of a Facility By a Single User	9

B.	Use by Multiple Users	9

V.	FEES	9

VI.	General Operation and Maintenance Direction	10

A.	Unique Resource Considerations at this Communication Site	10

B.	Wiring and Grounding	10

C.	Equipment	11

D.	Cables and Transmission Line (Wave Guides)	13

E.	Radiation	13

F.	Utilities-Availability of and Requirements for:	14

G.	Sanitary Facilities	14

H.	Security And Law Enforcement	15

I.	Site Maintenance	15

J.	Inspections	16

K.	Fire Prevention and Hazard Reduction Requirements	16

L.	Access Maintenance and Restrictions	17

VII.	CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION	17

A.	Responsibilities	17

B.	Construction Methods and Resource Protection	18

C.	Construction Inspection	19

D.	New or Remodeled/Expanded Buildings	20

E.	New or Remodeled/Expanded Towers	21

VIII.	SITE ASSOCIATION/ADVISORY GROUP	21

IX.	APPENDICES	22

A.	Site Map	22

B.	Authorized Facilities	22

C.	Site Photographs	22

D.	Inspection Checklist	22

INTRODUCTION

## Terms and Definitions

The terms used in this communication site plan conform to the definitions listed in the October 27, 1995, Federal Register notice “Fee Schedule for Communications Uses on Public Lands” and clarifications provided in Bureau of Land Management (BLM) Handbook 2860-1.  In the event of a conflict, between the plan and these sources, the Federal Register notice and the BLM Handbook will govern.

The words “lease” and “lessee” as used in this plan refer to the relationship between the BLM and the communications use leaseholder, the lessee.  The words “customer” and “tenant” refer to the relationship between the lessee and the occupants in the lessee’s facilities.

LEASE – An authorization issued to a communication facility owner or facility manager, allowing for the use of Public Lands to construct and or operate a communications facility and unless specifically prohibited, to sublease to occupants in that facility.

LEASEHOLDER OR LESSEE – Facility Owner/Facility Manager

CUSTOMER – Entities that pay a facility owner, facility manager or tenant for communications services and are not re-selling or broadcasting communications services to others

TENANT – A communications user who rents space in a communications facility and operates communication equipment for the purpose of re-selling, or broadcasting communications services to others for profit.

COMMUNICATIONS SITE – An area of BLM administered public land designated through the land and resource management planning process.  A communications site may be limited to a single communications facility, but most often encompasses more than one.  Each site is identified by name; usually a local prominent landmark, such as Campbell Tract Communications Site.

FACILITY MANAGER – The holder of a BLM communications use authorization who leases space for other communication users.  A facility manager does not directly provide communications services to third parties.

FACILITY OWNER – Individual, commercial activities, organizations, or agencies that owns a communication facility on Federal land; own and operate their own communications equipment; and hold a communication use authorization.

NON-BROADCAST – This category includes Commercial Mobile Radio Service (CMRS), Facility Managers, Cellular Telephone, Private Mobile Radio Service (PMRS), Microwave, Local Exchange Network, and Passive Reflector.

BROADCAST – This category includes Television Broadcast, AM and FM Radio Broadcast, Cable Television, Broadcast Translator, Low Power Television, and Low Power FM Radio.

## Purpose

This plan is intended to be used by BLM officials administering communication uses at Campbell Tract, existing lessees, and applicants desiring a lease or a lease amendment.  The plan will be kept updated by amending pages or sections of the plan rather than issuing a revised edition of the plan.  When a revision is necessary, the plan will be amended by letter from the Anchorage Field Manager enclosing a copy of revised pages or sections.  The amendments will be consecutively numbered.

General management direction for all land use is outlined in the Alaska Southcentral Management Framework Plan dated 1980, Management Plan for Campbell Tract Facility dated 1988, the U.S. Code of Federal Regulations (CFRs) and the BLM Handbook and applicable Instruction Memoranda.  Specific direction for site management planning on designated communications site is contained in BLM Handbook 2860-1.  Primary regulations and policy pertaining to issuance of rights-of-way and leases by the BLM are found in Title 43, Code of Federal Regulations (CFR), Sections 2801- 2803 and BLM Handbook 2860-1.

Primary management of the current site is to assure integrity of the historical government-only two-way radio, meteor burst station and high frequency receiving antenna uses.

No communications site plan has ever been prepared for this site.  This plan has technical standards for better management of the Campbell Tract communications site.  This plan governs development and management of the Campbell Tract communications site and will be modified in the future as needs and conditions warrant.  Any future such uses must be designed, installed, operated, and maintained to be compatible and not interfere with the primary uses.  This site-specific plan is administrative in nature and is Categorically Excluded from further review under the National Environmental Policy Act (NEPA) (516.DM2, Appendix 1,1.7).  Any additional development of the site will be addressed in a site-specific NEPA document.

## Site Description

The site consists of four locations within the Campbell Tract administrative withdrawal which is administered by the Anchorage Field Office, and located on the east bench of Anchorage, Alaska in portions of Section 3, Township 13 North, Range 3 West in the Seward Meridian, at approximately 61º 09’ North Latitude and 149º 46’ West Longitude.  Four facilities are located on the BLM administered parcel adjacent to the Anchorage Field Office, administrative facilities, and air strip. The elevation of the Campbell Tract Communication Site is approximately 316 feet above mean sea level (msl).  A site map is provided as Appendix A.

## Area Served

This site serves the Anchorage Ranally Metro Area (RMA).  This RMA is in the 100,000 – 299,000 population zone which may be adjusted annually based upon changes in population and growth.  This information will be used for fee determination.

## Access

Access to the various facilities is via local maintenance roads within the Campbell Tract parcel.  Roads are maintained by the BLM.

## Site History and Development

Communications facilities for the BLM were first developed prior to 1968.  All facilities on the Campbell Tract are owned by the BLM. The first facilities to be developed were the two-way radio receiving and transmitting sites.  These sites are a back-up transmitter/receiver to Site Summit (Gordon Lion Mountain).  If Site Summit were to go down, BLM would have this as a back-up radio for resource folks on-site and for talking to planes landing at the Campbell Tract Airstrip.  The two-way radio receiving site (Facility 1 – “VHF Site”) was built on the east side of tract.  The receiving facility is a high frequency receiving antenna.  This building is supposed to be updated and a battery back-up installed.

The separate site (Facility 3 – “HF Site”) is a transmitting site for the receiving VHF site as well as a receiver.  It was built on the west side of tract.  This facility consists of a building and conical monopole antennae.  The conical monopole, looks almost like a tree because of the lattice tower surrounded by all the wires.  These wires could be mistaken as guy wires, but the entire set up is the antennae.  This configuration allows for a broad coverage of different frequencies; meaning a large segment of many frequencies can be carried through this one antennae.  There are four receivers and one transceiver (both receiver and transmitter).  The users of this site are Federal and the Civil Defense.  The Civil Defense is a conglomerate made-up of State, Federal, and the Anchorage Amateur Radio Group.  The purpose is to provide a transmitting/ receiving system for data communication during an emergency; however, the system is tested daily, where one user sends traffic to another user.  The Anchorage Amateur Radio Group has supplied the licenses to run the emergency system, while the federal and state governments are supplying the equipment.  This is a “cold” system; it operates at 100 watt output.

The separate locations for receiving and transmitting for the Site Summit back-up system were done in order to utilize the same frequency for both sending and receiving.

In 1978, a separate facility was authorized for a meteor burst station (Facility 2).  This is a data-only site that can communicate anywhere in the state.  There are currently five federal/state users: National Weather Service (NWS), Natural Resources Conservation Service (NRCS), Army Corp of Engineers (Corp), State of Alaska (State), and BLM.  The NWS and State receive weather reports from monitors/transmitters around the state; NRCS receives information regarding snow depth; the Corp receives river depth data; and BLM receives data from remote weather sties and sensors such as trail counters.  The data comes into the site via five antennas at the site, which make up 1500 watts of power.  This information is compiled in the building and comes out as data.  The data is sent through a DSL phone circuit to all users.  In addition, the Corp also has data retransmitted to Elmendorf.  The site is called the Meteor Burst Site because the information comes from signals that have bounced off of meteor trails.  The equipment at this site constantly sends out signals searching for others signals that would be carrying data from other monitors/data collectors throughout the state.  All towers are cold, therefore; it is safe for the public to be at the site.  The meteor burst site is very sensitive to noise.  It has been noted that the current location is picking up too much noise and interfering with it receiving data.  A new location may be necessary.

The BLM Radio shop is also a facility (Facility 4).  Most equipment are test antennas, but the grid microwave dish is the primary transmitter/receiver for Campbell Tract communications (it transmits and receives information from Site).  This microwave is also used by Coast Guard and “Customs.”  This is the primary system for radio communications to Campbell Tract, where the VHF site is the back-up if Site Summit were to fail.  The microwave carries eight channels, but has the capacity to carry 24 channels.  Currently, three of the channels are for the Coast Guard; one channel is for “Customs” (U.S. Customs and Border Patrol); and BLM uses the remaining four channels.  BLM maintains all channels even for the other federal users.  This microwave will be replaced with another grid that will be suitable to sustain upgrades to the system.  The other antennas on the radio shop are all test antennas, used by the shop when testing to see if radio equipment is functioning.  Inside the radio shop is a third back-up to the Campbell Tract radio dispatch system.  If the primary and secondary system were to fail, Southern Zone Dispatch, housed at Campbell Tract, could flip a switch and connect to this transceiver.

## Goals and Objectives of Site Management Plan

1.	Campbell Tract Site will be managed as a government-only low-power radio site.

2.	Communication equipment on Campbell Tract Site will be managed to be consistent with the intent of the administrative withdrawal for the Campbell Tract.

3.	The overall appearance of the site and the integrity of the natural environment will be improved through stringent maintenance requirements and selection of authorized paint colors.

- New development is not anticipated due to withdrawal and neighborhood constraints and concerns.

- New facilities will be developed only after appropriate site-specific NEPA analysis.

AUTHORITY AND DIRECTION

## Authority

BLM authority to authorize communications uses on Anchorage Field Office (BLM) land is granted by the Federal Land Policy and Management Act of 1976, 90 Stat. 2776 (43 U.S. C. 1761-1771) and is reflected in Title 43, Code of Federal Regulations (CFR), Sections 2801- 2803

and WO IB 98-23.

BLM authority for communications site management planning is contained in BLM Handbook 2801-1, Plan of Development.  Direction on and policy for communication use authorizations is contained in BLM Manual (BLM Manual) section 2860.

Authority for the issuance of authorizations and/or licenses for the transmission and reception of electronic radiation for communication purposes is granted by Congress and administered by the Federal Communications Commission (FCC) and/or the National Telecommunication and Information Administration – Interagency Radio Advisory Committee (NTIA/IRAC).

## Relationship to Communications Site Lease

This site plan will be incorporated into all leases now and in the future issued for this communications site and must be used in conjunction with the lease. PROVISIONS OF THE SITE PLAN ARE ENFORCED THROUGH THE LEASE. Each lessee is expected to include the requirements of the lease and the site plan into any documents, which describe the business relationship between the lessee and the lessee's tenants and customers. The lessee is responsible for enforcing those provisions.

GENERAL RESPONSIBILITIES

## The BLM retains the responsibility for:

Issuing and amending leases and existing rights-of-way to facility owners and facility managers, only for the areas actually occupied by the authorized improvements.  Granting occupancy and use of Public Lands rest exclusively with the BLM Title 43, CFR, Sections 2801-2803

- .  The issuance of a FCC license (authorization), or frequency assignment, does not authorize occupancy of Public Lands.

1.   Approving any new/modified facility(ies) at the site.

- Approving amendments to leases to qualified buyers of facilities on the site.

## Facility Owners and Facility Managers (or their designated representatives) are responsible for:

- Complying with their authorization and all sections of this Site Management Plan.

- Ensuring that all new facilities, expansions, or improvements are consistent with the Anchorage 2020 Comprehensive Plan, the future Ring of Fire Resource Management Plan; any environmental document(s)/decisions for the site; and this Site Plan.

- Ensuring facilities/equipment not complying with Federal/State/local laws/regulations/ ordinances will be removed or modified within one year of the approval of this plan.  Any modification needs pre-approval by the BLM.

- Keeping all facilities within the established limits of their authorized area.

- Providing the BLM, with the name, address and phone number for a local contact person.  The Facility Owner and Facility Manager and the contact person may be the same individual.  The contact person will be available for emergencies and will have the authority to make decisions about construction issues, facility maintenance and all equipment within the facility.

- Adhering to the terms of the Facility Owner/Manager Lease or Right-of-Way:

  - Facility Owners and Facility Managers are authorized to rent building/tower space to tenants and/or customers without prior written approval from the BLM.

  - Tenants and/or customers may not construct there own equipment shelter (building, shelter or cabinet) or antenna support structure (tower or mast).  The facility owner/manager must own all communication shelters and towers under their lease. [If that is not possible, a separate SF-299 application, cost-recovery deposit, analysis, and authorization are required.  This will also result in the use being a tenant/customer of the original lease holder in addition to being a separate facility for billing purposes.]

  - Tenants and/or customers using a facility covered by a Facility Lease/right-of-way will not have separate BLM permits to authorize the use.

  - Facility Owners and Facility Managers are responsible for complying with the terms and conditions of the Facility Lease or their valid right-of-way.  Facility Owner/Managers are also responsible for ensuring that their tenants and customers are in compliance with the terms and conditions of the Lease or right-of-way, and applicable FCC or NTIA/IRAC license terms and conditions.

  - The Facility Owner and Facility Manager may not place any unreasonable restrictions nor any restriction restraining competition or trade practices on tenants and/or customers, or potential tenants and/or customers.

- Ensuring that all communications equipment is properly installed, operated, and maintained.

- Ensuring that all communication equipment meets ANSI, FCC and BLM regulations, guidelines and standards concerning radiation limitations.

  - Monitoring radiation levels at their facility and;

  - Immediately correcting any radiation levels that are, or could be a hazard to human health. (FCC 47CFR sections 1.1307(b), 1.1310 and 2.1093) and FCC OET Bulletin 54, August 1999.

- Providing a certified copy of their use and the category of use along with the current phone numbers and addresses of all tenants and customers as of September 30 each year.  This report is due by October 15th.

- Keeping the premises around their buildings free of trash and debris.

- Placing the lessee/right-of-way holder’s name, address, phone number, and authorization number on the door of their communication site building.

## FCC and NTIA/IRAC are responsible for:

The responsibilities of the FCC and NTIA/IRAC are frequency management.  Correcting interference problems is the responsibility of the affected licensees.  The FCC and NTIA/IRAC are not normally responsible for the resolution of conflicts when the licensees or agencies are operating within the limits of the authorizations.

AUTHORIZED USES AND USERS WITHIN A FACILITY

## Exclusive Use of a Facility By a Single User

All of the original right-of-way grants at Campbell Tract were for single user facilities.  If space in the existing facilities is available, it is preferred that these facilities be utilized to their optimal capacity prior to any new facilities being authorized.

## Use by Multiple Users

Development of any new facilities, which are proposed after existing facilities are fully utilized must be designed for more than one user. This includes multiple use of buildings, towers, back-up generators, grounding systems, fuel containers, access ways and parking areas.

Facility Owners and Facility Managers are not required to lease facility space to others if they can prove to the authorized BLM officer that:

- Space is not available;

- The use is incompatible with the existing facilities;

- Additional space is needed by the facility owner/manager;

- Additional users would violate system security needs; or,

- Potential interference is not resolvable.

FEES

The BLM will charge Facility Owners and Facility Managers annual fees based on the Fee Schedule for Communications Uses on Public Lands as adjusted annually.  These fees will be fair market value for the use of Public Lands.  Since this site is within an established RMA with the population zone between 100,000 and 299,000, Zone 6 of the rental schedule, will be used for these calculations unless specifically agreed to by the authorizing officer and until populations or RMA designations change.

Fees that Facility Owners and Facility Managers may charge their tenants and “customers” are to be: reasonable (consistent with, and not in excess of, other fees for similar facilities) and commensurate with the uses and occupancy of the facilities and services provided to tenants and “customers”.

General Operation and Maintenance Direction

## Unique Resource Considerations at this Communication Site

- Currently, no special resource coordination considerations have been identified with on-site or adjacent resource values.  Should special conditions arise through the revision process of the RMP, this plan will be amended accordingly.

## Wiring and Grounding

1.	All equipment is to be installed within existing buildings and on equipment racks that are grounded and shielded.  Grounding is to be installed in accordance with accepted standards.

2.	All electrical wiring and grounding must meet the ‘National Electrical Code” and applicable estate codes.  All permanent wiring shall be installed in metallic conduit.  Surge protection shall be installed on all power distribution panels.

3.	Lightening protection “down” conductors installed upon communications towers shall be treated as “Transmission lines”.  Therefore, they shall have an insulating jacket.  Periodic bonding of the down conductor to the tower (Galvanized) steel shall be made with proper bonding connectors that are tin plated or made of brass.

4.	Each building is to have its own separate grounding system for all users in that structure.  Wherever practical, interconnection of individual grids and/or the simultaneous placement of a large sized copper ground wire with any new grounding systems that are buried on the site will be required.

5.	Site or facility grounding must be constructed of copper, with #2 AWG or larger wire or 2” or larger solid copper strap, connected to an adequate site/facility ground electrode system.  The site/facility ground electrode system shall be bonded to the power service entrance grounding electrode conductor.  Guy wires should also be grounded using manufacturers approved methods to preclude bi-metallic junction and corrosion.  All equipment on the site (buildings, towers, power units, transmitters, receivers, antennas, combiners, telephone systems, power cabinets, HVAC units, etc) must be connected to the site/facility ground by direct connection.  Electrical system ground wiring is required for electrical ground fault protection and circuit breaker coordination.  The grounding systems shall comply with applicable laws, codes and in accordance with standard engineering practice.  Below ground connections must use either an exothermic welding process (i.e. Cadweld, Thermoweld, etc.), copper wedge pressure devices (i.e. Ampact, Wrench-lock, etc.), or brazed copper connections in conjunction with a mechanical UL listed connector (to be used as a physical strength enhancement component).  Brazing by itself is not an acceptable method of bonding below earth grade (buried) communications equipment.

## Equipment

Equipment Ownership

All equipment shall be labeled with:

- The owner’s name;

- Transmitter frequency(ies);

- A valid FCC, or IRAF, authorization;

- Transmitting power output(s); and

- A current 24-hour phone contact number.

Transmitting Equipment

All transmitters will have protective devices (shields, filters, isolation components), designed into or externally installed, to prevent interference with other users.  All transmitters will meet FCC licensing requirements.

The re-radiation of intercepted signals from any unprotected transmitter and its associated antenna system will be prevented by the use of appropriate filters (wide band and narrow band broadcast transmitters).

The direct radiation of out-of-band emissions (i.e. noise or spurious harmonics) will be reduced to a level such that they may not be identified as a source of interference as defined in the FCC Rules and Regulations (e.g. Part 90.209(e)).  If site noise (electromagnetic noise) becomes an issue, noise threshold limits will be established, and amended into the Site Plan.

All transmitters not in immediate use and not specifically designated as standby equipment shall be removed.  Loads connected to circulators are to be capable of dissipating the total power output of the transmitter.

Receiving Equipment

A bandpass device (cavity, crystal filter, etc.) is recommended at the input of all receiving devices.  Cavity filters, or other protective device, may be used at receiver inputs to reduce interference.

Where duplexing is used, use of the notch type device should be avoided.  In situations where a notch type device is used, a bandpass filter must be used with the transmitter.

Tower

- Generally only one tower is authorized for each facility owner.  Facility Owners and Facility Managers may obtain permission to construct the second tower only after submitting evidence that demonstrates that their existing tower(s) is/are completely filled and full use has been made of combining systems.  When a single equipment building is required, multiple antenna support structures may need to be designed and authorized to accommodate all uses without interference.

- All towers will be left unpainted, if they are dull, galvanized steel.  Paint is required, only if they have a shiny (i.e. reflective) surface.  Only non-reflective, BLM approved dark gray to green colors will be approved unless FCC requires red/white striping.  All towers will be treated for low to non-reflectance.

- No lights, beacons or strobes will be allowed on towers (including antennas).

- The maximum tower height for this site is 50 feet.

Antennas

            - As stated, the maximum antenna height will be less than 50 feet.

            - Microwave (dish) antennas (other than ground mounted satellite dishes) will be limited to a maximum of ten (10) feet in diameter.  Smallest diameter dishes are preferred if technically feasible.

            - All antennas must meet all OSHA safety standards.  If an antenna exceeds FCC public or occupation standards (see FSS OET Bulletin 57), it will be remedied within 24 hours after measures are taken or isolated (e.g., fencing, signing, relocation, lowering power levels are all possible remedies).  Ground measurements of Radio Frequency Radiation, RFR, levels will be taken before mitigation measures are implemented.

            - Color(s) for dish antennas, or covers, must be pre-approved by the BLM.  White dish antennas and/or covers will not be approved.  Existing white dishes and covers must be repainted or replaced with grey as repairs or replacement become necessary.

            - Antennas will be treated for low to non-reflectance.

Interference

The responsibility for correcting interference problems is a matter for resolution between the permit/lease holder of the facility(ies), the user causing the interference, and the affected party(ies).  Generally, the first users on a site have seniority with respect to the resolution of interference complaints.  Senior holders have an obligation to maintain their equipment to industry standards, to operate their systems in accordance with the terms of both the FCC license and NTIA/IRAC frequency authorization, and to comply with the BLM authorization.  New users on a site must correct, at their expense, interference problems that they create.  They must cease operation of the suspect equipment until the problem is corrected.  If interference problems cannot be resolved or corrected within a reasonable time, the new use that is causing the interference may be terminated and the equipment removed.

The BLM does not have authority for correcting interference problems, but can act as a mediator to help all affected parties.  Interference problems must be coordinated with the FCC or NTIA/IRAC, whichever is appropriate.

Interference with law enforcement and/or emergency communications must be corrected immediately.  The operation of equipment covered by this Site Plan shall not interfere with United States Government radio or electronic operations already in existence on public land within two (2) miles of the site to which this authorization refers.  The user causing this interference, shall, at its own expense, take all action necessary to prevent or eliminate such interferences.  If it does not eliminate such interference within ten (10) days after receipt of notice from the BLM to do so, this use will be terminated.

If electromagnetic noise becomes an issue, noise thresholds will be established and appended to this Plan.

## Cables and Transmission Line (Wave Guides)

All new cabling will be jacketed and shielded and shall either be flexible or semi-rigid type.  Existing substandard cables will be upgraded as repairs or replacement become necessary.

Cables will be properly installed and will be strapped and fastened down.

All transmission lines (wave guides) are to be supported in accordance with manufacturer’s specifications.

Unjacketed transmission line of any type is prohibited. No transmission lines shall be left unterminated.

Double shielded braided, or solid shielded cable will be used.  No RG-8 type cable is permitted.  No connector-type adapters will be used on transmission lines.  Only correct connectors that will mate to connected devices are to be used.

## Radiation

All communications uses must meet ANSI, FCC and BLM regulations guidelines and standards concerning radiation limitations.

Monitoring radiation levels at the site is the responsibility of all site users and will occur at intervals to comply with FCC regulations and guidelines.  A copy of the monitoring report will be provided to the BLM within 30 days of its completion.

Onsite RFR measurements will be taken using appropriate equipment that can adequately measure both on-tower and on the ground levels before mitigation measures related to RFR are implemented.

Security fences with RFR notice signs are required around areas that exceed public use levels.  All fencing location and design will be pre-approved by the BLM.

Warning signs will comply with ANSI C95.2 color, symbol, and content conventions. Contact information including name and telephone number will also be included on warning signs.

Lowering power levels for on-tower access during maintenance will be coordinated between affected users.

Any identified RFR radiation problems that are, or could be, a human health hazard must be corrected within 24 hours after measurement tests have been completed or be removed from the site by the site user(s).  If the proposed corrective action involves any new ground disturbance, it must be pre-approved by the BLM.

## Utilities-Availability of and Requirements for:

Commercial Electrical Power

Commercial power is provided to the site under permit to Chugach Power.  The distribution line and portions of the service drops are aerial.  Future service drops or modifications will be buried.

Telephone Service

ACS provides the commercial telephone service to this site.

Fuel Tanks

No backup power is currently authorized at any of the facilities.  If needed in the future, the following criteria should be considered:

All facility owners are responsible for providing fuel storage (propane and diesel) and emergency power for their tenants.  No tenants will be authorized their own fuel tank and/or generator.  Fuel storage will preferably be consolidated into a tank large enough in size to accommodate all tenants by each facility owner.  At a minimum, tanks will be grouped together in a consolidated area adjacent to their facilities.  All fuel, storage tanks (e.g. LPG, propane and diesel) must meet current fire department, Federal, State and Municipality safety and hazardous materials requirements.

- All tanks will be:

a.	Signed in red letters, “SMOKING OR OPEN FLAME PROHIBITED WITHIN 20 FEET”;

b.	In conformance with National Fire Protection Association (NFPA) requirements; and,

c.	Painted an approved color, or screened by an enclosure to blend in with the natural environment.  (If an enclosure is used, it must be pre-approved and painted an approved color).

2.	Diesel tanks will also be:

a.	Enclosed in BLM and fire department approved secondary containment vaults that are painted a BLM approved color.

b.	Constructed with underground fuel lines.  Fuel line must be constructed of black, treated pipe and fittings, and must be posted.

## Sanitary Facilities

1.	Plans for any new sanitary facilities must be pre-approved by the BLM.  If it is determined by the BLM that the user needs such facilities, they will be provided by the applicant/holder in a manner and location satisfactory to the BLM and within the requirements of the Municipality Health Department.

## Security And Law Enforcement

The BLM is the key law enforcement agency for the area.  They are responsible for most civil and criminal matters.  The BLM will be responsible for enforcing matters related to uses of BLM lands (e.g. resource protection issues).

Patrol and policing for security purposes is the holder’s responsibility.  If holders desire to have the protection of extra fencing, BLM approval must be obtained first.  To reduce visual clutter and efficiently utilize existing space, fencing groups of buildings will be encouraged.

Gates must be adequate for BLM and Fire Department access needs.

Fencing

Several facilities currently have perimeter fencing.  If future facilities determine that fencing is desirable, they must meet the following criteria:

1.	All fences must meet health and safety requirements.

2.	All fence locations and design require BLM pre-approval.  The standard fencing type will be chain-link (i.e. cyclone).

3.	The standard fence height will be eight (8) feet.

4.	Fencing will be designed and of a type to minimize interference issues.

5.	Fences will be signed with RFR notices if RFR is above public levels.

## Site Maintenance

The objective of maintenance activities is to present a clean, neat, and orderly appearance at the site and have all of the authorized improvements safe for workers and the public.  All users will keep up the overall appearance of the site.

Miscellaneous debris remaining after any construction and/or equipment installation, removal or modification, is not only a hazard, but can cause interference or intermodulation problems.  In particular, all loose wire or metal objects are to be removed from the site.

The users of the Site will remove all graffiti within 10 working days of finding it.  If graffiti is on natural features (e.g. rocks), the graffiti will be removed in a method approved by the BLM Authorized Officer.

Holders will not be permitted to leave or dispose of trash, garbage or cut brush on public lands.  No outside trash or litter containers will be provided.  Site users (i.e. holders) will remove litter from the site as it is produced.

Policing of litter in common areas (i.e. areas between buildings and developed sites) is the shared responsibility of those holders bordering these areas.

During construction and/or maintenance, paintbrushes will not be cleaned off on the rocks around the site and excess materials (e.g. cement) will be removed from public lands.

Peeling paint on buildings and/or towers will be re-painted within ten (10) days of notification of the holder by the BLM.

## Inspections

Unless waived in writing by the BLM, the holder is to provide, annually, a certified inspection of the facilities and equipment covered by the authorization.  The inspection will include technical review that assures that authorized equipment is operating within the specifics of this Site Plan, the FCC authorization, ANSI Standards, and the manufacturer’s specifications.  In addition, the inspection must assure that the authorized equipment is secure, free of rust, properly grounded, and otherwise properly operated and maintained.  This inspection should also review general good "housekeeping". A copy of the inspection report, certified by a telecommunication specialist, is to be provided to the BLM within 30 days of completion.  Appendix D provides an example of the inspection checklist.

The BLM may also conduct un-announced periodic reviews to monitor for authorization compliance.

## Fire Prevention and Hazard Reduction Requirements

Facility owners and managers will be required to maintain to mineral soil, a minimum of thirty (30) feet clearance around their buildings and a minimum of ten (10) feet clearance around any propane tanks.  Identified threatened, endangered, or sensitive plant species must remain within the minimum clearance areas.

Smoking is prohibited while walking in flammable vegetation.

The roof structure shall be kept reasonably clear of leaves, twigs, and other debris at all times.

No explosive will be stored at this site.  Flammable materials shall be stored in conformance with the requirements of local fire regulations.  Flammables will be placed in closed containers and stored away from sources of ignition and combustible materials.  If flammables are stored within a building, the building will be locked, properly signed and well ventilated.

Approved spark arresters will be required and maintained on all internal combustion engines.

At least one (1) U.L. rated 4 B:C dye chemical fire extinguisher is required inside each building.  Prior to each June, fire extinguisher(s) shall be inspected and refilled by holders, if necessary.

Any fire will be immediately reported to “911”, the nearest BLM office or the Municipal Sheriff.

Periodic fire prevention inspections are made by BLM Officers.  They will call to your attention any lack of compliance with the above regulations, plus any other existing hazards.  Compliance with these inspections is required within the time limits specified.

All fire protection standards must be accomplished by the beginning of fire season unless otherwise agreed to, and then maintained throughout the fire season.

For new construction, the BLM will provide the Holder with a separate Construction Fire Plan which will be prepared at that time as applicable.

## Access Maintenance and Restrictions

Roads

The access road to the facilities is on local roads maintained by the BLM.

Holders who damage or disturb the access road, or any associated structures, such as ditches, culverts, roadside vegetation, signs and/or underground utilities or facilities, will be required to repair the road or associated structures to conditions equal to or superior to those prior to any damage or disturbance.  These actions may require a new NEPA analysis.

Interior Site Driveways/ Parking Areas

Roads within the communications site will be maintained by the site users.  Interior roads will be planned and approved during establishment of new facilities.  Interior roads will be maintained in a manner to allow only one entrance to the site.  The intent is to discourage off-road vehicle use in and around the site.

Road Closures

Native surface roads are subject to periodic closures to entry during periods of extreme fire danger, inclement weather, or wet conditions.  Authorized site users may use the site during these periods, but should use judgment and may need to seek advance approval from the BLM.

CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION

## Responsibilities

In addition to the responsibilities listed in Section III, New Facility Owners and Facility Managers are responsible for:

1.	Submitting a complete application to the Anchorage Field Office prior to any new construction, or modifications to existing improvements (ATTN: “Realty Specialist”).  The application must include:

a.	Submitting the appropriate Cost Recovery fees in connection with the application.

b.	A copy of the approved Site Plan Base Map showing all of the proposed (new) facilities including structures, towers, and auxiliary equipment;

c.	Completed drawings/plans prepared by a registered engineer and approved by the BLM;

d.	Identification of any microwave beam paths, a plot of their azimuth(s), and their proposed elevation(s) on the tower;

e.	All proposals must include documentation that shows that proposed facilities will not be obstructing, or interfering with, any existing fixed point to point antennas, omni directional broadcast antennas, or microwave beam paths in the directions of primary population targets.  Proposed beam path needs must be shown on Site Plan Base Map; and,

f.	Any needed recommendations, changes or modifications to their original proposal, based on any required resource surveys and/or reports.

2.	Demonstrating that their proposals will not cause undue interference with any existing uses before new facilities can be approved by the BLM.  In addition, it is the applicant’s responsibility to show that any new facilities will make the most efficient use of the limited amount of space at the site.

3.	Showing that their proposals will provide for future users without additional construction are encouraged.

4.	Providing engineering and geotechnical investigations for development of specific foundation designs and grading plans.

5.	Providing an Erosion Control Plan prior to construction activities.  At a minimum, the Erosion Control Plan must include: sediment control, stipulations that cut/fill slopes will be graded and contoured to prevent erosion and/or excessive runoff, and recommendations for temporary erosion control measures, (e.g. netting, silt fences, swales, and/or sediment collection areas).

6.	Coordinating with other Federal (e.g., FCC and FAA), State and Municipal agencies and obtainment of all required approvals and/or permits.

7.	Providing 30-day notice to all facility owners/managers at the site, as well as the BLM, of all new frequencies proposed for the site.  A completed BLM technical data sheet or equivalent must be sent with the 30-day notice to allow for comment of potential interference.  This would be for new frequencies for themselves and their tenants.

8.	Insuring that all written approvals have been obtained from the BLM prior to construction.  In addition:

New and/or modified facilities will not obstruct existing fixed point-to-point antennas or omni-directional broadcast antennas in directions of primary population targets.

## Construction Methods and Resource Protection

Plans submitted by an applicant for any new construction or modifications shall specify provisions for soil rehabilitation measures including, but not limited to, soil replacement and stabilization and for proper handling of runoff from buildings, parking area, access roads, and undeveloped common areas.

The following methods and resource protection measures will be required to minimize impacts during construction:

1.	Avoid and protect sensitive resource areas, as identified by the BLM.

2.	Compliance with the Erosion Control Plan.

3.	During construction and/or maintenance, paintbrushes will not be cleaned off on rocks around site and no marks of any kind (including survey marks) will be permitted on rocks.

4.	Minimize ground disturbance and vegetation removal as much as possible during construction activities.  All ground-disturbing activities require BLM pre-approval.

5.	Any extensive cut and fill slopes will be re-vegetated with vegetation species approved by BLM as soon as possible after construction.  All re-vegetation requires BLM pre-approval. If necessary, reseeding will be required until vegetation is successfully established as determined by the BLM.

6.	No grading material will be cast off during construction/reconstruction activities. Excess soil can be used for fill material on road and/or building/tower pads.

7.	Temporary, on-site storage of construction materials will require pre-approval by the BLM.

8.	Construction materials and supplies, except for hazardous materials (see number 9 below) may be left unattended at the construction site at the end of each workday, but at the owner’s risk.

9.	Hazardous materials, including, but not limited to all fuels, oils, and lubricants are not to be left unattended at the site at any time.  During construction, these materials are to be removed from the site at the end of each workday, or temporarily stored inside a locked and signed building until the following workday.

10.	All surplus construction materials and/or waste debris must be removed from the site no later than thirty (30) days after construction has been completed.

11.	Any earth moving or heavy equipment (e.g. dozers, graders, cranes, backhoes, etc.) leaving the designated roadway and/or approved parking area(s) to perform authorized activities at the site, will be washed off prior to being brought onto public land to prevent the introduction and spread of noxious weeds into the area.

## Construction Inspection

1.	All new construction, reconstruction, or major modification shall conform to the established technical standards and accepted engineering practices (i.e., the Uniform Building Code).

2.	Any construction inspections required by other applicable agencies are the responsibility of the holder.  Copies of completed inspections are to be provided to the Field Manager, either as they occur or as part of the final as-built plan.  Inspection information shall become a permanent part of the proponent’s authorization file.

3.	The Holder agrees that corrective work detailed in BLM, or other agency required compliance inspections, would be completed by the scheduled completion date.  If the Holder disagrees or has questions about specific items, the Holder must contact the BLM in order that the disagreement or item may be resolved.

4.	A final set of as-built plans will be submitted to the Field Manager within 90 days of acceptance of structure (if contracted) or of completion date.

## New or Remodeled/Expanded Buildings

- Any new buildings must be designed to accommodate multiple users along with fitting into the physical environment as defined in a site-specific environmental analysis developed at the time of the proposal.

- Buildings are required to be one-story, flat roofed.  The roof must be metal or covered with metal to be fire resistant.  Roofs can be equipped with antenna support structures, such as poles and railings that can extend up to 25-feet above ground level.

- Facility Owners and Facility Managers are encouraged to construct the interior of their buildings in a modular fashion, so that they can:

a.	Sublease sections to others;

b.	Provide tenants and customers with internal separation and security;

c.	Reduce physical interference; and

d.	Increase management effectiveness.

- The following materials are approved for construction of new facilities (i.e. buildings)

#### a.	Floors – Concrete slab with drainage.

b.	Walls – Concrete block, pre-fabricated concrete, or other pre-approved fire resistant materials.

c.	Roof – Metal, concrete, or other fireproof material as approved by the BLM.  These should be painted to eliminate shiny surfaces, per BLM approved dark gray to green colors.  Proposals for wooden roofs will not be approved.

d.	Partitions – If it is felt partitions are necessary in buildings, ensure they are constructed with fire resistant material (e.g., concrete block, reinforced concrete, or properly grounded expanded metal.

e.	Color – Proposed color for use on all exterior building surfaces must be pre-approved by the BLM. The goal of the color selection for the facilities is to make the building as inconspicuous as possible and make buildings located on the skyline look inconspicuous when viewed from a distance.  The intent is to reduce or eliminate glare from reflective and/or illuminated surfaces such as windowpanes, sheeting and reflective paints.  Non-reflective, BLM approved dark gray to green colors will be used on equipment buildings.

f.	Pre-fabricated equipment shelters which meet the above requirements may be approved.

- Building entry lights must:

a.	Only light the immediate area in the vicinity of the door;

b.	Be motion activated and have a limited time duration (e.g., 3-5 minutes); and

c.	Have a shielded beam that is pointed at the building door.

Requests for all-night (i.e. “dusk-to-dawn”) lighting, or entry lighting that would be visible from outside of the site will not be approved.

## New or Remodeled/Expanded Towers

- All new construction, reconstruction, and modifications to towers will be pre-approved by the BLM prior to implementation.

- It is the applicant/holder’s responsibility to assure that a new, or modified, structure will not unduly interfere electronically or physically with any existing equipment at the site.  Towers must be spaced, so as to prevent ground level radiation and/or interference problems.  This must be clearly demonstrated in writing to the BLM prior to issuance of a lease, permit, or amendment.

- All new towers will comply with current structural and safety specifications and design standards, including safety-climbing devices.  Towers should be as narrow and “open” as safety and structural integrity allow.  New towers will be designed using maximum wind, snow, and/or tower loading anticipated for the site.

SITE ASSOCIATION/ADVISORY GROUP

A Site Association is not recommended for the Campbell Tract Communication Site.  If formed in the future, the Site Association would be responsible for obtaining and maintenance of an administrative access and upkeep of internal roads and parking areas.  The Site Association would also be responsible for ensuring cooperation between users for on-tower access.  A Site Safety officer would be identified within the Site Association. The Site Association would be expected to develop a Radio Frequency Radiation Plan/Agreement and recommend measures to reduce interference issues (e.g., through use of filters).

The goal of the Site Association would also be to maximize the effective use of the site.  The objective of a sanctioned association will be to represent all site users as a group when dealing with the Anchorage Field Office on matters relating to the Site administration.  The association would be able to work in cooperation with the BLM (BLM), and the State of Alaska to identify problems or opportunities and make recommendations to these agencies for any changes in management strategies at the site.  The association could also provide input to these agencies regarding the future addition of equipment and facilities at the site. While the advice and recommendations of the association would not be binding on these agencies, they could use the input for administration of the site.  The BLM and State of Alaska would be a member of such a group and would help jointly develop the charter (i.e., the ground rules).

In the absence of a formal Site Association, the BLM may utilize a Site Advisory Group that can make suggestions and/or recommendations to specific problems associated with the administration of the site.

APPENDICES

## Site Map

## Authorized Facilities

## Site Photographs

## Inspection Checklist

APPENDIX A

SITE MAP

APPENDIX B

LEASEE FACILITY TABLE

(See associated User’s Table on this Website)

|  | Auth # | Use | Building | Tower | Access/Parking | Other |
| --- | --- | --- | --- | --- | --- | --- |
| Facility 1 “VHF Site” BLM Two-way Radio | AKAA 077728 | PMRS | 10’x 12’ pre-fab | 35’ H frame wood 35” wood pole | Access and parking |  |
| Facility 2 BLM “Meteor Burst Site” | AKAA 14262 | PMRS | 12’x 30’ metal | 5 - 35’ guyed | Access and parking |  |
| Facility 3 “HF Site” BLM Receiver Anchorage Amateur Radio Club | AKAA 077728 AKAA xxxxxx* | PMRS OT | 10’x 12’ prefab | 50’ guyed high frequency receive antenna | Access and parking |  |
| Facility 4 BLM Radio Shop | AKAA xxxxxx* | PMRS | South end of maintenance bldg | 2 - 45’ lattice 1 – 35’ lattice | Access and parking |  |

* The use by the Anchorage Amateur Radio Club must be authorized under a communication use lease and the BLM Radio Shop use must be authorized under a right-of-way grant for communication purposes.

APPENDIX C

SITE PHOTOGRAPHS

BLM Facility 1

BLM Facility 2

BLM Facility 3

BLM Radio Shop

APPENDIX D

“Campbell Tract Annual Technical Inspection”

Date Inspected: _____________________________   	Time Inspection: ________________________________

Permit Holder: ______________________________  	Authorization # _________________________________

Site Technician : ____________________________   	 Phone # _______________________________________

Number of Transmitters ______________________   	 License Posted _________________________________

Please mark the following Items as Acceptable (A) or Unacceptable (U).

Electrical Wiring ------------------- (A)     (U)        	Grounding --------------------- (A)     (U)

Equipment Installation ------------ (A)     (U)	Housekeeping ----------------- (A)     (U)

Building Repair -------------------- (A)     (U)	Tower Repair ------------------ (A)     (U)

Please mark the following Items as Yes (Y) or NO (N) or (NA)

Isolators ---------------------------- (Y)     (N)     (NA)	Circulators --------------------- (Y)     (N)     (NA)

Cavities ----------------------------- (Y)     (N)     (NA)	Terminators -------------------- (Y)     (N)     (NA)

Filters ------------------------------- (Y)     (N)     (NA)	Lightning Protection ---------- (Y)     (N)     (NA)

Comments: __________________________________________________________________________________

____________________________________________________________________________________________

Recommended Corrective Action:  ________________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

Required Corrective Action To Be Taken:  __________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

Committee Representatives:  _____________________________________________________________________

Bureau of Land Management Representatives: _______________________________________________________

Please make the required corrective action within the next 120 days.

Please make a written report of corrective action taken and submit to the BLM in Anchorage.  If you should have any questions, please call the Anchorage Field Office at (970) 267-1246.

# Footnotes

Site Summit.  This is a communication site on military land.  BLM has equipment on Site Summit as do other federal agencies.

Cold.  Radio frequency factor does not exceed the threshold for general public safety.