STATEMENT OF WORK

FIRE DETECTION AND ALARM SYSTEM

MANUAFACTURER TECHNICIAN SUPPORT FOR INSTALLATION ONBOARD THE U.S. MARAD VESSEL

NS SAVANNAH (NSS)

TABLE OF CONTENTS

Section

1.0 Background

2.0 Scope of work

3.0 Task Requirements

4.0 Final Acceptance/Deliverables

5.0 Government Furnished Equipment / Government Furnished Materials

6.0 Production meetings and schedules

List of Tables:

Table 1, Overall Contract Schedule of Milestones and Deliverables

List of Attachments (provided electronically):

Attachment 1, Fire Alarm Installation Specification

Attachment 2, Installation Drawing Set:

Fire Detection and Alarm:

401-1002, Fire Detection and Alarm System, rev. B.

Attachments 1 and 2 are hereby incorporated by reference into the SOW.

List of Submittals/schedules are identified in individual specifications.

1.0 BACKGROUND

The Volpe National Transportation Systems Center (Volpe Center) provides project management and marine engineering support to the Maritime Administration (MARAD).  MARAD is owner and custodian of the Nuclear Ship SAVANNAH (NSS). Conceived in the 1950's as part of President Eisenhower's "Atoms for Peace" program, the NSS was designed, constructed and operated as a joint research and development project of the Maritime Administration and the Atomic Energy Commission (AEC). MARAD's contribution was the ship, the AEC's was the reactor and related nuclear systems. The reactor was first brought to power in 1961, with seagoing trials following in 1962. The AEC ended its participation in the project in about 1965, transferring liability and title of the reactor to MARAD. NSS was operated in experimental and commercial demonstration service throughout the 1960's. Having completed its research and development objectives, the ship was removed from service in 1970. When alternative uses for the ship failed to materialize, its nuclear power plant was de-fueled, partially decommissioned and prepared for long-term lay-up.

From 1981 to 1994 the vessel was bareboat chartered to the Patriots Point Development Authority, Charleston, SC for public display. The NSS charter was terminated by mutual agreement in 1994. The vessel was placed in MARAD's James River Reserve Fleet for long-term retention.

MARAD began assessing and evaluating possible course of action for radiological decommissioning. In the post 9-11 environment, MARAD made assessments of the physical vulnerability of the ship and plans for total decommissioning of the ship with potential use as a museum and is presently registered as a National Historic site.

In support of MARAD’s mission the Volpe National Transportation Systems Center (Volpe Center) is providing this Statement of Work (SOW) to install a new Fire Detection and Alarm System (FA) (Task 1).

2.0 GENERAL REQUIREMENTS

The contractor shall provide all the labor, materials, and be a duly authorized representative of the Fire Alarm Manufacturer to install and terminate all the fire alarm devices, associated equipment, panel hook-ups, test, commissioning and training for the fire detection and alarm system per the drawing.  The contractor shall be responsible to procure and install all the speaker strobe devices, smoke and heat detectors, pull stations, panels (primary and remote), and ancillary electrical components per drawing 401-1002 for Fire Alarm system for loops 2, 3, 4, 5 and 6, and C deck area of library/documents storage/Battery Room.  Under a separate Government contract, electricians will install the rough wiring and will be properly identified.  C deck area includes the three (3) documentation storage rooms that encompass the breadth of the vessel on C deck.  The contractor shall warranty the fire alarm (FA) components and related installation of devices/components for 1 year from date of Government system acceptance.  The contractor shall participate in the planning/ship check meeting at the front end of the job with the Volpe Center COTR, determine locations of all devices, prior to the installation of wiring by others.  The contractor shall provide final as-built drawings in electronic and hard copy formats, redlined wiring installs will be provided by the wiring installers to be incorporated by the contractor with devices, panel wring details, etc.

The contractor shall identify the proposed manufacturer of the fire alarm equipment, provide a complete list of all fire alarm components, panels, and makes/models/part numbers/quantities required to be supplied with the solicitation proposal submittal.  In addition, provide component cut sheets for Volpe review and provide fire alarm technicians qualifications (mfg. Certifications/NICET certifications). The contractor shall identify/verify manufacturers FA wiring (type/style/size) required, including the listed metal wire molding and backing boxes for purchase by the government.  FA wiring and any metal raceway (metal wire mold) will be procured by the government.  Refer to the drawings for the FA materials.  All amplifiers shall have an additional 50% capacity for anticipated future installation of additional speakers.  FA panels shall be installed by the FA contractor, the panels will be roughed-in under separate contract.

The Fire Alarm Contractor shall demonstrate at least three similar projects in scope and size onboard ship, including references and points of contact. The contractor shall provide the proposed workers names, titles, experience levels and NICET certifications.

The Fire Alarm Contractor shall install system hardware, and equipment per Attachment 1 (Fire Detection and Alarm System).  The Government will provide seven (7) days notification prior to the scheduled installation date for the purpose of planning, vessel ship-check, submittals for government approval and ordering of materials.  Completion of onboard work shall be accomplished on or before a (2) two consecutive calendar week duration; this schedule includes allowing 2 days for government inspections and functional testing.  The installation start date for the electrical wiring work by others will be on or about October 6th, 2008.  The vessel will be available for contractor workers, a minimum of regular duty hours for 8 hours per day, 5 days per week.  Additional daily hours and weekends may be requested with prior approval of the Contracting Officer.

Note – Installations shall follow the guidance design drawings to the greatest extent feasible (Note - proposed Kidde panel is no longer in production, contractor shall propose an alternative marine listed panel and remote panel).  Any major deviations shall be identified during the proposal submittal.  Any additional changes to the scope of work/materials during the project must be approved by the Contracting Officer.

Within 14 days of notification to proceed from the Contracting Officer the FA Contractor shall conduct the ship-check of the vessel with the Volpe COTR and Volpe contracted electricians.  The ship-check objectives are to co-ordinate/plan the work installation, mark the device locations, interference issues, and to determine any unforeseen problems (major deviations) which may affect the overall design/installation.  The Contractor shall provide a written ship-check condition report and red lined drawings within five (5) days of the ship-check to the COTR, and identify any problems found and proposed solutions, as necessary.  An example of a minor deviation is defined as moving a device a few feet to accommodate interference issues, examples of a major deviation is proposing alternate device make/models, redefining a loop configuration, etc.

Installations shall meet all of the requirements of the installation specifications, detailed design drawings, to include system functional testing prior to acceptance by the Volpe COTR.

The Contractor shall provide all labor, tools, and installation consumables required to successfully install and program the system devices and fire alarm hardware/electronics and materials, according to this Statement of Work (SOW), the attached installation specifications (Fire Detection and Alarm) and detailed fire alarm design drawing set.  This scope of materials includes all incidental items such screws, nuts, bolts, tie backs, nameplates, wire identification tags, paint, etc. not disclosed on the Bills of Materials/Drawings.

The vessel is located dockside at:

Vane Brothers, Canton Marine Terminal, Pier 13

4601 Newgate Ave

Baltimore MD  21224

The Contractor shall adhere to “good housekeeping practices”.  All daily trash removal, equipment removal, etc. shutdown of lighting, etc., shall be performed daily by the contractor in the presence of the Volpe COTR before leaving the vessel.  The contractor’s work force shall be aware of and comply with the Savannah’s Health and Safety Plan, Fire Prevention Plan, emergency equipment locations, designated shore side smoking areas, and fire safety procedures for the vessel while working aboard and is readily available onboard the vessel.

3.0 TASKS:

Fire Detection and Alarm System (FA):

Refer to the Fire Detection and Alarm Specification and Drawings.

The fire detection and alarm installation for lay berth will cover occupied areas of the A-deck and above, including associated stairwells, passageways and portions of B-deck aft of the Reactor Space. The following loops (2, 3, 4, 5, and 6) shall be installed at this time as shown on drawing No. 401-1002. (This includes a partial loop that covers C deck technical library area and shall include protecting these 3 documents storage areas encompassing the breadth of the vessel plus the battery room.)  Note - this work onboard Savannah will be accomplished in non-radiation areas.

Fire Detection Alarm System (FA) Equipment and operation:

The equipment shall be similar to a marine listed Kidde Fenwal (FenwalNET 2000) Fire Alarm and Detection System or equal.  It will be a Multi-Loop System, Class A computerized, and programmable system.  The equipment shall be U.S. Coast Guard approved, NFPA, and UL listed for marine use.

The FA System shall be powered by a 120VAC power source via a 120/120VAC Isolation Transformer (transformer to be installed by Volpe contracted electricians under separate contract).  The Isolation Transformer shall prevent power spikes from damaging the Alarm Panel internal components.

The ship shall be alarm zoned into specific fire zones (loops).  Each zone will be alarmed so as to notify the area where a fire is located and other areas that would require evacuation through that alarmed area.  Should it be necessary to evacuate the entire ship, a Master Pull Station shall be activated, alarming the entire ship.  The Alarm Panel, Master Pull Station, Battery Back-up Enclosure and required accessory panels, shall be located in the Security Office on A-Deck, as shown in drawing 401-1002.  There shall be a speaker microphone at the panel and speaker strobes located throughout the ship in accordance with NFPA 72, Fire safety Codes and guidance drawings.  The contractor shall provide recommendations for programming the system, voice commands and discuss with Volpe COTR.

Heat Sensors shall be installed in all compartments where smoke and/or fumes/vapors could be present under normal conditions and inadvertently activate a Smoke Detector.  Smoke Detectors shall be installed in all other areas of the ship, as required.  Refer to guidance drawing.

There will be areas of the ship where the type of sensor initially installed shall require replacement as conditions change. Areas where there will be industrial smoke caused by welding and burning will initially require a Heat Sensor and later could require a Smoke Detector, depending on the final disposition of that compartment.

Manual Pull Stations shall be installed at all means of egress.

Should there be a loss of power, battery back-ups shall be installed to maintain the Fire Alarm System in operating condition for a minimum of 24 hours in stand-by operation followed by 5 minutes of alarm activation as required by NFPA 72- 1996 or later.

The contractor shall maintain a daily redlined as-built drawing of the fire alarm components installed during work progress.

4.0	FINAL ACCEPTANCE/DELIVERABLES

Work acceptance by the government will be based on compliance with this SOW, the installation specifications, detailed design drawings and successfully passing the Functional Test requirements (as detailed in the installation specification).

Warranty:  Provide 1 year warranty applies to all labor, material (FA components/panels installed), and complete fire detection and fire alarm system installation.

Deliverables:

- Contract submittals for evaluation of components, panels, quantities, cut sheets

- Contract submittal qualifications, certifications

- Participate in ship check planning review with Volpe/electricians, confirm locations of devices

- Shop drawings of proposed panel, sequence of operations matrix recommended

- Specified new FA materials/FA component installation, wiring hook ups

- Programming panels

- Start-up/testing/commissioning system, include test plan, test report

- As-built drawings (Volpe to provide wiring redlines), 6 paper copies drafts/finals + electronic CAD

- Training

- O+M manuals, 6 paper copies drafts/finals + electronic CAD

- Spare parts identified per the FA specification and guidance drawing

- 1 year warranty on FA components/hook ups

- Troubleshooting call ins (warranty period)

- 6 month and first annual recertification testing/inspections

- GOVERNMENT FURNISHED INFORMATION/MATERIALS:

The following electronic copies are included as part of the solicitation:

1.   Installation Specifications as Attachment 1.

2.   Detailed FA Design Drawings as Attachment 2, AutoCAD.

3.  FA wiring material, metal molding, backing boxes and installation

6.0	PRODUCTION MEETING and SCHEDULES

The contractor’s fire alarm technicians shall participate in a 15 minute daily briefing held onboard the subject vessel with the COTR and any MARAD representative.  At the beginning of each day (0730) to discuss areas of work and any lockout/tag out, etc.

# Table 1 - Contract Schedule

| ## Task | ## Period of Performance |
| --- | --- |
| Pre-installation Ship check | NLT 14 days after purchase order award (co-ordinate with Volpe COTR and rough-in electrical contractors) |
| Ship-check report identifying any discrepancies. | NLT 5 days after ship check |
| DRAFT Shop Drawings | NLT 14 days after ship check (Note - shop drawings required only if major deviations are proposed). |
| Final shop Drawings | NLT 7 days after government review |
| Installation schedule | NLT 7 days prior to installation start date in MS Project |
| Daily briefings | Daily at 0730 onboard vessel (M-F). |
| Inspection, Functional Test and Acceptance by Volpe/MARAD | At completion |
| Draft/Final Functional Test Plan | 2 and 3 weeks after ship check |
| Functional test report. | 5 days after completion of testing |
| As-built drawings | NLT 14 days after completion of installation work |
| Draft/Final O+M Manuals | Draft 7 days prior to training date for Government review |
| Training Plan | Draft 7 days prior to training date for Government Review |

Note - refer to the FA Specification for detailed submittal requirements at time of bid.

INSTRUCTIONS, CONDITIONS AND NOTICES TO OFFERORS

This Request for Quotation is a solicitation expected to result in a single award, subject to receipt of an acceptable proposal. The Offeror’s written proposal for the proposed Statement of Work (SOW) must include the following two (2) components:

1. PRICE PROPOSAL

The contractor shall provide a total proposed price for CLIN 0001.

2. TECHNICAL PROPOSAL

The Offeror shall provide a description of related work experience.  The technical proposal will be evaluated in terms of the following:

- Technical experience in the areas of marine Fire Alarm installations.

Any proposal that does not include the two (2) components specified above shall be considered non-responsive.

AWARD CRITERIA:

BASIS FOR AWARD – BEST VALUE

The Government intends to evaluate proposals and award a purchase order, in accordance with the RFQ.  Therefore, the offeror’s initial proposal should contain the offeror’s best terms from a cost or price standpoint.

An award will be made to the vendor whose quote, conforming to the solicitation, is determined to offer the best value to the Government in terms of 1) technical experience; and 2) the lowest proposed price.

PRICE

The Government will evaluate quotes based on the total price proposed for CLIN 0001.

ORDER OF IMPORTANCE

Technical experience is significantly equal to price in the selection of an offeror for award.  The winning proposal will be based on the following selection criteria, listed in descending order of importance:

- Proposed related work experience; and

2.   Proposed price for performing the work