Nuclear

Safety

Specialist

Qualification Standard
Reference Guide

September 2005

PURPOSE	1

SCOPE	1

1.	Nuclear safety specialists shall demonstrate a working-level knowledge of the fission process.	2

2.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the various methods to reduce exposure.	3

3.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of criticality control, safety parameters, alarm systems, and poisons.	4

4.	Nuclear safety specialists shall demonstrate a working-level knowledge of terminology used in nuclear safety analysis.	8

5.	Nuclear safety specialists shall demonstrate a working-level knowledge of the principle hazard and accident analysis methods.	16

6.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of terminology associated with probabilistic risk assessment (PRA) techniques.	21

7.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of basic heating, ventilation, air conditioning system (HVAC), and filtration system construction, operation, and application.	24

8.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of process instrumentation principles of operation as applied to nuclear safety-related systems.	27

9.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of piping and instrumentation drawings (P&ID).	30

10.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of electrical diagrams and schematics.	30

11.	Nuclear safety specialists shall demonstrate a familiarity level knowledge of electrical logic diagrams.	31

12.	Nuclear safety specialists shall demonstrate a working level knowledge of radioactivity and transformation mechanisms.	32

13.	Nuclear safety specialists shall demonstrate a working level knowledge of principles and concepts for internal and external dosimetry and dose consequences.	33

14.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the biological effects of radiation.	34

15.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the principles and use of radiological instrumentation and radiological monitoring/survey practices.	35

16.	Nuclear safety specialists shall demonstrate a working-level knowledge of 10 CFR 830.204, Documented Safety Analysis, and DOE Guide 421.1-2, with respect to its impact on Department nuclear safety.	38

17.	Nuclear safety specialists shall demonstrate a working-level knowledge of the safety basis requirements for environmental restoration and decommissioning activities.	43

18.	Nuclear safety specialists shall demonstrate a working-level knowledge of 10 CFR 830.207, DOE Approval of Safety Basis and DOE-STD-1104, with respect to its impact on department nuclear safety.	45

19.	Nuclear safety specialists shall demonstrate a working-level knowledge of 10 CFR 830.206, Preliminary Documented Safety Analysis, with respect to its impact on department nuclear safety.	47

20.	Nuclear safety specialists shall demonstrate a working-level knowledge of 10 CFR 830.202, Safety Basis and DOE-STD-1027, with respect to its impact on department nuclear safety.	48

21.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of Department of Energy (DOE) O 420.1A, Facility Safety, DOE G 420.1-1, Nonreactor Nuclear Safety Design Criteria and Explosive Safety Criteria Guide, for use with DOE O 420.1, Facility Safety, and DOE-STD-1020, Natural Phenomena Hazards Design and Evaluation Criteria for Department of Energy Facilities, with respect to its impact on Department nuclear safety.	50

22.	Nuclear safety specialists shall demonstrate a working-level knowledge of the Technical Safety Requirements as described in 10 CFR 830.205, Technical Safety Requirements and DOE Guide 423.1-1, with respect to its impact on Department nuclear safety.	57

23.	Nuclear safety specialists shall demonstrate a working-level knowledge of 10 CFR 830.203, Unreviewed Safety Question Process and DOE Guide 423.1-1, with respect to its impact on Department nuclear safety.	64

24.	Nuclear safety specialists shall demonstrate a familiarity level knowledge of the functional interfaces between safety system software components and the system level design.	69

25.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the relationships between the problems being addressed by safety analysis and design codes, the design requirements for the codes, and the components of the codes.	70

26.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of Department of Energy (DOE) Policy 450.4, Safety Management System Policy, and Policy 450.5, Line Environment, Safety and Health Oversight, as applied to nuclear safety.	70

27.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the following criticality safety-related American National Standards Institute/American Nuclear Society (ANSI/ANS) standards:	72

28.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the following Department of Energy (DOE) Orders, Technical Standards, and Notice:	74

29.	Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the Price-Anderson Amendments Act of 1988 and its relationship to subparts A and B of 10 CFR 830.	78

30.	Nuclear safety specialists shall demonstrate a working-level knowledge of the requirements in Department of Energy (DOE) Technical Standard DOE-STD-3009-94, Preparation Guide for U.S. Department of Energy Nonreactor Nuclear Facility Safety Analysis Reports and DOE-STD-3010, Airborne Release Fractions/Rates and Respirable Fractions for Nonreactor Nuclear Facilities.	79

31.	Nuclear safety specialists shall demonstrate a working-level knowledge of NSTP-2003-1 that describes the relationship between human factors/human performance and institutional programs that support the safety analysis.	91

32.	Nuclear safety specialists shall demonstrate a working-level knowledge of assessment techniques (such as the planning and use of observations, interviews, and document reviews) to assess facility performance, report results of assessments, and follow up n actions taken as the result of assessments.	93

33.	Nuclear safety specialists shall demonstrate a working-level knowledge of the Department of Energy (DOE)/facility contract provisions necessary to provide oversight of a contractor’s operations.	97

34.	Nuclear safety specialists shall demonstrate a working-level knowledge of problem analysis principles and the techniques necessary to identify problems, potential causes, and corrective action(s) associated with nuclear safety issues at DOE Defense Nuclear Facilities.	99

Selected Bibliography and Suggested Reading	103

# PURPOSE

The purpose of this reference guide is to provide a document that contains the information required for a National Nuclear Security Administration (NNSA) technical employee to successfully complete the Nuclear Safety Specialist (NSS) Functional Area Qualification Standard.  In some cases, information essential to meeting the qualification requirements is provided.  Some competency statements require extensive knowledge or skill development.  Reproducing all the required information for those statements in this document is not practical.  In those instances, references are included to guide the candidate to additional resources.

# SCOPE

This reference guide has been developed to address the competency statements in the October 2001 edition of DOE-STD-1183-2004, Nuclear Safety Specialist Functional Area Qualification Standard.  Competency statements and supporting knowledge and/or skill statements from the qualification standard are shown in contrasting bold type, while the corresponding information associated with each statement is provided below it.  The qualification standard for the NSS contains 34 competency statements.  Some of the competency statements contain performance-based requirements.  These statements will not be covered in this reference guide.

Every effort has been made to provide the most current information and references available as of September 2005.  However, the candidate is advised to verify the applicability of the information provided.

Please direct your questions or comments related to this document to Gary Gilliland, Training and Development Department at, 845-5689.

TECHNICAL COMPETENCIES

## Nuclear safety specialists shall demonstrate a working-level knowledge of the fission process.

Define the following terms:

Excitation energy

Critical energy

Fissile material

Fissionable material

Fertile material

### Excitation energy

Excitation energy is the measure of how far the energy level of a nucleus is above its ground state.

### Critical Energy

Critical energy is the minimum excitation energy required for fission to occur.

### Fissile Material

Fissile material is composed of nuclides for which fission is possible with neutrons of any energy level.

### Fissionable material

Fissionable material is composed of nuclides for which fission with neutrons is possible.

### Fertile material

Fertile material is material that can undergo transmutation to become fissile material.

Describe the curve of binding energy per nucleon vs. mass number and give a qualitative description of the reasons for its shape.

As the number of particles in a nucleus increases, the total binding energy also increases.  The rate of increase, however, is not uniform.  This lack of uniformity results in a variation in the amount of binding energy associated with each nucleon within the nucleus.  This variation in the binding energy per nucleon (BE/A) is easily seen when the average BE/A is plotted versus atomic mass number.  As the atomic mass number increases, the BE/A decreases for A > 60.  The BE/A curve reaches a maximum value of 8.79 MeV at A = 56 and decreases to about 7.6 MeV for A = 238.  The general shape of the BE/A curve can be explained using the general properties of nuclear forces.  The nucleus is held together by very short-range attractive forces that exist between nucleons.  On the other hand, the nucleus is being forced apart by long range repulsive electrostatic (coulomb) forces that exist between all the protons in the nucleus.  As the atomic number and the atomic mass number increase, the repulsive electrostatic forces within the nucleus increase due to the greater number of protons in the heavy elements.  To overcome this increased repulsion, the proportion of neutrons in the nucleus must increase to maintain stability.  This increase in the neutron-to-proton ratio only partially compensates for the growing proton-proton repulsive force in the heavier, naturally occurring elements.  Because the repulsive forces are increasing, less energy must be supplied, on the average, to remove a nucleon from the nucleus.  The BE/A has decreased.  The BE/A of a nucleus is an indication of its degree of stability.  Generally, the more stable nuclides have higher BE/A than the less stable ones.  The increase in the BE/A as the atomic mass number decreases from 260 to 60 is the primary reason for the energy liberation in the fission process.  In addition, the increase in the BE/A as the atomic mass number increases from 1 to 60 is the reason for the energy liberation in the fusion process, which is the opposite reaction of fission.

Explain why only the heaviest nuclei are easily fissioned.

The heaviest nuclei require only a small distortion from a spherical shape (small energy addition) for the relatively large coulomb forces that are forcing the two halves of the nucleus apart to overcome the attractive nuclear forces holding the two halves together.  Consequently, the heaviest nuclei are easily fissionable compared to lighter nuclei.

Explain why uranium-235 fissions with thermal neutrons and uranium-238 fissions only with fast neutrons.

Uranium-235 fissions with thermal neutrons because the binding energy released by the absorption of a neutron is greater than the critical energy for fission.  The binding energy released by uranium-238 absorbing a neutron is less than the critical energy for fission, so additional kinetic energy must be possessed by the neutron for fission to be possible.

Characterize the fission products in terms of mass groupings and radioactivity.

Fission products have some general characteristics in common.  They generally decay by emission.  The most common mass numbers are grouped near 95 and 140.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the various methods to reduce exposure.

- Describe aspects of dose reduction:

Time

Distance

Shielding

Inverse square law

ALARA

### Time

Minimizing time in an area where a radiation dose exists minimizes exposure.

### Distance

Maximizing distance from a radiation source helps minimize exposure.

### Shielding

Maximizing shielding will reduce exposure from a radiation source.

### Inverse square law

Inverse square law applies to any point source that spreads its influence equally in every direction and which doesn’t have a limit to its range.  A point radiation source can be characterized in terms of this law whether you are talking about roentgens, rads, or rem.  All measures of exposure will drop off by inverse square law, meaning the further the distance from the point source, the less the intensity of exposure.

### ALARA (As Low As is Reasonably Achievable)

ALARA is an approach in managing and controlling exposures and releases of radioactive material to the environment so that the levels are as low as is reasonable, taking into account social, technical, economic, practical, and public policy considerations.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of criticality control, safety parameters, alarm systems, and poisons.

- Discuss the effects and applications of the following factors relevant to criticality safety of operations:

Mass

Shape

Interaction

Separation

Geometry

Moderation

Reflection

Concentration

Volume

Density

Neutron absorbers

Heterogeneity

Enrichment

### Mass

The minimum masses required to attain a critical state are 500 grams of Pu and 800 grams of U.

### Shape

Limiting the size and configuration of vessels and equivalent thickness restrictions on tanks has also been a common practice in criticality control.

### Interaction

When more than one can, vessel, etc., containing fissile material is present in an area, the index of criticality (the multiplication factor) for the interacting system will be greater than if the units were isolated.  That is, a collection of units, such as a storage array, could become critical even though the individual units would be far sub-critical in isolation.

### Separation

Separation is the sorting of nuclear material based on atomic weight and mass.  This process can be performed to reclaim spent fuel or to separate materials that are mined and collected in mining operations.

### Geometry

The configuration of fissionable material within its container is referred to as its geometry.  Containers are designed to minimize the chance of material being able to configure itself into a geometry that would allow for criticality.

### Moderation

Moderation is the slowing down of neutrons from their fast-birth energies.  The fission likelihood or cross-section is several hundred times greater for slow neutrons than fast ones.  Hydrogenous materials such as water, oil, and cutting fluids are excellent moderators.

### Reflection

Reflection is the bouncing of neutrons back into a region containing fissile material by collisions with atoms in surrounding materials.  For example, a thin layer of cutting fluid on a fissile part being machined represents almost no reflection.  Immersing that same part in a bucket of water, such that there are a few inches of water surrounding it, could reduce the amount of fissile material required for criticality by about a factor of two.

### Concentration

In solutions, the concentration of fissile material has a large impact on the critical mass and critical volume.  For example, the minimum critical masses of U and Pu are about 800 and 500 grams (g), respectively, at solution concentrations of 30 to 40 g/liter.  Below 5 g/liter, infinite volumes cannot be made critical.

### Volume

Container volumes of less than six liters are often used as an aid to criticality control, particularly for solutions and loose powders which could accidentally become flooded.

### Density

Density is a measure of the spacing between atoms.  Obviously, the greater the spacing, i.e., the lower the density, the greater neutron leakage will be.  However, for low density powders and cutting chips which may have a critical mass in excess of 100 kilograms fissile when dry, the critical mass may drop to about one kilogram during accidental flooding scenarios.

### Neutron Absorbers

Neutron absorbers refer to other materials that play a dominant role in absorbing neutrons but do not fission.  Boron, cadmium, and gadolinium are examples.  Neutron poisons are most common in solution processing such as in a boron-epoxy loaded stirrer rod in a precipitation vessel.

### Heterogeneity

Heterogeneity refers to an alloy or solution containing different fissionable materials.  Heterogeneous materials typically have a higher critical mass than do homogenous materials.

### Enrichment

Enrichment refers to the fissile content of uranium, the most common being 93 percent, U(93), in which 93 out of 100 atoms are of mass 235, the remaining 7 being of mass 238.  For plutonium, the convention is the opposite; the enrichment is the non-fissile (Pu) content.  Most plutonium is about 94 percent Pu-239 and 6 percent Pu-240.

Discuss the influence of the presence of non-fissionable materials mixed with, or in contact with, fissionable material on nuclear criticality safety.

Non–fissionable materials affect the ability of the fissionable material to reach potential configurations that could lead to a criticality.  The greater the amount of non-fissionable material present, the lesser the chance of a criticality for the fissionable material.

Discuss the concept of contingencies for checking the validity of criticality safety limits.

Process designs shall incorporate sufficient factors of safety to require at least two unlikely, independent, and concurrent changes in process conditions before a criticality accident is possible.  Protection shall be provided by either (1) the control of two independent process parameters, or (2) a system of multiple controls on a single process parameter.  The number of controls required upon a single controlled process parameter shall be based upon control reliability and any features that mitigate the consequences of control failure.  In all cases, no single credible event or failure shall result in the potential for a criticality accident.

Define the following terms:

Criticality accident

Minimum accident of concern

Process area

### Criticality Accident

The release of energy as the result of accidentally producing a self-sustaining or divergent fission chain reaction is referred to as a criticality accident.

### Minimum Accident of Concern

Minimum accident of concern refers to the smallest accident a criticality alarm system is required to detect.  A criticality accident such as this would produce approximately 1015 fissions in its first minute and provide an absorbed dose in free air of 20 rad at 2 meters if no significant shielding were present.

### Process Area

A process area is any area involved in the chemical processing, mechanical processing, handling, or storage of fissionable materials.

Discuss the general principles associated with the use of criticality alarm systems including the following:

Installation

Coverage

Detection

Alarms

Dependability

### Installation

The installation of an alarm system implies a nontrivial risk of a criticality accident and emergency plans in the event of alarm actuation shall be maintained.

### Coverage

Where inventory of fissionable materials in individual, unrelated areas exceeds 700g of U-235, 520g of U-233, 450g of Pu-239, or 450g of any combination of these three isotopes, the need for criticality alarm system coverage shall be evaluated.

### Detection

Where criticality alarm coverage is required, a means shall be provided to detect excessive amounts or intensities of radiation and to signal personnel evacuation.

### Alarms

When implemented, criticality alarms shall be for immediate evacuation purposes only and of sufficient volume and coverage to be adequately heard in all areas that are to be evacuated.  They shall be capable of automatic actuation and set high enough to minimize actuation by sources other than criticality, but low enough to detect the minimum accident of concern.  Upon actuation, the signal shall be of the lock-in type and shall not reset even if the radiation levels fall below the alarm setpoint.  A corresponding evacuation alarm shall be signaled immediately following detection of a criticality accident; in addition, the evacuation alarm shall be capable of manual initiation.

### Dependability

Consideration shall be given to the detection of false alarms.  To achieve this, methods such as the use of concurrent response of two or more detectors or reliable single channel detectors shall be used.  A means (that will not cause an evacuation) to test the response and performance of the alarm system shall be provided.  Upon completion of testing, the system shall be immediately returned to normal operating condition.  Where operations continue in process areas during a loss of normal power, emergency power supplies shall be provided for alarm systems or they shall be monitored by portable alarms.  Detectors shall not fail to actuate when subject to a radiation field of at least 10 rad/second.

Describe the use of neutron poisons.

Neutron poisons are non-fissionable atoms that are effective at capturing or absorbing neutrons.  Neutrons captured or absorbed by poisons are no longer available to cause fission.

Define the following terms:

Burnable poison

Non-burnable poison

Chemical shim

### Burnable poison

A burnable poison is a material that loses its neutron absorption characteristics over time due to neutron absorption.

### Non-burnable poison

A non-burnable poison is a material that has relatively constant neutron absorption characteristics over core life.

### Chemical shim

A chemical shim is a soluble neutron poison that is circulated in the coolant during normal operation.

Explain the purpose and use of Raschig Rings as a neutron poison.

Borosilicate-glass Raschig Rings contain a form of boron, a neutron poison.  By placing several of the small glass rings (3 cm in height, 3 cm outside diameter, and 0.5 cm thickness) in a container of soluble fissile material, the borosilicate glass absorbs neutrons, but most significantly, the surface area of the fissile solution increases, increasing the probability of neutron leakage into the rings and diminishing the likelihood of a criticality accident.

## Nuclear safety specialists shall demonstrate a working-level knowledge of terminology used in nuclear safety analysis.

- Define the following accident related terms:

Accident

Authorization agreement

Authorization basis

Beyond design basis accident

Design basis

Design basis accidents

Evaluation guidelines

Safety basis

Safety analysis

Consequence

Frequency

Risk

External event

Internal event

### Accident

An accident is an unplanned event or sequence of events that result in undesirable consequences.

### Authorization Agreement

An authorization agreement is an agreement between an organization and DOE on responsibilities for a facility or area.

### Authorization Basis

The authorization basis is comprised of those aspects of the facility design basis and operational requirements relied upon by DOE to authorize operation.  The authorization basis is described in documents such as the facility safety analysis report and other safety analysis documentation.

### Beyond Design Basis Accident

A beyond design basis accident is an accident of the same type as a design basis accident, but which is defined by parameters that exceed in severity the parameters defined for the design basis accident.  The same correlation applies to beyond derivative design basis accidents with regard to derivative design basis accidents.

### Design Basis

The design basis is the set of requirements that bound the design of structures, systems, and components within a facility.  Areas included are seismic qualifications, fire protection, and safe shutdown.

### Design Basis Accident (DBA)

The design basis accident is a postulated accident that establishes design and performance requirements for systems, structures, and components that are important to safety.

### Evaluation Guidelines

The evaluation guidelines establish the hazardous material dose/exposure values that the safety analysis is evaluated against.  Theoretically, individual doses/exposures exceeding the evaluation guideline should not occur at a given point inside the evaluation area.  Offsite evaluation guidelines are established for the purpose of identifying and evaluating safety-class structures, systems, and components.

### Safety Basis

The safety basis is comprised of the information relating to the control of hazards at a nuclear facility upon which DOE depends for its conclusion that activities at the facility can be conducted safely.

### Safety Analysis

A safety analysis is a process for systematically identifying hazards of a DOE operation by analyzing and evaluating potential accidents and their risks as well as the adequacy of hazard control measures.

### Consequence

A consequence is the direct effect of an event, incident, or accident.  It is expressed as a health effect (e.g., death, injury, or exposure), property loss, environmental effect, evacuation, or quantity spilled.

### Frequency

Frequency is the ratio of the number of observations in a statistical category to the total number of observations.

### Risk

Risk is the quantitative or qualitative expression of possible loss that considers both the probability that a hazardous event will cause harm and the consequences of that event.

### External Event

An external event is an event unconnected with the operation of a facility or activity which could have an effect on the safety of the facility or activity.

### Internal Event

An internal event is an event that is part of the operation of a facility or activity which could have an effect on the safety of the facility or activity.

Define the following hazard related terms:

Hazard

Hazard categorization

Hazard category 1

Hazard category 2

Hazard category 3

Hazardous material

### Hazard

A hazard is the existence of a source of danger which could cause illness, injury, or death to personnel or damage to a facility or the environment.

### Hazard Categorization

DOE has established a process to classify facilities into hazard categories.  DOE-STD-1027 contains the flow charts which, when followed, determine the hazard classification.

### Hazard Category 1

The classification of hazard category 1 is designated when a hazard analysis shows the potential for significant offsite consequences.  This classification is primarily reserved for reactors capable of operating at a steady state power level greater than 20 megawatts (Class A reactor).  A facility may also be classified as hazard category 1 if the Program Secretarial Officer (PSO) deems it necessary.  This designation would be due to the level of off-site emergency planning required to permit operation.

### Hazard Category 2

The classification of hazard category 2 is designated when a hazard analysis shows the potential for significant onsite consequences.  A release of materials from a hazard category 2 facility would result in exposures greater than that of 1 rem at 100 meters.  Thus, emergency planning requirements are very important.  The potential for a nuclear criticality accident at a facility will also earn it a hazard category 2 classification.

### Hazard Category 3

The classification of hazard category 3 is designated when a hazard analysis shows the potential for only significant localized consequences.  Minimum threshold values for a hazard category 3 facility would result in less than a 10 rem exposure at 30 meters over a 24-hour period.  The consequences of a localized release of materials would be in excess of state and federal reporting requirements.

### Hazardous Material

A hazardous material is a substance or material that has been determined by the Secretary of Transportation to be capable of posing an unreasonable risk to health, safety, and property when transported in commerce, and which has been so designated.

Define the following safety control related terms:

Limiting conditions for operations (LCO)

Limiting control settings (LCS)

Safety limits (SL)

### Limiting Conditions for Operations (LCO)

LCOs are the limits that represent the lowest functional capability or performance level of one or more safety-related items required for the safe operation of a facility.

### Limiting Control Settings (LCS)

LCSs are the settings on process variables associated with safety systems that control the facility function and will prevent exceeding the associated safety limits.

### Safety Limits (SL)

SLs are limits on process variables associated with those passive physical barriers that are necessary for the intended facility function and that are required to guard against the uncontrolled release of hazardous materials.

Differentiate between the following categories of individuals who may be affected by an accident at a Department nuclear facility:

Off-site individual

On-site individual

Public

Worker

### Off-Site Individual

An off-site individual is any member of the public or any other individual who may not be normally assigned to or located within the subject site boundaries, and therefore would likely not be trained on site specific hazards.  The offsite area consists of the area beyond the site boundaries.

### On-site Individual

An on-site individual is any member of the public or any other individual who may be normally or temporarily located within the subject site boundaries.  This individual may not be trained on the presence of site-specific hazards.  The on-site area includes any area that has been established as a national defense area or national security area.

### Public

Public means the surrounding population of individuals not normally assigned to, or not having responsibilities in any way directly related to, the construction, operation, maintenance, or administration of a site or any facilities within a site.  This population is generally (but not always) located off-site (e.g., tours, roads, business, etc., may require the public to travel through or enter into a site).

### Worker

A worker is an individual who by nature of employment has direct responsibilities related to the construction, operation, maintenance, or administration of any site or a facility within a site.  This includes those workers who may not have direct responsibilities for a given site but may have responsibilities that result in being located within the site boundary.  Consequently, workers in general are normally associated with being on-site, but may be either on-site or off-site.

Differentiate between the function of structures, systems, and components in the following classifications:

Safety-class structures systems, and components (SSCs)

Safety-significant structures, systems and components (SSCs)

Defense in depth

### Safety-Class Structures, Systems, and Components (SSCs)

SSCs are designated as safety class if failure could adversely affect the environment or safety and health of the public as identified by the safety analysis.

### Safety-Significant Structures, Systems, and Components (SSCs)

SSCs that are not designated as safety-class, but whose preventive or mitigative function is a major contributor to defense in depth (i.e., prevention of uncontrolled material releases) and/or worker safety as determined from hazard analysis are considered safety significant.  As a general rule of thumb, safety-significant SSC designations based on worker safety are limited to SSCs whose failure is estimated to result in an acute worker fatality or serious injuries to workers.  Considerations should be based on engineering judgment of possible effects and the potential added value of safety-significant SSC designation.

### Defense in Depth

Defense in depth classification consists of two components:

Equipment and administrative features that provide preventive or mitigative functions so that multiple features are relied on for prevention or mitigation to a degree proportional to the hazard potential

Integrated safety management programs that control and discipline operations

Differentiate between the function and contents of the following documents:

Documented safety analysis

Preliminary documented safety analysis

Safety analysis report

Basis for interim operations

Technical safety requirements

Preliminary hazards analysis

### Documented Safety Analysis (DSA)

A DSA reviews the extent to which a nuclear facility can be operated with respect to workers, the public, and the environment, including a description of the conditions, safe boundaries, and hazard controls that provide the basis for ensuring safety.

### Preliminary Documented Safety Analysis (PDSA)

A PDSA is a document that is prepared in connection with the design and construction of a new DOE nuclear facility or a major modification to a DOE nuclear facility that provides a reasonable basis for the conclusion that the nuclear facility can be operated.

### Safety Analysis Report (SAR)

A SAR documents that a nuclear facility can be constructed, operated, maintained, shut down, and decommissioned safely and in compliance with applicable laws and regulations.

### Basis for Interim Operations (BIO)

The BIO is the documented establishment of allowable operations for a current facility and its operational controls until a fully compliant document is developed and approved by DOE.

### Technical Safety Requirements (TSRs)

TSRs are comprised of the limits, controls, and related actions that establish the specific parameters and requisite actions for the safe operation of a nuclear facility.

### Preliminary Hazards Analysis (PHA)

A PHA represents a level of analytical detail appropriate for preparation of safety documents for facilities.

Differentiate between the controls which have the following designations:

Mitigating controls

Preventive controls

Administrative controls

Design features

Passive controls

Active controls

Safety SSCs

### Mitigating Controls

Mitigating controls are SSCs that serve to mitigate the consequences of a release of radioactive or other hazardous materials in an accident scenario.

### Preventive Controls

Preventive controls are any SSCs that serve to prevent the release of radioactive or other hazardous materials in an accident scenario.

### Administrative Controls (ACs)

ACs are the provisions relating to organization and management, procedures, recordkeeping, assessment, and reporting necessary to ensure the safe operation of a facility.

### Design Features

The design features of a nuclear facility are those features specified in the TSRs that would have a significant effect on safe operation if altered or modified.

### Passive controls

Passive controls are nuclear criticality safety control methods that do not require human intervention or electrical or mechanical reaction to off specification conditions.  These means of control take advantage of natural forces, such as gravity, physical chemistry limitations, and inherent physical characteristics, such as rigidity and structural integrity of cylindrical geometries, and limited compressibility of solids.  These means of control include devices to prevent unsafe accumulations of fissionable material within a unit, such as siphon breaks, filters, and pipe blanks between process vessels, and spacing devices such as birdcages, racks, and stanchions between containers, as well as fixed neutron poisons, either within vessels (such as raschig rings) or between containers.

### Active controls

Active controls are the active means for ensuring nuclear criticality safety control methods.  These means of control include active electrical, mechanical, and hydraulic hardware that sense a process variable important to nuclear criticality safety and provide automatic action to secure the system to a safe condition without requiring human intervention.

### Safety SSCs

Safety SSCs are both safety-class SSCs and safety-significant SSCs.

Differentiate between the following types of facilities:

Nuclear facility

Non-reactor nuclear facility

Radiological facilities

### Nuclear Facility

A nuclear facility is a facility that conducts activities or operations that involve radioactive and/or fissionable materials in such form and quantity that a nuclear hazard potentially exists to the employees or the general public.  Included are reactors and accelerators.

### Non-Reactor Nuclear Facility

Non-reactor nuclear facilities are nuclear facilities excluding reactors and accelerators.

### Radiological facilities

Radiological facilities are facilities that do not meet or exceed category 3 threshold criteria but still possess some amount of radioactive material.

Differentiate between the following chemical terms:

Temporary Emergency Exposure Limit-1

Temporary Emergency Exposure Limit-2

Temporary Emergency Exposure Limit-3

Emergency Response Planning Guide-1

Emergency Response Planning Guide-2

Emergency Response Planning Guide-3

### Temporary Emergency Exposure Limit (TEEL)-1

The maximum concentration in air below which it is believed nearly all individuals could be exposed without experiencing other than mild transient adverse health effects or perceiving a clearly defined objectionable odor.

### Temporary Emergency Exposure Limit (TEEL)-2

The maximum concentration in air below which it is believed nearly all individuals could be exposed without experiencing or developing irreversible or other serious health effects or symptoms that could impair their abilities to take protective action.

### Temporary Emergency Exposure Limit (TEEL)-3

The maximum concentration in air below which it is believed nearly all individuals could be exposed without experiencing or developing life-threatening health effects.

### Emergency Response Planning Guide (ERPG)-1

The maximum concentration in air below which it is believed nearly all individuals could be exposed for up to one hour without experiencing other than mild transient adverse health effects or perceiving a clearly defined objectionable odor.

### Emergency Response Planning Guide (ERPG)-2

The maximum concentration in air below which it is believed nearly all individuals could be exposed for up to one hour without experiencing or developing irreversible or other serious health effects or symptoms that could impair their abilities to take protective action.

### Emergency Response Planning Guide (ERPG)-3

The maximum concentration in air below which it is believed nearly all individuals could be exposed for up to one hour without experiencing or developing life-threatening health effects.

Identify the types of chemical or toxicological hazards that may be found in nuclear facilities.

Any chemical or toxicological hazard that is included in the DSA may be present.

## Nuclear safety specialists shall demonstrate a working-level knowledge of the principle hazard and accident analysis methods.

- Identify and discuss the use of different methods for qualitative hazard analysis.  Identify specific strengths and weaknesses with the various methods.

The two primary methods of performing a qualitative hazard analysis are process hazard analysis (PHA) and failure modes and effects analysis (FMEA).  The basic outputs, however, remain unchanged.  The PHA approach uses a check list that identifies all hazards and then determines all possible incidents that may happen.  The FMEA approach identifies equipment and then proceeds to determine all possible failures or errors that may occur.  PHA is an easier system to use for someone who does not have a full understanding of all operations within a facility, such as an outside consultant.  The weakness of the PHA approach is in its generalities.  FMEA is a more thorough approach but requires a much greater knowledge of operations of that facility/organization.  Hazard evaluation presents potential accidents in terms of hazards, energy sources, causes, preventive and mitigative features, consequence estimates, and frequency estimates.

Discuss the methods used to identify and categorize the hazards associated with Department nuclear safety analysis.

The results of the hazard analysis provide a comprehensive evaluation of the complete DSA accident spectrum.  This evaluation will be essentially qualitative in that its aim is to produce a well-reasoned and clear assessment of facility hazards and their associated controls.  The focus of hazard analysis is on the completeness of consideration given to the accident spectrum, as opposed to a formalized definition of accident sequences and assumptions.  Summary discussion of methodology is appropriate, but detailed bases for judgment and any simple mathematical estimates used in the hazard analysis to guide the judgments of the analysis for specific accident scenarios are not required to be formally documented in the DSA.

The results of the final hazard categorization activity are specified in DOE-STD-1027.  This standard includes the facility hazard categorization and, where segmentation has been employed, the segment boundaries and individual segment classifications.

Identify and discuss the methods used to determine and analyze failure modes of SSCs, ACs, and control programs.

Summary methods germane to safety typically include

a general overview of safety in terms of SSCs and administrative features

identification of any safety-significant SSCs

identification of any safety management programs that will be assigned TSR coverage in the form of ACs for adequate safety

A general prioritization of the features needs to be included and expressed in terms of the magnitude of a process hazard.  A summary-level discussion is required, not a detailed discussion or defense of the prioritization logic.  The discussion should exam the raw information in the hazard evaluation tables and distill it into a clear overview of safety features at the facility.  The use of relevant accident examples can frame and focus the discussion.  Identify structures, systems, and components as safety-significant SSCs where appropriate.  As a general rule of thumb, safety-significant SSC designations based on safety are limited to those systems, structures, or components whose failure is estimated to result in a prompt worker fatality, serious injuries to workers, or significant radiological or chemical exposures to workers.  Categorize administrative features in terms of the programmatic elements.  Provide documented evidence that safety features are an integral part of facility design and operation, that basic facility operations to ensure safety are adequate, and that workers are protected by a number of means including programs described as ACs.

Identify and discuss methods available to reviewers to determine if a hazard analysis has omitted important accident vulnerabilities.

The developments of DBAs along with identification of any other possible accidents are reviewed to determine if all hazards that may cause an accident are addressed.  In DOE-STD-3009, a flow chart shows that an iterative process is used.

Identify and discuss the relationship between hazard analysis and the postulation of accidents for quantitative consequence analysis in Documented Safety Analyses for DOE nuclear facilities.  Describe what factors govern the choice of an accident warranting further consequence analysis.

The hazard analysis identifies DBAs that will be used in the accident analysis.  These accidents represent a complete set of bounding conditions.  The identification of DBAs results from the hazard evaluation ranking of the complete spectrum of facility accidents.  The approach used at any specific facility is based on the detail needed for a given facility and the experience of the analysts.  This involves ranking risk for accidents by consequence and frequency.  The ranking schemes are designed to separate the lower risk accidents that are adequately assessed by hazard evaluation from higher risk accidents that may warrant additional quantitative analysis if the phenomena involved are not simplistic.  Rankings use a bin system.  For example, frequency bins should typically cover two orders of magnitude.  Although the exercise of binning is essentially qualitative, analysts often use a simple numerical basis for judgments to provide consistency.  Another methodology would be to use a summary of historical data.  Likewise, before beginning the evaluation, a conservative Gaussian plume estimation of the amount of material needed outside the building to cause a certain dose might be performed to aid in defining thresholds of significance.  However the ranking of frequency and consequence into such broad categories is more of a qualitative than a quantitative exercise.  An important factor in estimating binning thresholds for consequences is to tie the thresholds to the evaluation guideline so that accidents that could challenge the guideline are correctly identified for formal accident analysis.  The binning requirement of this subsection does not preclude the use of other sorting mechanisms in addition to risk sorting if an analyst finds such mechanisms useful.  This accident selection activity identifies the process and criteria used to select the unique and representative potential accidents to be included in accident analysis.  Unique accidents are those with sufficiently high-risk estimates that individual examination is needed.  Representative accidents bound a number of similar accidents of lesser risk.  Representative accidents are examined to the extent they are not bounded by unique accidents.  In any case, at least one bounding accident from each of the major types determined from the hazard analysis should be selected unless the bounding consequences are “low.”  Accidents are identified and listed by accident category and type.

Identify and discuss essential elements of deterministic and probabilistic risk assessment techniques.

### Probabilistic Risk Assessment (PRA)

PRA is the use of probabilistic-based accident and systems modeling techniques to quantitatively analyze, study, define, and prioritize credible accident scenarios.  The process is normally broken into three levels:

Level I, estimation of accident frequencies

Level II, transport of radionuclides into the environment

Level III, estimation of effects of radionuclides in the environment on the surrounding population

In general the Level I process consists of the following elements:

Accident identification and screening to identify credible accidents and eliminate incredible accidents.  Credible events are normally associated with “initiators,” or events which could lead to the onset of an accident.  Therefore, one of the products of this effort would be the identification of a set of initiators.

Development of accident progression event tree “top events” where success or failure of defense-in-depth SSCs or barriers, operator actions crucial to SSC or barrier integrity, and phenomenological events are modeled to define accident “end states.” Trees must be developed for each initiator or for groups of similar initiators identified above.

Quantification of event tree “top events.” This process often involves the development of detailed fault trees to determine top event failure probability.  Fault trees generally reduce SSC success criteria to combinations of individual sub-component failures through the use of Boolean algebra.

Quantification of initiating events where the frequency of occurrence is determined for each initiator event of interest.

Accident sequence event quantification, which is the process of determining the sum total failure frequency for all credible accident sequences by combining the initiator frequency with subsequent failures of defense-in-depth SSCs, barriers, operator actions or phenomenological events as defined in the accident progression event tree.

Analysis and documentation of results.

### Deterministic Risk Assessment

Deterministic risk assessment is the use of computer-based integrated modeling numerical methods for simultaneous solution of multiple equations to study accident progression and related response phenomenon.  This process is often used to quantify complex phenomenological events such as transport of radionuclides upon release.

Given an accident source term of radionuclide/hazardous chemical release, discuss the factors that should be considered in selection of an appropriate computer code for off-site transport and deposition.

### Source Term Methods

Source term estimation is the process of determining the amount and the types of radioactive isotopes released during a nuclear accident.  This is generally part of the front-end work performed in support of a Level II PRA, where to estimate a source term, the environmental conditions surrounding and evolving during an accident are studied using computer codes and laboratory experiments.  Using this information, estimation of release fractions of nuclides (isotopes) are made based upon the estimated or known source isotopic content.  Some of the factors that influence isotope release include

temperature

presence of a fire

thermal-hydraulics

explosions

breach of mechanical barriers to release such as cladding or sealed containers

### Environmental Transport Methods

The environmental transport method estimates the ways in which those release fractions determined previously are transported from the source to the environment and is typical of a Level III analysis.  Of specific interest are the multiple paths that releases may take into the environment, namely, airborne, surface waterborne, and subterranean hydrology paths.  For most radiological accidents, the airborne path is the most significant and is therefore the basis for the majority of transport studies/models.  The main factors significantly affecting transport include:

the chemical state of the radionuclide (solid, liquid, or gas);

the release path (airborne or waterborne);

the initial energy of release (explosive, fire, steam effects);

manmade barriers/mitigative measures (confinements, buildings, filters, spray removal systems, etc.);

dispersion or plume effects;

weather effects including prevailing winds, rain, snow, and inversions.

Also, software approved by DOE or software that can be verified to be correct and accurate in accordance with DOE software QA procedures may be used to determine off-site transportation and deposition models.

Discuss the physics of fires and explosions as the means of generating airborne plumes of hazardous materials and damaging barriers to releases.  Also describe how the physics affects the quantities or rates at which hazardous materials may become airborne as a result of spills, evaporation, entrainment, fires and other accidents.

Appendix-A of DOE-STD-3009-94 gives definitions to be used for the physics of an accident.

Discuss the phenomena and modeling of airborne dispersion of toxic materials addressing weather effects, turbulent mixing, mixing heights, plume temperature, evolution and potential settling or plate out of particulates and aerosols, precipitation, building wake, and surface roughness effects.

The phenomena and modeling of airborne dispersion is addressed in Appendix-A of DOE-STD-3009.  The application of the different inputs is discussed in DOE-STD-3009.  The standard discusses the use of the most conservative approach, which is the application of the worst possible conditions to maximize the effects of a plume.

Discuss the mechanisms involved in the damage caused by extreme natural phenomena including: hurricanes, tornadoes, ice storms, wind, flood, earthquakes and wild fires.

The mechanisms involved in the damage caused by external forces include the acceleration of a facility or system from events like earthquakes; mechanical damages resulting from tornados, hurricanes, ice storms, and wind; erosion caused by flooding or hurricanes; and thermal damage stemming from fires or ice storms.

Define and discuss the following terms:

Chi/Q

Dose conversion factor

Breathing rate

Aerodynamic equivalent diameter

Solubility class

Population dose

### Chi/Q

Chi/Q is a sampling distribution methodology.

### Dose Conversion Factor

The dose conversion factor is used to convert radionuclide type to equivalent exposure values.

### Breathing Rate

The breathing rate is the rate of respiration based on physical activity being performed.

### Aerodynamic Equivalent Diameter

The aerodynamic equivalent diameter is the diameter of a sphere of density 1 g/cm3 that exhibits the same terminal velocity as the particle in question.

### Solubility Class

Solubility class relates to the ability for a given chemical or nuclide to be suspended into solution.

### Population Dose

If all the individuals in the population of interest are exposed to the same concentrations of a substance, then the estimates of individual dose represent the average dose rate for members of the population and the population dose is the average dose times the number of persons in the population.

Given a source term, determine dose consequences applying Chi/Q, dose conversion factor, breathing rate and specific activity as applicable.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Given a simple accident scenario, demonstrate knowledge by constructing a simple neutral gas dispersion and heavy gas dispersion.  Estimate consequences using an accident modeling code including hand calculations and explain the assumptions, inputs and results.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Discuss the process for evaluating assumptions made for scenarios being modeled.

All assumptions made in the accident analysis are to be validated as part of the accident analysis activity.  For example, if an operator is supposed to push button Z to stop an accident progression, the accident analysis needs to make it clear that the operator can actually do so.  Making it clear may simply involve noting there are no physical phenomena associated with the accident that would preclude the operator from doing so.  Likewise, basic assurance must be provided that equipment relied upon in unusual or severe environments will function.  This assurance does not constitute the need for or expectation of full, formal environmental qualification.  The above guidance is not meant to imply that the DSA must contain detailed validations for all assumptions.  The DSA needs to present information at a level that is considered sufficient for review and approval of the DSA.  Referencing an auditable trail of information as part of the controlled supporting documentation is acceptable.

Discuss the methods used in the calculation of criticality accidents.

Various calculational methods are used depending on the complexity of the problem being evaluated.  The methodology and approach to determining criticality accidents require the ability to perform some or all of the following tasks:

Identify and discuss the application of several common hand calculation methods.

Select a single hand-calculation technique (buckling method, solid angle, or area density) and prepare an example of its use.

Develop an input model for one of the criticality safety codes (i.e., MONK, VIM, KENO/SCALE, MCNP, DANTSYS, ANISN, and COG).

Describe how cross section data impact Monte Carlo and deterministic codes.

Describe the importance of validation of computer codes and how it is accomplished.

Describe the methodology supporting Monte Carlo codes and deterministic codes.

Describe pitfalls of Monte Carlo calculations.

Discuss the strengths and weaknesses of Monte Carlo and Discrete Ordinants codes.

The diffusion theory model is not strictly valid for treating fissile systems in which neutron absorption, voids, and/or material boundaries are present.  In the context of these limitations, identify a fissile system for which a diffusion theory solution would be adequate.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of terminology associated with probabilistic risk assessment (PRA) techniques.

- Identify the strengths and weaknesses of probabilistic risk assessment for safety design and regulatory decision-making.

Probabilistic risk assessment has limitations.  It may sometimes exclude or not adequately quantify potentially important risk factors, such as very-low-frequency accident initiators, various failures derived from a common event, physical processes resulting from several low-frequency failures, or long-term health effects from potentially toxic materials.  Furthermore, because a risk assessment often deals with low-frequency but high-consequence accident risks, there is considerable potential for its results to be misunderstood.

The most useful aspects of the probabilistic risk assessment are not exclusively the risk numbers that are generated; they are also the insight gained by a systematic and methodical consideration of what can go wrong with a system.  A procedural analysis helps us to understand the likely vulnerabilities of the system, the threats they pose, and the measures that could be applied to mitigate or prevent them.  Risk assessment is a particularly powerful tool when there is only a limited set of alternatives for risk evaluation.  Thus, meaningful insights can be obtained by a risk assessment without depending on the accuracy of an “actual risk” value; such values are notoriously difficult to ascertain.

Define the following terms with respect to reliability engineering and probabilistic risk assessments:

Probability

Reliability

Availability

Unavailability

Risk

Safety

Accident sequence

Dominant contributors

Minimal cut set

### Probability

Probability is represented as a number in a scale from 0 to 1 which expresses the likelihood that an event will occur.

### Reliability

Reliability is the probability that an item is able to perform a required function under stated conditions for a stated period of time.

### Availability

Availability is the fraction of the total time that a device or system is able to perform its required function.

### Unavailability

Unavailability is the probability of the system being in a failed state at any given time.

### Risk

Risk is a combined effect of the probability of the occurrence of an undesired event and the magnitude of the event.

### Safety

Safety is the freedom from unacceptable risk or personal harm.

### Accident Sequence

An accident sequence is a specific unplanned sequence of events that has a specific undesirable consequence.

### Dominant Contributors

Dominant contributors are inputs that have the greatest effect on a given set of inputs.

### Minimal Cut Set

A minimal cut set is a cut set such that if any term is removed from the list the system will no longer fail.

Define the following terms and differentiate between the associated processes:

Event tree

Fault tree

Failure modes and effects analysis (FMEA)

### Event Tree

An event tree is a method for illustrating the sequence of outcomes that may arise after the occurrence of a selected initial event.

### Fault Tree

A fault tree is a method of representing the logical combinations of various system states which lead to a particular failure event.

### Failure Modes and Effects Analysis (FMEA)

FMEA is the study of the potential failures that might occur in any part of a system to determine the probable effect of each on all other parts of the system and on probable operational success.

Discuss how probabilistic risk assessment methods can help in understanding accident scenarios.

Acceptance criteria have been inextricably linked to accident scenarios that are prescribed in some manner.  The results of quantitative probabilistic risk assessments, principally those of nuclear power or production facilities, are sometimes compared to another type of risk acceptance criteria referred to as safety goals.  PRAs are fundamentally different analytical methods from deterministic accident scenarios and produce a different type of product.  For example, in PRAs the failure of a safety feature to perform an intended function is always postulated, irrespective of the safety classification of the feature.  A conceptually different approach is needed for safety analysis of existing facilities, where an analysis of the safety of the “facility as is” is performed.  The primary objective of the analytical process must then turn to the identification of needed controls and their potential inadequacies, and the corresponding corrective or compensatory measures.  For these existing facilities, safety assurance is provided through an aggressive approach based on a comprehensive analysis of all hazards leading to the release of radiological or toxicological material, and ensuring that the controls identified against each hazard are relevant, specific, and effective.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of basic heating, ventilation, air conditioning system (HVAC), and filtration system construction, operation, and application.

- Given engineering diagrams of a heating, ventilation, air conditioning system, identify the following components and discuss their purposes:

- Blowers

- Fans

- Dampers

- Chillers

- Filters

- HEPA filters

- Heat exchangers

- Scrubbers

- Hoods

- Glove boxes

- Flow, pressure, temperature, current, level, voltage and position indicators, recorders and controllers

Blower and fans circulate air through ventilation system.

Dampers direct and restrict flow through a ventilation system.

Chillers remove heat from air allowing it to enter a space at a lower temperature.

Filters are used to remove any particulates in the air; HEPA filters work with an efficiency level greater than 99 percent.

Heat exchangers add or remove heat from air to allow air to condition space.

Scrubbers are used to remove particulates in air systems in a localized area.

Hoods are used to contain contaminates within a given boundary by using a high velocity of air to flow and remove any airborne hazards prior to leaving hood space.

The glovebox isolates contaminates from the space where they are located.

Indicators are used to give a positive indication of system parameters and to allow for warnings of unstable conditions.

Discuss the relationships between the following in heating, ventilation, and air conditioning systems:

Supply ventilation

Flow

Exhaust ventilation

### Supply Ventilation

The supply ventilation is the air delivered to the conditioned space and used for ventilation, heating, cooling, humidification, or dehumidification.

### Flow

The flow is the path in a ventilation system through which air travels and includes the route for the supply air and return air and the path through the conditioned space.

### Exhaust Ventilation

The exhaust ventilation is the air removed from the conditioned space that was used for ventilation, heating, cooling, humidification, or dehumidification.

Describe the purpose of the heating, ventilation, and air conditioning system in the following applications:

Hoods

Glove boxes

Hot cells

Confinement systems

HEPA filtration

### Hoods

Hoods maintain a negative pressure area for storage of toxic chemicals.

### Glove boxes

Glove boxes contain hazardous material in an enclosed environment which prevents the material from spreading to areas that may affect workers or the public.

### Hot Cells

Hot wells are areas used to remotely handle highly radioactive or contaminated equipment.  This type of facility allows for all operations to be performed at a safe distance with adequate protection for workers.

### Confinement Systems

Confinement systems identify and describe the set of SSCs that perform confinement functions such as process vessels, glove boxes, ventilation systems, and facility walls.

### HEPA Filtration

HEPA filtration is the use of high-efficiency particulate air filtration with an efficiency of 99.97 percent.

Discuss the reason for and safety significance of the following system parameters:

Positive vs. negative system pressure

Differential pressure across filters

Differential pressure across components

### Positive vs. Negative System Pressure

Negative pressure systems minimize the spread of contamination or contaminants in the event of failure of a system, while a positive pressure system would help increase the spread of contamination or contaminants in the event of a failure.

### Differential Pressure across Filters

As differential pressure across a filter increases, it indicates an increase in the amount of material contained in the filters.  For radioactive systems, this may lead to increased radiation levels above what is prescribed in the DSA.

### Differential Pressure across Components

As differential pressure across a component increases, it indicates an increase in the amount of material settling out in that component.  For radioactive systems, this may lead to increased radiation levels above what is prescribed in the DSA.

Discuss the potential hazards and failure modes (to equipment and personnel) associated with the use of heating, ventilation, and air conditioning systems and components within nuclear safety-related systems.

During the design of the heating, ventilation, and air conditioning system, a careful analysis of the failure modes of each component and the effect of a failure on the operation of the system should be undertaken.  One of the more popular analysis methods is called a fault tree analysis.  This method may be used on entire systems, subsystems, and individual components.  For example, if attempting to do a fault tree analysis on a room pressure control system, choose the component you wish to analyze, such as a through-the-wall velocity sensor.  List this at the top of the tree.  Next consider all of its failure modes and list them underneath.  Next, for the most serious failure modes, consider all the affects on controlled components and other coupled and decoupled systems and list them underneath that mode.  Repeat this process until all the paths are complete.  It may be necessary to do all the branches of the tree to discover which paths represent the worst scenarios.  When all the failure modes of all the components, subsystems, and systems have been completed, you can make some strategic design modifications to eliminate or ameliorate the most serious scenarios by installing more reliable components in key locations or installing redundant controls or systems to provide backup and thus truncate the tree.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of process instrumentation principles of operation as applied to nuclear safety-related systems.

- Explain the process-related reason for measuring temperature, pressure, flow, and fluid level.

Temperature, pressure, flow, and fluid levels are monitored in processes to provide indication of potential failures.  Monitoring provides an indication of failure prior to having equipment damaged or destroyed or possibly releasing material to the environment.  The long-term tracking of operations allows for trend analysis of potential equipment failures.

For the temperature detection devices listed, explain how the instrument provides an output representative of the temperature being measured:

Thermocouple (TC)

Resistance temperature detector (RTD)

### Thermocouple

Thermocouples will cause an electric current to flow in the attached circuit when subjected to changes in temperature.  The amount of current that will be produced is dependent on the temperature difference between the measurement and reference junction, the characteristics of the two metals used, and the characteristics of the attached circuit.  Heating the measuring junction of the thermocouple produces a voltage which is greater than the voltage across the reference junction.  The difference between the two voltages is proportional to the difference in temperature and can be measured on the voltmeter (in millivolts).  For ease of operator use, some voltmeters are set up to automatically display temperature through use of electronic circuitry.  Other applications provide only the millivolt readout.  To convert the millivolt reading to its corresponding temperature, the applicable conversion chart supplied by the manufacturer needs to be used.

### Resistance Temperature Detector (RTD)

The RTD incorporates pure metals or certain alloys that increase in resistance as temperature increases and, conversely, decrease in resistance as temperature decreases.  RTDs act somewhat like an electrical transducer, converting changes in temperature to voltage signals by the measurement of resistance.  The metals that are best suited for use as RTD sensors are pure, of uniform quality, stable within a given range of temperature, and able to give reproducible resistance-temperature readings.  Only a few metals have the properties necessary for use in RTD elements.  RTD elements are normally constructed of platinum, copper, or nickel.  These metals are best suited for RTD applications because of their linear resistance-temperature characteristics, their high coefficient of resistance, and their ability to withstand repeated temperature cycles.  The coefficient of resistance is the change in resistance per degree change in temperature, usually expressed as a percentage per degree of temperature.  The material used must be capable of being drawn into fine wire so that the element can be easily constructed.

RTD elements are usually long, spring-like wires surrounded by an insulator and enclosed in a sheath of metal.  This particular design has a platinum element that is surrounded by a porcelain insulator.  The insulator prevents a short circuit between the wire and the metal sheath.  Inconel, a nickel-iron-chromium alloy, is normally used in manufacturing the RTD sheath because of its inherent corrosion resistance.  When placed in a liquid or gas medium, the Inconel sheath quickly reaches the temperature of the medium.  The change in temperature will cause the platinum wire to heat or cool, resulting in a proportional change in resistance.  This change in resistance is then measured by a precision resistance measuring device that is calibrated to give the proper temperature reading.

For the pressure detection devices listed, explain how the instrument provides an output representative of the pressure being measured:

Magnehelic differential pressure device

Photohelic differential pressure device

### Magnehelic Differential Pressure Device

A magnehelic differential pressure device transmits the effects of changes in air pressure from a diaphragm to an indicating pointer by means of magnetic linkage and without the use of gears or other direct mechanical linkages.  This system avoids wear and physical contact, which might destroy the accuracy and sensitivity of the instrument.  Because it uses no fluid, it eliminates evaporation, freezing, or toxicity problems.  It also ensures inertia-free, drift-free pointer movement and offers unusually high resistance to shock and vibration.  The gauges on this device are also unharmed by pressure surges and ambient temperature fluctuations.  The device quickly provides gas pressures—positive, negative, or differential.  Because operation does not depend on gravity, you can either face- or flush-mount the device in any position.

### Photohelic Differential Pressure Device

Photohelic gauges use a precise pressure switch that lets you control low and high gas pressures.  Knob controls adjust dual set points, which allow for variable deadband control.  These set points contain photocells that actuate double pull double throw (DPDT) relays when pressures reach a preset upper or lower limit, and they can be set up to control corrective damper action.  As the pressure changes in response to damper motion, and the indicator returns to the null band, damper motion is halted.

For the position detection devices listed, explain how the detector provides an output representative of the position being represented:

Limit switches

Potentiometer

Linear variable differential transformer types

### Limit Switches

A limit switch is a mechanical device which can be used to determine the physical position of equipment.  The limit switch gives on/off output that corresponds to valve position.  Normally, limit switches are used to provide full-open or full-shut indications.  Many limit switches are of the push-button variety.  When the valve extension comes in contact with the limit switch, the switch depresses to complete, or turn on, the electrical circuit.  As the valve extension moves away from the limit switch, spring pressure opens the switch, turning off the circuit.

### Potentiometer

A potentiometer provides an accurate indication of position throughout the travel of a valve or control rod.  The extension is physically attached to a variable resistor.  As the extension moves up or down, the resistance of the attached circuit changes, changing the amount of current flow in the circuit.  The amount of current is proportional to the valve position.  Potentiometer valve position indicator failures are normally electrical in nature.  An electrical short or open will cause the indication to fail at one extreme or the other.  If an increase or decrease in the potentiometer resistance occurs, erratic indicated valve position occurs.

### Linear Variable Differential Transformer Types

A linear variable differential transformer (LVDT) is a device which provides accurate position indication throughout the range of valve or control rod travel.  The extension valve shaft, or control rod, is made of a metal suitable for acting as the movable core of a transformer.  Moving the extension between the primary and secondary windings of a transformer causes the inductance between the two windings to vary, thereby varying the output voltage proportional to the position of the valve or control rod extension.  If the open and shut position is all that is desired, two small secondary coils could be utilized at each end of the extension’s travel.  As a rule, failures are limited to rare electrical faults which cause erratic or erroneous indications.  An open primary winding will cause the indication to fail to some predetermined value equal to zero differential voltage.  This normally corresponds to mid-stroke of the valve.  A failure of either secondary winding will cause either full-open or full-closed indications.

Referring to a piping and instrumentation drawing (P&ID) containing temperature, pressure, level, flow, or position detection components, explain their function in the designated system and relationship to system safety.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Discuss the importance of safety and process instrumentation to nuclear safety including redundancy and calibration requirements.

Equipment used for monitoring system operations that are important to safety should have a redundancy built into the system or should be built in such a way as to maintain a higher level of reliability.  Also, the equipment must provide a high level of reliability in calibration operations and performance to guarantee that all indications relating to safety are accurate and indicate true conditions.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of piping and instrumentation drawings (P&ID).

- Given a piping and instrumentation drawing, identify/interpret the symbols used for system components including the following at a minimum:

Valves

Pumps

Heat exchangers

Filters/strainers

Fans

Compressors

Instruments

Indicators

Controllers

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Identify how valve conditions (open/closed) are depicted.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Determine and follow system flowpath(s).

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Discuss the role of piping and instrumentation diagrams relative to identification of failure modes and mapping fault propagation through networks to support the identification of accident vulnerabilities.

P&IDs are usually designed to present functional information about a system or component.  As a rule, P&IDs do not have a drawing scale and present only the relationship or sequence between components.  These drawings only present information on how a system functions, not the actual physical relationships.  These drawings allow for easy identification of important equipment and also allow an individual to trace component failure throughout the system to readily identify how faults propagate and to identify weakness in system components essential for safety.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of electrical diagrams and schematics.

- Given a system diagram, identify/interpret the following symbols:

Motors

Controllers

Breakers

Generators

Batteries

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Given the appropriate diagram, state the condition (energized/de-energized) in which all electrical devices are shown, unless otherwise noted on the diagram.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Given a system diagram, identify the power sources and/or loads and their status.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Discuss the role of electrical one-line diagrams for identifying failure modes and for mapping fault propagation through networks to support the identification of accident vulnerabilities.

Electrical diagrams are usually designed to present functional information about a system or component.  As a rule electrical diagrams do not have a drawing scale and present only the relationship or sequence between components.  These drawings only present information on how a system functions, not the actual physical relationships.  These drawings allow for easy identification of important equipment and also allow an individual to trace component failure throughout the system to readily identify how faults propagate and to identify weakness in system components essential for safety.

## Nuclear safety specialists shall demonstrate a familiarity level knowledge of electrical logic diagrams.

- Given a logic diagram, identify/interpret the symbols used on logic diagrams to represent the components.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Identify the symbols used to denote a logical “1” (high/on) and a logical “0” (low/off) as used in logic diagrams.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Given a logic diagram and appropriate information, determine the output of each component and the logic circuit.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Given a logic diagram, identify three different trip settings and trace the resulting actions should the trip occur.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Discuss the role of control logic diagrams in identifying failure modes and for mapping fault propagation through networks to support the identification of accident vulnerabilities.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

## Nuclear safety specialists shall demonstrate a working level knowledge of radioactivity and transformation mechanisms.

- Define the following term:

Activation

### Activation

Activation is the process by which materials become radioactive.

Given the “Chart of Nuclides,” trace the decay chain for a specified nuclide.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Given either half-life or the radioactive decay constant, solve radioactive decay problems.

The following equation is applied:

At = Ao e-λt

At = activity present at time t

Ao = activity initially present

λ = decay constant (time)-1

t = time

Using the specific activity or decay constant of an isotope, convert between mass quantities and curies.

The relationship between activity, number of atoms, and decay constant is shown below:

A = λ N

where:

A = Activity of the nuclide (disintegrations/second)

λ = decay constant of the nuclide (second)-1

N = Number of atoms of the nuclide in the sample

The unit of measure for mass is the atomic mass unit (amu). One atomic mass unit is equal to 1.66 x 10-24 grams. A curie is a unit of measure of the rate of radioactive decay equal to 3.7 x 1010 disintegrations per second. This is approximately equivalent to the number of disintegrations that one gram of radium-226 will undergo in one second.

## Nuclear safety specialists shall demonstrate a working level knowledge of principles and concepts for internal and external dosimetry and dose consequences.

- Define the following terms:

Committed effective dose equivalent

Total effective dose equivalent

Whole body

Derived air concentrations (DAC)

Annual limit of intake (ALI)

Weighting factors

Stochastic effects

Non-stochastic (deterministic) effects

### Committed Effective Dose Equivalent

The committed effective dose equivalent is the dose equivalent calculated to be received by a tissue or organ over a 50-year period after the intake of a radionuclide into the body.

### Total Effective Dose Equivalent

The total effective dose equivalent is the sum of the effective dose equivalent and the committed effective dose equivalent.

### Whole Body

Whole body refers to a dose resulting from exposing the entire body to radiation.

### Derived Air Concentration (DAC)

The DAC is the airborne concentration that equals the ALI divided by the volume of air breathed by an average worker for a working year of 2000 hours.

### Annual Limit of Intake (ALI)

The ALI is the derived limit for the permissible amount of radioactive material taken into the body of an adult radiation worker by inhalation or ingestion in a year.

### Weighting Factors

Generally, weighting factors refers to a method of attaching different importance values to different items or characteristics; in the context of radiation protection, the proportion of the risk of effects resulting from irradiation of a particular organ or tissue to the total risk of effects when the whole body is irradiated uniformly.

### Stochastic Effects

Stochastic effects are malignant and hereditary diseases for which the probability of an effect occurring, rather than its severity, is regarded as a function of dose without a threshold for radiation protection purposes.

### Non-Stochastic (Deterministic) Effects

Non-stochastic (deterministic) effects are effects due to radiation exposure for which the severity varies with the dose and for which a threshold normally exists.

Discuss the conservatisms of International Commission on Radiological Protection (ICRP) Publications 26, 30, 60, 68, 71, and 72 as they relate to dose conversion factors and consequence analysis in hazard categorization and accident analysis.

A Review of ICRP Publications 26, 30, 60, 68, 71, and 72 is required.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the biological effects of radiation.

- Describe the effects of radiation exposure on the cellular level including:

Direct effects

Indirect effects

### Direct Effects

If radiation interacts with the atoms of the DNA molecule, or some other cellular component critical to the survival of the cell, it is referred to as a direct effect.  Such an interaction may affect the ability of the cell to reproduce and, thus, survive.  If enough atoms are affected such that the chromosomes do not replicate properly, or there is a significant alteration in the information carried by the DNA molecule, then the cell may be destroyed by “direct” interference with its life-sustaining system.

### Indirect Effects

If a cell is exposed to radiation, the probability of the radiation interacting with the DNA molecule is very small since these critical components make up such a small part of the cell.  However, each cell, just as is the case for the human body, is mostly water.  Therefore, there is a much higher probability of radiation interacting with the water that makes up most of the cell’s volume.  When radiation interacts with water, it may break the bonds that hold the water molecule together, producing fragments such as hydrogen (H) and hydroxyls (OH).  These fragments may recombine or may interact with other fragments or ions to form compounds, such as water, which would not harm the cell.  However, they could combine to form toxic substances, such as hydrogen peroxide (H2O2), which can contribute to the destruction of the cell.

Describe the regulatory limits established by EPA federal guidance reports No.11 and 13 and subsequent DOE radiological evaluation guideline and EPA protective actions guides for nuclear accidents.

The documents may be found at http://www.epa.gov/radiation/docs/federal/520-1-88-020.pdf and http://www.epa.gov/radiation/docs/federal/402-r-99-001.pdf.

Identify and discuss the range of doses above which one may expect acute radiation illness and early fatalities.

Acute doses of radiation can cause a pattern of clearly identifiable symptoms (syndromes).  These conditions are referred to in general as Acute Radiation Syndrome.  Radiation sickness symptoms are apparent following acute doses greater than or equal to100 rad.  Acute whole body doses of greater than or equal to 450 rad may result in a statistical expectation that 50 percent of the population exposed will die within 60 days without medical attention.  As in most illnesses, the specific symptoms, the therapy that a doctor might prescribe, and the prospects for recovery vary from one person to another and are generally dependent on the age and general health of the individual.

Blood-forming organ (bone marrow) syndrome (an exposure greater than 100 rad) is characterized by damage to cells that divide at the most rapid pace (such as bone marrow, the spleen, and lymphatic tissue).  Symptoms include internal bleeding, fatigue, bacterial infections, and fever.

Gastrointestinal tract syndrome (an exposure greater than 1000 rad) is characterized by damage to cells that divide less rapidly (such as the linings of the stomach and intestines).  Symptoms include nausea, vomiting, diarrhea, dehydration, electrolytic imbalance, loss of digestion ability, bleeding ulcers, and the symptoms of blood-forming organ syndrome.

Central nervous system syndrome (an exposure greater than 5000 rad) is characterized by damage to cells that do not reproduce such as nerve cells.  Symptoms include loss of coordination, confusion, coma, convulsions, shock, and the symptoms of the blood forming organ and gastrointestinal tract syndromes.  Scientists now have evidence that death under these conditions is not caused by actual radiation damage to the nervous system, but rather from complications caused by internal bleeding and fluid and pressure build-up on the brain.  Other effects from an acute dose include the following:

Exposure to 200 to 300 rad to the skin can result in the reddening of the skin (erythema), similar to mild sunburn, and may result in hair loss due to damage to hair follicles.

Exposure to 125 to 200 rad to the ovaries can result in prolonged or permanent suppression of menstruation in about fifty percent of women.

Exposure to 600 rad to the ovaries or testicles can result in permanent sterilization.

Exposure to 50 rad to the thyroid gland can result in benign (non-cancerous) tumors.

As a group, the effects caused by acute doses are called deterministic.  Broadly speaking, this means that the severity of the effect is determined by the amount of dose received. Deterministic effects usually have some threshold level below which the effect will probably not occur, but above which the effect is expected.  When the dose is above the threshold, the severity of the effect will increase as the dose increases.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the principles and use of radiological instrumentation and radiological monitoring/survey practices.

- Discuss the purpose, principles of detection and operation, and field application of the following:

Continuous air monitors (CAM) including tritium alarms

Area radiation monitors (ARM)

Criticality detection/alarm systems

Process radiation monitors

### Continuous Air Monitors (CAM) including Tritium Alarms

The requirements of air monitoring programs should be established to ensure that airborne radioactivity monitoring is performed at a frequency consistent with the existing and potential hazards and activities planned in the area. The selection of air monitoring equipment should be based on the specific job being monitored. Air monitoring equipment includes portable and fixed air sampling equipment and CAMs. Air sampling equipment shall be used where an individual is likely to receive an annual exposure of 40 or more derived air concentration (DAC) hours.  This intake generally represents a committed effective dose equivalent to an individual of approximately 100 millirem. Samples shall also be taken as necessary to characterize the hazard in areas where respiratory protection devices have been prescribed for protection against airborne radionuclides.  Air samples should be adequate to evaluate the concentrations of airborne radioactive materials at the individual’s work locations.  Real-time (or continuous) air monitors are used to provide early warning to individuals of events that could lead to substantial unplanned exposures to airborne radioactivity.  Such exposures could result from a breakdown of engineered controls or improper establishment of boundaries during work that creates airborne radioactivity.  Real-time air monitoring is necessary to detect and provide warning of airborne radioactivity concentrations that warrant immediate action to terminate inhalation of airborne radioactive material.  Air sampling equipment should be positioned to measure air concentrations to which individuals are exposed.  If this cannot be achieved, a program of personal breathing-zone air sampling should be initiated.  Air monitoring equipment shall be routinely calibrated and maintained on an established frequency.  Air monitoring equipment should be calibrated at least once each year.  CAMs should be capable of measuring 1 DAC when averaged over 8 hours (8 DAC-hours) under laboratory conditions.  Real-time air monitoring equipment required from above should have alarm capability and sufficient sensitivity to alert individuals that immediate action is necessary to minimize or terminate inhalation exposures.  A technical basis document should be developed for the airborne radioactivity monitoring program.  The technical basis document should provide the basis for air monitor selection, placement, and operation.  The proper operation of CAMs should be verified daily by performing an operational check.  Operational checks should include positive air-flow indication, non-zero response to background activity, and internal check sources or 60 Hz electronic checks when available.  Real-time air monitoring equipment operation should be verified weekly by checking for instrument response with a check source or with ambient levels of radon daughters.

### Area Radiation Monitors (ARMs)

ARMs should be installed in frequently occupied locations with the potential for unexpected increases in dose rates and in remote locations where there is a need for local indication of dose rates prior to personnel entry.  ARMs should not be substituted for radiation exposure surveys in characterizing a workplace.  The need for and placement of ARMs should be documented and assessed when changes to facilities, systems, or equipment occur.  ARMs should be tested at least quarterly to verify audible alarm system operability, audibility under ambient working conditions, and operability of visual alarms when so equipped.  If installed instrumentation is removed from service for maintenance or calibration, a radiation monitoring program providing similar detection capability should be maintained, consistent with the potential for unexpected increases in radiation dose rates.  Where an ARM is incorporated into a safety interlock system, the circuitry should be such that a failure of the monitor either prevents entry into the area or prevents operation of the radiation producing device.  If the circuitry is required to ensure compliance with the high radiation area access control requirements, then the circuitry shall be fail-safe.

### Criticality Detection/Alarm Systems

Criteria for criticality detection/alarm systems are listed below:

Criticality alarm systems shall be designed to detect immediately the minimum accident of concern.  The minimum accident may be assumed to deliver the equivalent of an absorbed dose in free air of 20 rad at a distance of 2 meters from the reacting material within 60 seconds.

Systems shall be designed so that instrument response and alarm latching shall occur as a result of radiation transients of 1-millisecond duration.

The alarm signal shall be for evacuation purposes only, and of sufficient volume and coverage to be heard in all areas that are to be evacuated.  Very high audio background noise in some areas may require that the alarm be supplemented with visual signals; however, high background noise is a dangerous situation that should be prevented by design.

Instrument response to radiation shall be calibrated periodically to confirm the continuing performance of the instrument.  The calibration interval may be determined on the basis of experience but shall be no less frequent than annually.  Tests should be performed at least monthly and the results of testing should be documented.

The nuclear criticality safety program shall be evaluated and documented and shall include

an assessment of the need for criticality accident detection devices and alarm systems

installation of such equipment where total risk to personnel will be reduced

The need for criticality alarm systems shall be evaluated for all activities in which the inventory of fissionable material in individual unrelated work areas exceeds the design limits.  If the fissionable material mass exceeds the limits and the probability of criticality is greater than 10-6 per year, a criticality alarm system shall be provided to cover occupied areas in which the expected dose exceeds 12 rad in free air.  The criticality alarm system should include a criticality detection device and a personnel evacuation alarm.  Reasonable grounds for incredibility may be presented on the basis of commonly accepted engineering judgment.  The alarm signal shall be for immediate evacuation purposes only and of sufficient volume and coverage to be heard in all areas that are to be evacuated.  The alarm trip point shall be set low enough to detect the minimum accident of concern.  The minimum accident of concern may be assumed to deliver the equivalent of an absorbed dose in free air of 20 rad at a distance of 2 meters from the reacting material within 60 seconds.  The alarm signal shall activate promptly when the dose rate at the detectors equals or exceeds a value equivalent to 20 rad/minute at 2 meters from the reacting material.  A visible or audible warning signal shall be provided at a normally occupied location to indicate system malfunction or loss of primary power.  Each alarm system should be tested at least once every three months.  An evacuation drill shall be conducted at least annually.  Criticality alarm systems may consist of one to several detectors per unit.  In multi-detector units, at least two detectors shall be at the alarm level before initiating the alarm; in redundant systems, failure of any single channel shall lead into the trip state.

### Process Radiation Monitors

Process radiation monitors are monitors that are used just like the ARMs, but which are applied for a certain process or operation.

## Nuclear safety specialists shall demonstrate a working-level knowledge of 10 CFR 830.204, Documented Safety Analysis, and DOE Guide 421.1-2, with respect to its impact on Department nuclear safety.

- Discuss the basic purposes and objectives of a Documented Safety Analysis.

The purpose of the DSA is to establish safety basis requirements for hazard category 1, 2, and 3 DOE nuclear facilities.  The documented safety analysis for a hazard category 1, 2, or 3 DOE nuclear facility must, as appropriate for the complexities and hazards associated with the facility

describe the facility (including the design of SSCs) and the work to be performed;

provide a systematic identification of both natural and man-made hazards associated with the facility;

evaluate normal, abnormal, and accident conditions, including consideration of natural and man-made external events, identification of energy sources or processes that might contribute to the generation or uncontrolled release of radioactive and other hazardous materials, and consideration of the need for analysis of accidents which may be beyond the design basis of the facility;

derive the hazard controls necessary to ensure adequate protection of workers, the public, and the environment; demonstrate the adequacy of these controls to eliminate, limit, or mitigate identified hazards; and define the process for both maintaining the hazard controls current at all times and controlling their use;

define the characteristics of the safety management programs necessary to ensure the safe operation of the facility, including (where applicable) quality assurance, procedures, maintenance, personnel training, conduct of operations, emergency preparedness, fire protection, waste management, and radiation protection;

with respect to a nonreactor nuclear facility with fissionable material in a form and amount sufficient to pose a potential for criticality, define a criticality safety program that

ensures that operations with fissionable material remain subcritical under all normal and credible abnormal conditions

identifies applicable nuclear criticality safety standards

describes how the program meets applicable nuclear criticality safety standards

Describe the responsibilities of contractors for the development and maintenance of a Documented Safety Analysis.

In establishing the safety basis for a hazard category 1, 2, or 3 DOE nuclear facility, the contractor responsible for the facility must

define the scope of the work to be performed;

identify and analyze the hazards associated with the work;

categorize the facility consistent with DOE-STD-1027-92;

prepare a documented safety analysis for the facility;

establish the hazard controls upon which the contractor will rely to ensure adequate protection of workers, the public, and the environment.

In maintaining the safety basis for a hazard category 1, 2, or 3 DOE nuclear facility, the contractor responsible for the facility must

update the safety basis to keep it current and to reflect changes in the facility, the work, and the hazards as they are analyzed in the documented safety analysis;

annually submit to DOE either the updated documented safety analysis for approval or a letter stating that there have been no changes in the documented safety analysis since the prior submission;

incorporate in the safety basis any changes, conditions, or hazard controls directed by DOE.

Define the following terms and discuss the purpose of each:

Design basis

Engineered design features

Safety analysis

Safety basis

Basis for interim operation

Transportation safety document

Safety analysis report for packaging

Health and safety plan

Hazards analysis report

### Design Basis

The design basis is comprised of the design inputs, the design constraints, and the design analysis and calculations.  It includes topical areas such as seismic qualification, fire protection, and safe shutdown.  It encompasses consideration of such factors as plant availability, plant efficiency, costs, and maintainability, and that subset that relates to safety and the authorization basis.

### Engineered Design Feature

Engineered design features are the safety design limits on engineered controls, either passive or active, and the bases placed on equipment designs or operations to ensure safe conditions under all normal, abnormal, and accident conditions.

### Safety Analysis

A safety analysis reviews the extent to which a nuclear facility can be operated with respect to workers, the public, and the environment, including a description of the conditions, safe boundaries, and hazard controls that provide the basis for ensuring safety.

### Safety Basis

The safety basis is comprised of the documented safety analysis and hazard controls that provide reasonable assurance that a DOE nuclear facility can be operated safely in a manner that adequately protects workers, the public, and the environment.

### Basis for Interim Operation

The basis for interim operations is the documented establishment of allowable operations for a current facility and its operational controls until a fully compliant document is developed and approved by DOE.

### Transportation Safety Document

The transportation safety document describes the methodology and compliance process to meet equivalent safety for any deviation from the hazardous materials regulations.

### Safety Analysis Report for Packaging

The safety analysis report for packaging is the document that demonstrates that the package will satisfy the standards of 10 CFR 71 and any other standards that the Headquarters certifying official may determine applicable for granting a certificate of compliance.  Each certificate shall be issued for a five-year period, after which the certificate must be renewed by the Headquarters certifying official.

### Health and Safety Plan (HASP)

For all facilities having or dealing with hazardous waste, a HASP shall be developed.  It shall, at a minimum, cover each site, task, operation, activity, or project, and address the following elements:

Health and safety risk or hazard identification for each site task, operation, activity, or project defined in the workplan (All chemical, radiological, and physical hazards, e.g., noise and heat, must be identified in the HASP.  Actions taken to mitigate risks or hazards shall be identified.  This risk or hazard identification should have a common basis with, or integrate the results of, other documents such as a SAR.)

Required training for employees for each site task, operation, activity, or project and hazard

Personnel protective equipment to be used by workers for each site task and operation

Employee medical surveillance requirements

Frequency and types of required personnel monitoring (including air, noise, radiation, heat, stress, etc.) including the methods of maintenance and calibration of monitoring and sampling equipment to be used

Site control measures including work zones, buddy systems, security, communications, and safety work practices

Decontamination procedures

Emergency response plans for safe and effective responses to emergencies

Confined space entry procedures

Programs to protect against and mitigate spills

### Hazards Analysis Report (HAR)

A HAR documents the hazard analysis (HA) of an operation and associated activities.  At a minimum, the HAR shall include the following:

An executive summary that provides an overview of the HAR and its main conclusions

An introduction that provides a discussion of the objectives, the scope of the analysis, the operations conducted, and the limitations and assumptions employed in the HA

A description of the nuclear explosive and its intrinsic hazards

A description of the nuclear explosives operations (NEO) and the facility(ies) where the operation is to be conducted (The discussion should focus on the facility and nuclear explosive configurations and processes, including equipment and tooling.  The discussion should also address whether interfaces between the operation and facility have safety implications.  Generic safety controls utilized during the operation should be discussed.)

A discussion of the methodology used to conduct the HA and derive safety controls and safety requirements

A summary of the identification of hazards and potential hazard scenarios under normal and abnormal conditions considering both internal and external environments for each step in the operations

Describe the different requirements for the scope and content of each type of documented safety analysis and discuss the general content of each as well as the required sections of each.

The different types of safety analyses, the applicability of each, and the required sections are described in 10 CFR 835 appendix A to subpart B table-2.  The URL is included below:

http://www.eh.doe.gov/enforce/rands/10cfr830.pdf

The content requirements for each type of DSA are contained in the following documents.  The document URLs are also included below:

DOE-STD-3009	http://www.eh.doe.gov/techstds/standard/std3009/std3009_cn2.pdf

DOE-STD-3011	http://www.eh.doe.gov/techstds/standard/std3011/std3011.html

DOE-STD-1120	http://www.eh.doe.gov/techstds/standard/std1120/s1120v1.pdf

29 CFR 1910.120	http://www.access.gpo.gov/nara/cfr/waisidx_04/29cfrv5_04.html

DOE-STD-3016	http://www.eh.doe.gov/techstds/standard/std3016/dpstd301699.pdf

DOE-O-460.1A	http://www.directives.doe.gov/pdfs/doe/doetext/neword/460/o4601a.pdf

DOE-O-461.1	http://www.directives.doe.gov/pdfs/doe/doetext/neword/461/o4611.pdf

DOE-M-461.1-1	http://www.directives.doe.gov/pdfs/doe/doetext/neword/461/m4611-1.pdf

Discuss the approval requirements for the documented safety analysis for new facilities and subsequent changes to the documented safety analysis.

DOE evaluates the DSA by considering the extent to which the DSA (1) adequately addresses the criteria set forth in 10 CFR 830.202 and 10 CFR 830.204, and (2) satisfies the provisions of the methodology used to prepare the DSA.  DSA review and approval focuses on the adequacy of the following approval bases:

Base information

Hazard and accident analyses

Safety SSCs

Derivation of TSRs

Safety management program characteristics

Once technical justification exists to support conclusions that the DSA adequately describes how the facility is satisfactory with respect to the approval bases, the DSA may generally be considered adequate.  These approval bases also form the foundation for documenting DSA approval in a safety evaluation report (SER).  Any changes to the DSA are documented in the unreviewed safety question (USQ) for the facility and reviewed by DOE for the above mentioned requirements.

Define who approves facility operations prior to achieving Documented Safety Analysis upgrade approval.

The USQ rule has a primary role in preserving the DOE safety basis for each nuclear facility.  The concept of the USQ allows contractors to make physical and procedural changes and to conduct tests and experiments without prior DOE approval, as long as these changes do not affect the safety basis of the facility.  If the changes do affect the safety basis, the DOE must approve the USQ.

Discuss the provisions for deviations, temporary and permanent exemptions from the 10 CFR 830.204, and safe harbor methodologies.

Provisions for deviations, exemptions, or safe harbor methodologies are made for the following activities:

Activities that are regulated through a license by the Nuclear Regulatory Commission (NRC) or a State under an Agreement with the NRC, including activities certified by the NRC under section 1701 of the Atomic Energy Act (Act);

Activities conducted under the authority of the Director, Naval Nuclear Propulsion, pursuant to Executive Order 12344, as set forth in Public Law 106–65;

Transportation activities which are regulated by the Department of Transportation;

Activities conducted under the Nuclear Waste Policy Act of 1982, as amended, and any facility identified under section 202(5) of the Energy Reorganization Act of 1974, as amended;

Activities related to the launch approval and actual launch of nuclear energy systems into space.

Discuss the application of the graded approach relative to the DSA development.

Application of the graded approach ensures that the level of analysis, documentation, and actions used to comply with a requirement is commensurate with

the relative importance to safety, safeguards, and security;

the magnitude of any hazards involved;

the life cycle stage of a facility;

the programmatic mission of a facility;

the particular characteristics of a facility;

the relative importance of radiological and nonradiological hazards;

any other relevant factor from the rule.

## Nuclear safety specialists shall demonstrate a working-level knowledge of the safety basis requirements for environmental restoration and decommissioning activities.

- Discuss the application of DOE-STD-1120 and 29 CFR 1910.120 to decommissioning and certain environmental restoration activities.

The environmental, safety, and health (ES&H) principles presented in DOE-STD-1120 and 29 CFR 1910 apply to all phases of facility disposition.  These phases comprise deactivation, decommissioning, and any long-term surveillance and maintenance (S&M) activities that are conducted prior to each of these phases.  The guidance contained within DOE-STD-1120 and 29 CFR 1910 is not intended for non-facility environmental restoration activities or for material stabilization activities conducted as part of the operations phase of the facility life-cycle.  DOE-STD-1120 and 29 CFR 1910 are intended for use by facility disposition project teams implementing the DOE Work Smart Standards (WSS) process, as well as for use by those teams following a compliance-based approach using a Standards/Requirements Identification Document (S/RID) process.  All provisions of DOE-STD-1120 and 29 CFR 1910 cover any treatment, storage, or disposal (TSD) operation regulated by other rules such as state law or RCRA.  If an area is used primarily for treatment, storage, or disposal, any emergency response operations in that area shall ensure compliance with all parts of  DOE-STD-1120 and 29 CFR 1910.120.

Discuss the content of a safety basis HASP and how it can be used in a dynamic project, including management of hazard controls.

A HASP is a “living document” to be modified and updated as new regulations and other requirements are issued.  Guiding the development of this document has been the principle that an effective and high-quality HASP must provide

a clear chain of command for safety and health activities

accountability for safety and health performance

well defined Headquarters’ expectations regarding safety and health

well defined task and operational hazards/risks

comprehensive hazard prevention and control methods

recordkeeping requirements to track program progress

As this document was developed, the working group applied the following assumptions:

It is a generic document to be adapted on a site-by-site basis.

An adequate site characterization and comprehensive workplan exists at each field site.

Operations analysis and risk identification methods are adequate.

A written site safety and health program exists as required in 29 CFR 1910.120 (b).

Written site Standard Operating Procedures exist.

Site-specific information is available.

The site-specific HASP should include a description of the site that the HASP will encompass and its applicability to operations.  In developing this description, the preparer should include

a brief description

background information (e.g., site history, prior site activities)

known site contamination

a synopsis of site characterization

site operations to be performed

Discuss the provisions of 29 CFR 1926.65 and 1910.120 for Technical Safety Requirements.

The areas of engineering controls, work practices, personnel protective equipment (PPE) for substances, and applicable training for these rules are already developed in some context for use as TSRs for hazardous material or waste facilities.

Describe the application of DOE-STD-3011, Guidance for Preparation of Basis for Interim Operations (BIO) Documents, to nuclear facilities safety basis.

The DOE-STD-30011 is applicable to the following:

The deactivation of a nuclear facility

A nuclear facility with a limited operational life

The transition surveillance and maintenance of a nuclear facility

### Deactivation

Deactivation is the process of placing a facility in a stable and known condition and includes the removal of hazardous and radioactive materials.

### Nuclear Facility with a Limited Operational Life

A nuclear facility with a limited operational life is a facility for which there is a short remaining operational period before ending the facility’s mission and initiating deactivation and decommissioning, and for which there are no intended additional missions other than cleanup.

### Transition Surveillance and Maintenance Activities

Transition surveillance and maintenance activities are activities conducted when a facility is not operating, or during deactivation, decontamination, and decommissioning operations when surveillance and maintenance are the predominant activities being conducted at the facility.  These activities are necessary for satisfactory containment of hazardous materials and protection of workers, the public, and the environment.  These activities include providing periodic inspections, maintenance of SSCs, and actions to prevent the alteration of hazardous materials to an unsafe state.

Discuss the limitations associated with the safety basis for “certain environmental restoration activities.”

Environmental restoration is the process by which contaminated sites and facilities are identified and characterized and by which existing contamination is contained, or removed and disposed of.  According to 10 CFR 830, the approved safe harbor methods for dealing with environmental restoration activities are the method in DOE-STD–1120–98 or successor document or the method using the provisions in 29 CFR 1910.120 (or 29 CFR 1926.65 for construction activities) for developing a safety and health program and a site-specific health and safety plan.

Review a chapter of an environmental restoration/decommissioning activity safety basis.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Discuss the unique considerations with respect to control selection for waste management activities.

Controls used in waste management operations are developed out of the Code of Federal Regulations.  The engineered controls are addressed in 29 CFR 1910.120 and 29 CFR 1926.65.  Controls for waste management activities are addressed in the rules.

## Nuclear safety specialists shall demonstrate a working-level knowledge of 10 CFR 830.207, DOE Approval of Safety Basis and DOE-STD-1104, with respect to its impact on department nuclear safety.

- Describe the basic purpose and contents of a Safety Evaluation Report.

The purpose of the SER is to allow DOE to review the safety basis developed by the contractor and to approve operation of the facility to the standards set in the DSA and TSRs.  The contents of a SER are listed below:

Title page

Signature page

Executive summary

Review process

Base information

Hazard and accident analysis

Safety SSCs

Derivation of TSRs

Safety management program characteristics

TSRs

Records

Describe the bases for approval contained in a Safety Evaluation Report.

DSA review and approval focuses on the adequacy of the following approval bases.  These approval bases also form the foundation for documenting DSA approval in a SER:

Base information

Hazard and accident analyses

Safety SSCs

Derivation of TSRs

Safety management program characteristics

Base information is the first of the approval bases that should be reviewed and encompasses elements of DSA preparation, completeness, and general content.  Base information is not reviewed for accuracy in and of itself, but for sufficiency to allow assessment of the other approval bases that rely on this information.  The review for sufficiency can range from a simple screening effort to more detailed discussions, depending on the complexity of the DSA.

Insufficient or incomplete base information in a DSA may prevent further review of the DSA.  Reviewers should require resolution of major discrepancies in base information before evaluation of the more specific aspects of the safety basis proceeds.  It is for this reason that the SER need only provide a brief statement as to the adequacy of base information.  The approval bases for the TSR document are the TSR provisions.  These TSR provisions may be design features, safety limits, operating limits, surveillance requirements, or administrative controls.  The approval bases for a TSR document include a disciplined analysis and tracing of commitments to hazard controls through appropriate provisions that implement these controls in a TSR document.  In some cases the specific treatment of safety controls in the TSR is committed to in the DSA; in other cases, it is a judgment call as to the appropriate TSR treatment.  Determining the adequacy of the TSR provisions generally entails being able to conclude that

hazard controls that are discussed in the DSA are faithfully translated into TSR provisions

the TSR provisions are appropriate and consistent with the DSA

The sources of information in a DSA regarding these provisions are the hazards analysis, including a description of hazard controls; the description of safety SSCs, the classification of these SSCs as safety class, safety significant, or other important defense-in-depth SSCs, the description of the functional requirements for the safety SSCs, and the derivation of TSRs section; and the descriptions of the safety management programs.

Prepare a Safety Evaluation Report consistent with DOE-STD-1104 for a safety basis amendment or annual update.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

## Nuclear safety specialists shall demonstrate a working-level knowledge of 10 CFR 830.206, Preliminary Documented Safety Analysis, with respect to its impact on department nuclear safety.

- Describe the application of the requirements of DOE O 420.1A and its guidance to the development process for the Preliminary Documented Safety Analyses.

Non-reactor nuclear facilities shall be designed with the objective of providing multiple layers of protection to prevent or mitigate the unintended release of radioactive materials to the environment.  Defense in depth shall include

minimization of material at risk

the use of conservative design margins and quality assurance

the use of successive physical barriers for protection against the release of radioactivity

the provision of multiple means to ensure critical safety functions

the use of equipment and ACs which restrict deviations from normal operations and provide for recovery from accidents to achieve a safe condition

means to monitor accident releases required for emergency responses

the provision of emergency plans for minimizing the effects of an accident

Facilities shall be sited and designed in a manner that provides adequate protection for the health and safety of the public and workers, including those at adjacent facilities, from the effects of potential facility accidents involving the release of radioactive materials.  All nuclear facilities with uncontained radioactive materials shall have means to confine them.  Such confinement will act to minimize the spread of radioactive materials and the release of radioactive materials in facility effluents during normal operations and potential accidents.  For a specific nuclear facility, the number and arrangement of confinement barriers and their required characteristics shall be determined on a case-by-case basis.  Factors that shall be considered in confinement system design shall include type, quantity, form, and conditions for dispersing the material.  Engineering evaluations, trade-offs, and experience shall be used to develop practical designs that achieve confinement system objectives.  The adequacy of confinement systems to effectively perform the required functions shall be documented and accepted through the SAR.  Facilities shall be designed to facilitate safe deactivation, decommissioning, and decontamination at end of life.  Facilities shall be designed to facilitate inspections, testing, maintenance, and repair and replacement of safety SSCs as part of an overall reliability, availability, and maintainability program.  The objective is that the facility can be maintained in a safe state, including during these operations, and in keeping with the ALARA principle for occupational radiation exposure.  Facilities shall be designed to keep occupational radiation exposure within statutory limits and incorporate ALARA principles in design, including design provisions to facilitate decontamination during the operational period.

Facility process systems shall be designed to minimize the production of wastes and minimize the mixing of radioactive and non-radioactive wastes.  Safety SSCs identified in accordance with this section shall, commensurate with the importance of the safety functions performed, be designed so that they can perform their safety functions when called upon to operate, and under a quality assurance program that satisfies 10 CFR 830.120.

Describe the sequencing of the Preliminary Documented Safety Analysis relative to design, procurement, construction and operation of new facilities.

The sequence for developing a PDSA is to prepare a PDSA for the facility and then obtain DOE approval of the nuclear safety design criteria used in preparing the PDSA.  The PDSA must be approved before the contractor can procure materials or components or begin construction.  The DOE may authorize the contractor to perform limited procurement and construction activities without approval of a PDSA if DOE determines that the activities are not detrimental to public health and safety and are in the best interests of DOE.

Describe the circumstances when a Preliminary Documented Safety Analysis must be prepared.

If construction begins after December 11, 2000, the contractor responsible for a hazard category 1, 2, or 3 new DOE nuclear facility or a major modification to a hazard category 1, 2, or 3 DOE nuclear facility must prepare a PDSA for the facility.

Describe the relationship between the PDSA and the design process.

The design process and PDSA are interrelated.  They feed each other, with changes in one having a direct influence on the other, so the PDSA and design are “living documents” changing with the project.

Perform a detailed review of a PDSA chapter.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

## Nuclear safety specialists shall demonstrate a working-level knowledge of 10 CFR 830.202, Safety Basis and DOE-STD-1027, with respect to its impact on department nuclear safety.

- Describe when a contractor must establish a safety basis for a facility.

If a contractor is responsible for a hazard category 1, 2, or 3 DOE nuclear facility, the contractor must establish and maintain the safety basis for the facility.

Describe the requirements for the safety basis.

The safety basis must

define the scope of the work to be performed;

identify and analyze the hazards associated with the work;

categorize the facility consistent with DOE–STD–1027–92;

prepare a documented safety analysis for the facility;

establish the hazard controls upon which the contractor will rely to ensure adequate protection of workers, the public, and the environment.

Describe the requirements the contractor must perform to maintain the safety basis.

In maintaining the safety basis for a hazard category 1, 2, or 3 DOE nuclear facility, the contractor responsible for the facility must:

update the safety basis to keep it current and to reflect changes in the facility, the work, and the hazards as they are analyzed in the documented safety analysis;

annually submit to DOE either the updated documented safety analysis for approval or a letter stating that there have been no changes in the documented safety analysis since the prior submission;

incorporate in the safety basis any changes, conditions, or hazard controls directed by DOE.

Discuss the purpose and determine the hazard categorization of an operating nuclear facility.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Describe the exclusion types for radionuclides associated with hazard categorization determination.

Sealed radioactive sources that are engineered to pass the special form testing specified by the Department of Transportation (DOT) in 49 CFR 173.469 or testing specified by American National Standards Institute (ANSI) N43.6, Sealed Radioactive Sources, may be excluded from summation of a facility’s radioactive inventory.  The facility must have documentation that the source or prototypes of the source have been tested and have passed the tests specified by DOT or ANSI.  Facilities must also have in place a source control policy that complies with DOE Notice 5400.9, Sealed Source Control Policy, and the source control policy specified in Article 431 of the DOE RadCon Manual.  Should a sealed radioactive source fail, as indicated by an increase in the removable activity, the source shall be removed from service and handled in accordance with the source control policy established for the facility.  Hazardous materials used in exempted, commercially available products should not be considered part of a facility’s inventory.  These materials include timepieces, illumination devices, thermostats, electron tubes, microwave receiver tubes, etc.  Additionally, material contained in DOT Type B shipping containers may also be excluded from summation of a facility’s radioactive inventory if the certificates of compliance are kept current and the materials stored are authorized by the certificate.  However, Type B containers without overpack should have heat protection provided by the facility’s fire suppression system.  These exclusions do not apply to fissile material in the determination of hazard category 2 status relative to criticality.

Describe the differences between initial and final hazard categorizations and where these designations occur in the DSA development process.

The initial hazard categorization is specified in the preliminary assessment of facility hazards.  Once a hazards analysis has been performed, the hazard categorization can be finalized.  The final categorization is based on an “unmitigated release” of available hazardous material.  For the purposes of hazard categorization, “unmitigated” is meant to consider material quantity, form, location, dispersibility, and interaction with available energy sources, but not to consider safety features which will prevent or mitigate a release.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of Department of Energy (DOE) O 420.1A, Facility Safety, DOE G 420.1-1, Nonreactor Nuclear Safety Design Criteria and Explosive Safety Criteria Guide, for use with DOE O 420.1, Facility Safety, and DOE-STD-1020, Natural Phenomena Hazards Design and Evaluation Criteria for Department of Energy Facilities, with respect to its impact on Department nuclear safety.

- Discuss the purpose and policy associated with DOE O 420.1A, Facility Safety.

The purpose of this Order is to establish facility safety requirements for DOE/NNSA for

nuclear safety design

criticality safety

fire protection

natural phenomena hazards mitigation

a system engineer program

This Order applies to all DOE/NNSA facilities with responsibility for DOE-owned or DOE-leased facilities as follows:

All DOE nuclear and non-nuclear facilities

All DOE nonreactor nuclear facilities that are classified as hazard category 1, 2, or 3

All DOE explosives facilities

All DOE hazard category 1, 2, and 3 nuclear facilities

Discuss the role of department nuclear safety specialists with respect to the implementation of the requirements of DOE Order 420.1A, Facility Safety.

Nuclear safety specialists as directed by the cognizant Secretarial Officer, shall ensure that the requirements falling within the scope of this order are in compliance with this order.  Nuclear safety specialists are responsible for determining whether adequate protection can most effectively be achieved by continuing to operate under the terms of existing contracts requiring compliance with old orders or by modifying the contract to incorporate the requirements of revised orders.  Nuclear safety specialists are responsible for determining that implementation of new rule or order requirements will provide adequate protection prior to requesting contract modification to drop old order requirements from a contract.

Discuss the department policy and objectives with respect to safety-class and safety-significant criteria.

Some principles that should be incorporated in a functional classification process are listed below:

Protection of the public is contributed to by all facets of safety in design, including safety-class SSCs as well as safety-significant SSCs, and, in many DOE cases, by remote sitting.  The expectation is that public design basis accident dose consequences would generally be a small fraction of the evaluation guideline.

Protection of the public is predominant in safety design; protection of workers is no less important.  However, the degree of protection for facility workers achievable by SSCs is limited.  Other factors such as disciplined conduct of operations, training, and safety management programs are no less important in assuring worker safety.

In prioritization of items for a facility safety strategy

minimization of hazardous materials (material at risk) is the first priority

safety SSCs are preferred over ACs

passive SSCs are preferred over active SSCs

preventative controls are preferred over mitigative controls

facility safety SSCs are preferred over personal protective equipment

controls closest to the hazard may provide protection to both workers and the public

controls that are effective for multiple hazards can be resource effective

Discuss the facility and activity applicability of DOE O 420.1A, with respect to implementation associated with the design of nuclear facilities.

DOE O 420.1A requirements apply to the design and construction of new hazard category 1, 2, and 3 DOE nonreactor nuclear facilities and to the design and construction of modifications to existing DOE hazard category 1, 2, and 3 non-reactor nuclear facilities when the proposed modifications significantly degrades the approved safety basis for the facility.  Modifications to facility design and construction during the design and construction phase shall conform to the requirements for new facilities.  If explosives are also present in the facility, the design will also consider the requirements of TM5-1300, Structures to Resist the Effects of Accidental Explosions.

Identify and discuss the use of DOE standards for seismic safety.

Executive Order 12699 establishes the minimum seismic requirements for new Federal buildings.  The National Earthquake Hazards Reduction Program (NEHRP) updates the provisions required to meet these requirements every 3 years.  The Interagency Committee on Seismic Safety in Construction (ICSSC) compares model building codes with the NEHRP provisions.  Designers must consider the NEHRP provisions and ICSSC comparisons to ensure the use of the proper model building code in their design and evaluation.  Currently the International Building Code (IBC) 2000 and American Society of Civil Engineers (ASCE) 7-98 meet the requirements of the NEHRP provisions.  While using the IBC 2000 or successor documents, designers must consider the Seismic Use Group and Seismic Design Category.

Evaluations of existing SSCs must follow, or at least be measured against, the natural phenomena hazards (NPH) criteria provided in DOE-STD-1020.  For SSCs not meeting these criteria and which cannot be easily remedied, budgets and schedule for required strengthening must be established on a prioritized basis.  In addition, it is consistent with the intent of the federal program developed by the ICSSC.  When upgrading becomes necessary, the design should be based on the current design criteria in the standard for the new facility.  DOE G 420.1-2 provides guidance for facilities with a remaining service life of less than 5 years.

Define PC-1, PC-2, PC-3 and PC-4 and their relationship to nuclear facility design and the DSA.

| Performance Category (PC) | Performance Goal Description | NPH Performance Goal Annual Probability of Exceeding Acceptable Behavior Limits, PF |
| --- | --- | --- |
| 1 | Maintain Occupant Safety | 10-3 of the onset of SSC damage to the extent that occupants are endangered |
| 2 | Occupant Safety, Continued Operation with Minimum Interruption | 5x10-4 of SSC damage to the extent that the component cannot perform its function |
| 3 | Occupant Safety, Continued Operation, Hazard Confinement | 10-4 of SSC damage to the extent that the component cannot perform its function |
| 4 | Occupant Safety, Continued Operation, Confidence of Hazard Confinement | 10-5 of SSC damage to the extent that the component cannot perform its function |

The design and evaluation criteria for SSCs in Performance Categories 1 and 2 are similar to those given in model building codes.  Performance Category 1 criteria include no extra conservatism against natural phenomena hazards beyond that in model building codes that include earthquake, wind, and flood considerations.  Performance Category 2 criteria are intended to maintain the capacity to function and to keep the SSC operational in the event of natural phenomena hazards.  Model building codes would treat hospitals, fire and police stations, and other emergency-handling facilities in a similar manner to DOE-STD-1020 Performance Category 2 NPH design and evaluation criteria.  Performance Category 3 and 4 SSCs handle significant amounts of hazardous materials or have significant programmatic impact.  Damage to these SSCs could potentially endanger worker and public safety and the environment or interrupt a significant mission.  As a result, it is very important for these SSCs to continue to function in the event of natural phenomena hazards, such that the hazardous materials may be controlled and confined.  For these categories, there must be a very small likelihood of damage due to natural phenomena hazards.  DOE-STD-1020 NPH criteria for Performance Category 3 and higher SSCs are more conservative than requirements found in model building codes and are similar to Department of Defense criteria for high risk buildings and NRC criteria for various applications.

Discuss aspects of fire protection and fire hazards analysis and their relationship to nuclear facility design and the DSA.

The DOE and its contractors possess a variety of processes for analyzing fire hazards at a facility, activity, and job.  However, the outcome and assumptions of these processes have not always been consistent for similar types of hazards within the safety analysis and the fire hazard analysis.  Although the safety analysis and the fire hazard analysis are driven by different DOE Orders and requirements, these analyses should not be entirely independent and their preparation should be integrated to ensure consistency of assumptions, consequences, design considerations, and other controls.  Under the DOE policy to implement an integrated safety management system, identification of hazards must be evaluated and agreed upon to ensure that the public, the workers, and the environment are protected from adverse consequences.  If integrated safety management is not incorporated into the preparation of the safety analysis and the fire hazard analysis, inconsistencies between assumptions, consequences, design considerations, and controls may occur that affect safety.  In accordance with the integrated safety management system approach for having a uniform and consistent process, a method has been suggested by the DOE for determining when fire hazard analyses and safety analyses are required.

Identify and discuss the strengths and weaknesses of methods utilized to analyze the initiation and propagation of fires, and of their potential release of hazardous materials.

Fire hazards analyses (FHAs) must be developed for all nuclear facilities, significant new facilities, and facilities that represent unique or significant fire safety risks.  The FHA shall be developed using a graded approach.  The conclusions of the FHA shall be incorporated in the SAR Accident Analysis and shall be integrated into design basis and beyond design basis accident conditions.

DOE Elements and contractors shall develop, implement, and maintain a comprehensive fire protection program for facilities that includes

a reliable water supply of adequate capacity for fire suppression;

noncombustible or fire-resistive construction, where appropriate;

complete fire-rated barriers that are commensurate with the fire hazard to isolate hazardous occupancies and to minimize fire spread and loss potential consistent with defined limits as established by DOE;

automatic fire extinguishing systems throughout all significant facilities and in all areas subject to loss of safety-class systems, significant life-safety hazards, unacceptable program interruption, or fire loss potential in excess of defined limits;

redundant fire protection systems in areas where safety-class systems are vulnerable to fire damage and where no redundant safety capability exists outside of the fire area;

in new facilities, redundant safety-class systems in separate fire areas;

redundant fire protection systems provided in areas where the maximum possible fire loss (MPFL) exceeds limits established by DOE;

a means to summon the fire department in the event of a fire, such as a fire alarm signaling system;

a means to notify and evacuate building occupants in the event of a fire, such as a fire detection or fire alarm system and illuminated, protected egress paths;

physical access and appropriate equipment to facilitate effective intervention by the fire department, such as an interior standpipe system(s) in multi-story or large facilities with complex configurations;

a means to prevent the accidental release of significant quantities of contaminated products of combustion and fire fighting water to the environment, such as ventilation control and filter systems and curbs and dikes.

Such features would only be necessary if required by the FHA or SAR in conjunction with other facility or site environmental protection measures.

Fire and related hazards that are unique to DOE and are not addressed by industry codes and standards shall be protected by isolation, segregation, or use of special fire control systems, such as inert gas or explosion suppression, as determined by the FHA.  Fire protection systems shall be designed such that their inadvertent operation, inactivation, or failure of structural stability will not result in the loss of vital safety functions or inoperability of safety-class systems as determined by the SAR.

Identify and discuss the methods used to determine the seismic hazard level to be used in design.

Seismic design or evaluation of PC-1 and PC-2 SSCs is based on model building code seismic provisions.  In these criteria, the current version of the International Building Code shall be followed.  All of the IBC 2000 seismic provisions shall be followed for PC-1 and PC-2 SSCs.  Load combinations to be used for PC-1 and PC-2 will be based on the provisions in the IBC 2000.  Use of site-specific data will be limited per provisions of IBC 2000.  Post-Northridge earthquake SAC recommendations should be taken into consideration for steel structures.

For systems and components, seismic design forces are accounted as per the IBC 2000 provisions.  If a recent site-specific seismic hazard assessment is available, it can be used subject to limitations imposed in the IBC 2000.  For evaluation of SSCs using site-specific hazard analysis, the design shall be based on 5 percent critical damping as recommended by the IBC 2000.  Final earthquake loads are subject to approval by DOE.  A quality assurance program consistent with model building code requirements shall be implemented for SSCs in Performance Categories 1 and 2.  In addition, peer review shall be conducted for Performance Category 2 SSCs.

Identify and discuss the methods used to assess the structural response of structures and determine whether safety systems may be expected to remain functional following an earthquake of postulated intensity.

For PC-2 and lower SSCs, the seismic design and evaluation criteria employ the IBC 2000 seismic provisions with the exception that site-specific information may be used if appropriate to define the earthquake input excitation used to establish seismic loadings.  The maximum ground acceleration and ground response spectra determined in the manner defined in IBC 2000 are used in the appropriate terms of the IBC 2000 equation for base shear.  Use of site-specific earthquake ground motion data is considered to be preferable to the general seismic zonation maps from the IBC 2000 with limitations imposed in the IBC 2000 Code.  IBC provisions require a static or dynamic analysis approach in which loadings are scaled to the base shear equation value.  Elastically computed seismic response is reduced by “R” values ranging from 1¼ to 8 as a means of accounting for inelastic energy absorption capability in the IBC provisions and by these criteria for PC 2 and lower SSCs.  This reduced seismic response is combined with non-seismic concurrent loads and then compared to code allowable response limits (or code ultimate limits combined with code specified load factors).  Normally, relative seismic anchor motion (SAM) is not considered explicitly by model building code seismic provisions.  The International Building Code (IBC 2000) has been followed for PC-1 and PC-2 because it is the only the current model building code meeting NEHRP provisions.  The ICSSC has concluded that the following seismic provisions are substantially equivalent:

International Building Code, IBC 2000

1997 NEHRP Recommended Provisions

ASCE 7-98

The other model building codes may be followed provided site-specific ground motion data is incorporated into the development of earthquake loading similar to the manner described in this document for the IBC 2000.  For PC-3 and PC-4 SSCs, the seismic design and evaluation criteria specify that seismic evaluation be accomplished by dynamic analysis.  The recommended approach is to perform an elastic response spectrum dynamic analysis to evaluate elastic seismic demand on SSCs.  However, inelastic energy absorption capability is recognized by permitting limited inelastic behavior.  By these provisions, inelastic energy absorption capacity of structures is accounted for by the parameter, “Fµ.”  Elastically computed seismic response is reduced by Fµ values ranging from 1 to 3 as a means of accounting for inelastic energy absorption capability for more hazardous facilities.  Fµ values are much lower than R values, increasing the risk reduction ratio.  By these provisions, only the element forces due to earthquake loading are reduced by Fµ.  The same Fµ values are specified for both PC-3 and PC-4.  In order to achieve different risk reduction ratios appropriate for the different performance categories, the reduced seismic response is multiplied by a seismic scale factor.  Different seismic scale factors (SF) are specified for PC-3 and PC-4.  The resulting scaled inelastic seismic response is combined with non-seismic concurrent loads and then compared to code ultimate response limits.  The design detailing provisions from the ACI 349, which provide ductility, toughness, and redundancy, are also required such that SSCs can fully realize potential inelastic energy absorption capability.  Also, explicit consideration of relative SAM effects is required for PC-3 and higher.  For PC-3 or higher, the dynamic analysis based deterministic seismic acceptance criteria specified herein are independent of both the desired risk reduction ratio and the performance category specified, other than for the seismic scale factor, SF.  Thus, the deterministic acceptance criteria herein may be used over a wide range of applications including special situations where the desired seismic performance goal differs.

For PC-2 and lower SSCs, see IBC provisions. For PC-3 and higher SSCs

perform dynamic analysis considering the mass and stiffness distribution of the structure;

perform an elastic response spectrum analysis, but to permit limited inelastic behavior.  Elastic seismic response is reduced by the factor, Fµ, to obtain inelastic seismic demand.  Explicitly account for relative displacement effects, where applicable.

Identify the methods for evaluating the tolerance of structures and systems for natural phenomenon.

The methods for evaluating the tolerance of structures and systems are presented in order of increasing rigor or decreasing conservatism.  Following the “graded approach” philosophy, the method to be used should be selected on the basis of cost-benefit considerations.  The end result of this step will be a preliminary performance category list for the NPH-related safety system components of the facility.

### Method I: System-by-System Categorization

In this method, the performance category of a given component of a safety system will be the same as the highest performance category applicable to any component of the system guidelines, irrespective of the safety function of the particular component.  Thus, all the components of a system will have the same performance category.  This is the most conservative of the three methods and the only applicable method if the safety function of only the entire system is known, and information on the safety function of individual components of the system is unavailable.

### Method II: Segment-by-Segment Categorization

A segment of a system is defined here as a group of components that perform a safety function.  It may also be defined as a group of components belonging to a system that are physically located in a certain area, room, or building, or whose functions are such that it may be more cost-effective, or programmatically more desirable, to design or procure them using the same NPH design criterion.  In Method II, all components belonging to a segment of an NPH-related safety system are placed in the highest performance category of any component in that segment.

### Method III: Component-by-Component Categorization

In this method, each component of the NPH-related safety system is categorized individually.  Thus, each component is categorized based on its own function, and not lumped with the entire segment or system.  Method III is the most rigorous of the three methods, but the other two methods are more conservative.  Use of this method can minimize the number of higher category components, and thereby reduce the components that must be designed for higher level NPH design loads.  However, in order to accomplish this, detailed system safety and accident analyses will be needed.

The data and information necessary to categorize these components may be partially available in the facility hazard categorization documents or facility safety and accident analysis reports.  If the available data are not adequate, additional data can be obtained cost-effectively through a facility walkdown and by interviewing facility operations and maintenance personnel.  It may also be necessary to review design documents and operation manuals and procedures.

Components, failures of which can cause these situations, can be identified most effectively by a facility walkdown or by a careful evaluation of building layout plans and drawings.  A convenient and efficient method of categorizing a large number of these types of SSCs would be to group them on the basis of their NPH related characteristics or locations.

Following the “graded approach” philosophy, the rigor with which such failure potentials are to be determined should depend on the safety significance and the preliminary performance category of the target, the hazard category of the facility, and the relative costs of various methods of determining target failure potentials.  In the following paragraphs, two methods of assessing target failure potentials are presented in order of decreasing rigor.

### Systematic Analysis Method

Target failure potentials can be assessed using a qualitative but systematic approach by constructing a fault-tree of the scenario.  If justifiable from cost-benefit considerations, this may be a desirable method when necessary data for fault tree construction are available.  Generally, it should be used when the failure of the target is dependent on a large and complex chain of events that may follow the failure of the source, or to qualify a large system in its entirety.  Component-by-component application of this method is unlikely to be cost-effective.

### Approximate Method

In this method, the effects of source failure on a target are modeled approximately but rationally, considering possible scenarios identified by a facility walkdown.  Even though such models are approximate, their evaluation provides qualitative information that is often adequate for the purpose.

The consideration of adverse effects of system interaction of one component or system (source) on another (target) is very important in determining the performance categories of SSCs.  Adverse interaction effects can be different for different systems.  Examples of typical adverse interaction effects are listed below:

Structural failure and falling.  Inadequately designed, inadequately anchored, and unanchored components may fail, slide, and/or topple and fall on or bump into other components that are not designed to withstand such interaction effects.

Proximity and impact.  Adjacent components may impact each other, causing damage if the clearance between them is inadequate for NPH-induced deflections.  Such adverse interaction may occur even if the deflection of the source is within its design limits.

Differential displacement.  A target distribution system may span between different structural systems (source).  Differential displacements between the structural systems may be within acceptable behavior limits for the structures, but may still affect the distribution system adversely.

Mechanical or electrical failure.  The failure of a source mechanical or electrical component may impair the safety function of another component or system.

## Nuclear safety specialists shall demonstrate a working-level knowledge of the Technical Safety Requirements as described in 10 CFR 830.205, Technical Safety Requirements and DOE Guide 423.1-1, with respect to its impact on Department nuclear safety.

- Discuss the purpose of Technical Safety Requirements.

TSRs identify the limitations of each DOE owned, contractor operated nuclear facility based on the documented safety analysis and any additional safety requirements established for the facility.

Describe the responsibilities of contractors authorized to operate defense nuclear facilities for Technical Safety Requirements.

Contractors, in the preparation of DSAs, identify how the safety requirements of the safety management rule apply to a specific facility, and describe how the contractor undertakes to design, build, and operate the facility to be in conformance with the applicable statutes and DOE rules and directives to ensure facility safety.  The analysis of operations and accidents defines the limits of safe operations, identifies the required performance of safety-class and safety-significant SSCs, and describes any ACs or procedures that are necessary to meet the specific safety criteria for the facility.

Define the following terms and discuss the purpose of each:

Safety limits

Operating limits

Limiting control settings

Limiting conditions for operation

Surveillance requirements

Administrative controls

### Safety Limits (SLs)

SLs are the limits on process variables associated with those safety-class physical barriers, generally passive, that are necessary for the intended facility functions and which are required to guard against the uncontrolled release of radioactive materials.

### Operating Limits (OLs)

OLs are the limits required to ensure the safe operation of a nuclear facility, including limiting control settings and limiting conditions for operation.

### Limiting Control Settings (LCSs)

LCSs are boundaries on safety systems that regulate process variables to prevent exceeding a safety limit.

### Limiting Conditions of Operation (LCOs)

LCOs are the limits that represent the lowest functional capability or performance level of safety SSCs required for safe operations.

### Surveillance Requirements (SRs)

SRs are requirements relating to testing, calibration, or inspection to ensure the necessary operability and quality of safety SSCs and their support systems required for safe operations.

### Administrative Controls

ACs are provisions relating to organization and management procedures, record keeping, assessment, and reporting necessary to ensure the safe operation of a facility.

Discuss the margin of safety in a TSR.

TSRs set forth the minimum acceptable limits for operation under normal and specified failure conditions; they ensure that the available equipment and initial conditions meet the assumptions in the accident analysis.  The bases for TSRs define the acceptance limits from which margins of safety may be determined.

Describe the general content of each of the following sections of the Technical Safety Requirements:

Use and application

Basis

Design features

### Use and Application

The use and application section of the TSR should contain basic information and instructions for using and applying the TSR.  The following elements should be addressed under separate headings in this section:

Definitions.  Provide an alphabetical list of terms used throughout the TSR and their corresponding definitions.  Include a note on the first page of the list stating that defined terms appear in uppercase type throughout the TSR.

Operational modes (reactors).  Define the operational modes for reactor facilities and state that in the interest of uniformity, the operational conditions or modes listed are preferred and an attempt should be made to fit each reactor facility into this scheme.

Operational modes (nonreactor nuclear facilities).  Define the operational modes for nonreactor facilities and state that in the interest of uniformity, the operational conditions and modes listed are preferred and an attempt should be made to fit each nonreactor nuclear facility into this scheme.  If, however, a nonreactor nuclear facility cannot be made to fit, modes may be defined as needed, provided the definitions are clear and there are definite lines of demarcation between modes.

Frequency notation.  The frequency notations, as used in the surveillances and elsewhere, should be defined when included in the TSR.

### Basis

The TSR basis provides summary statements of the reasons for the selection of each specific SL, OL, and SR.  The bases show how the numerical values, conditions, surveillances, and action statements fulfill the purpose derived from the safety documentation.  Included in the basis should also be a description of the safety functions that each safety system provides and identification of what is included in each safety system.

### Design Features

This section describes those design features that, if altered or modified, would have a significant effect on the safe operation of the facility.  The important attributes of the passive design features that are taken credit for in the accident analysis should be described completely.  These design features are normally passive characteristics of the facility not subject to change by operations personnel, e.g., shielding, structural walls, relative locations of major components, installed poisons, or special materials.  Active safety features are normally described in the DSA and are the subject of the various TSRs, so they are not normally described in the design features section.  All changes or modifications that impact the safety basis of the facility are subject to the USQ process.

Discuss the definition and implementation principles for the term OPERABILITY as used in a Technical Safety Requirement.

Operability embodies the principle that a system, subsystem, train, component, or device can perform its safety function(s) only if all necessary support systems are capable of performing their related support functions.  A system or component can be degraded but still operable if it remains capable of performing its required safety function at the level assumed in the accident analysis.  If systems, components, or equipment are observed to be functioning, but under stress, then judgment must be used concerning a declaration of inoperability.  General principles of operability should be followed in generating LCOs:

General principle 1.  A system is considered operable as long as there exists assurances that it is capable of performing its specified safety function(s).

General principle 2.  A system can perform its specified safety function(s) only when all of its necessary support systems are capable of performing their related support functions.

General principle 3.  When all systems designed to perform a certain safety function are not capable of performing that safety function, a loss of function condition exists.

General principle 4.  When a system is determined to be incapable of performing its intended safety function(s), the declaration of inoperability should be immediate.

Discuss the relationship of functional requirements and performance criteria to the Technical Safety Requirements.

TSRs define the performance requirements of SSCs and identify the safety management programs used by personnel to ensure safety.  TSRs are aimed at confirming the ability of the SSCs and personnel to perform their intended safety functions under normal, abnormal, and accident conditions.  These requirements are identified through hazard analysis of the activities to be performed and identification of the potential sources of safety issues.  Safety analyses to identify and analyze a set of bounding accidents that take into account all potential causes of releases of radioactivity also contribute to development of TSRs.  Through analyses of the encompassing bounding accidents, the necessary safety systems and accident mitigating systems are identified and their characteristics are defined.  Flowing from the analyses is information that provides the bases for controls, limits, and conditions for operation, known as TSRs.  The content of the DSA must remain valid so that the safety basis of the facility, as implemented in operations through the TSR, remains valid.  Therefore, there is a commitment to the process of unreviewed safety questions regarding any proposed change to the facility or its operations as described in the DSA.  Likewise, all changes to the TSR bases presented in the DSA should be incorporated into the TSRs to ensure the information contained therein reflects the current safety basis of the facility.  Any proposed revision to a TSR should be examined to ensure the basis for the change is supported in the DSA.  The TSR rule requires that such revisions be submitted to DOE for review with the basis for the proposed change.  The change to the TSR must be approved by DOE before it is implemented.

Discuss the conditions that constitute a violation of the Technical Safety Requirements and state the reporting requirements should a violation occur.

Although the TSR elements have an importance hierarchy, a TSR violation can occur for each type of TSR.  Violations of a TSR occur as a result of the following four circumstances:

Exceeding an SL

Failure to complete an action statement within the required time limit following exceeding an LCS or failing to comply with an LCO

Failure to perform a surveillance within the required time limit

Failure to comply with an AC statement

Failure to comply with an AC statement is a TSR violation when either the AC is directly violated, as would be the case with not meeting minimum staffing requirements for example, or the intent of a referenced program is not fulfilled.  To qualify as a TSR violation, the failure to meet the intent of the referenced program would need to be significant enough to render the DSA summary invalid.  TSR violations involving SLs require the facility to begin immediately to go to the most stable, safe condition attainable, including total shutdown.  A grace period is sometimes provided to perform a missed surveillance to provide time for the performance of the missed surveillance, thereby avoiding the need for a facility to take immediate, possibly unnecessary corrective action.  Entering the grace period remains a TSR violation even though an immediate corrective action may not be required.

Reporting of all TSR violations should be made in accordance with the provisions of DOE O 232.1A, Occurrence Reporting and Processing of Operations Information.  The reporting of violations on ACs can involve judgment since the details of programs, like a program for criticality control, do not appear directly as a TSR, and some program requirements are more important than others.  Violations of controls identified in the accident or criticality scenarios in the DSA should be reported as if they were TSR violations.  To ensure consideration for mitigation in potential enforcement actions, identified TSR violations should be evaluated for voluntary reporting to the DOE Noncompliance Tracking System.

Discuss the requirements for administrative control of the Technical Safety Requirements.

ACs are the provisions relating to organization and management, procedures, record keeping, reviews, and audits necessary to ensure safe operation of the facility.  ACs may include reporting deviations from TSRs, staffing requirements for facility positions important to safe operation of the facility, ACs of the criticality safety program, and commitments to safety management programs important to worker safety.  In general, the ACs should document all those administrative functions that are required to meet facility safety criteria as identified in the DSA, including commitments to safety management programs.  It is expected that the ACs will be tailored to the facility activities and the hazards identified in the DSA.  This tailoring should be a direct result of the DSA, but it may also result from institutional requirements that address many facilities.  As a general practice, safety controls for individual accident scenarios based on engineered SSCs are preferred to ACs because they are usually more reliable and more predictable.  The tendency to use ACs as an expedient alternative to an LCO or LCS should be avoided when possible.  Efforts should be made to use engineered SSCs whenever possible for controlling the likelihood and consequences of accidents.  ACs should be considered for defense in depth rather than the primary or redundant controls.  While ACs may be acceptable for ensuring safe operation, their generally lower reliability, compared with engineered controls, should be evaluated carefully when choosing safety measures for long-term hazardous activities.  Human actions, taken either in response to an event or taken proactively to establish desired conditions, are subject to errors of omission or commission.  Sets of ACs are prone to common cause failure.  The following attributes, which can be tailored as appropriate, can increase reliability:

Use of reader/worker/checker systems

Independent verification

Positive feedback systems

Human factor analysis

Operator training and certification

Continuing training and requalification

Abnormal event response drills

Ergonomic considerations in procedures

When invoking ACs for control of accident scenarios, the preceding attributes, appropriate to the consequences of the accidents they are intended to prevent, should be considered and also invoked.

Discuss the possible source documents that may be used in developing technical safety requirements.  Discuss the role of documented safety analyses in selecting technical safety requirements and the respective flowdown.

The primary source document is the DSA for that facility.  Other inputs come from existing technical safety or operational safety documents that may exist for the facility.  Also, DOE-STD-3009-94, Preparation Guide for U.S. Department of Energy Nonreactor Nuclear Facility Safety Analysis Reports, along with DOE G 423.1-1 Implementation Guide for Use in Developing Technical Safety Requirements, may be used in developing TSRs.

The documented safety analysis identifies hazards that need to be analyzed.  This hazard analysis creates accident scenarios that identify accident conditions and risks.  Controls are developed to mitigate against the derived accidents.  These controls are what the TSRs identify as important to safety.  The safety-significant and safety-class controls have prescribed TSRs that are used to ensure they are able to meet their given requirements as part of the safety envelope.

Differentiate between the following facility designations:

Category A reactor facility

Category B reactor facility

### Category A Reactor Facility

Category A reactor facilities are production, test, and research reactors designated by DOE based on power level (e.g., design thermal power rating of 20 megawatts steady state and higher), potential fission product inventory, and experimental capability.

### Category B Reactor Facilities

Category B reactor facilities are test and research reactors designated by DOE based on power level (e.g., design thermal power rating of less than 20 megawatts steady state), potential fission product inventory, and experimental capability.

Discuss the requirements for emergency actions that depart from the approved Technical Safety Requirements.

In an emergency, if a situation develops that is not addressed by the TSR, site personnel are expected to use their training and expertise to take actions to correct or mitigate the situation.  Also, site personnel may take actions that depart from the requirements of a TSR provided (a) an emergency situation exists, (b) these actions are needed immediately to protect workers, the public, or the environment from imminent and significant harm, and (c) no action consistent with the TSR is immediately apparent.  Such action must be approved by a certified operator for reactor facilities or by a person in authority as designated in the TSRs for nonreactor nuclear facilities.  If emergency action is taken, both a verbal notification should be made to the responsible head of the field element and a written report made to the cognizant Secretarial Officer (CSO) within 24 hours.

Discuss the provisions a contractor may follow to develop alternatives to Technical Safety Requirements for environmental restoration activities.

A contractor for an environmental restoration activity may follow the provisions of 29 CFR 1910.120 or 1926.65 for construction activities to develop the appropriate hazard controls (rather than TSR guidance) provided the activity involves either (1) work not done within a permanent structure, or (2) the decommissioning of a facility with only low-level residual fixed radioactivity.  Implicit in this guidance is an understanding that reasonable efforts to remove radioactive systems, components, and stored materials has been completed and that the work does not prudently require the use of active safety systems or components designed to prevent or mitigate the accidental release of hazardous radioactive materials.  DOE-STD-1120-98 also provides guidance that should be considered in the development of alternatives to TSRs.

Discuss the requirements for the contractor to maintain the Technical Safety Requirements current.

As with all hazard controls, TSRs must be kept current and reflect changes in the facility, the work, and the hazards as they are analyzed in the documented safety analysis.  In addition, DOE expects a contractor to maintain TSRs, and other hazard controls as appropriate, as controlled documents with an authorized users list.

Discuss the application of the graded approach relative to Technical Safety Requirements.

The graded approach is not directly applicable to the TSRs required by 10 CFR 830.205.  However, the graded approach is specified for DSAs required by 10 CFR 830.204.  Thus, the level of detail in the DSA, and the number of safety parameters identified in the DSA section deriving the TSRs, will have a direct effect on the number and type of resulting TSRs.

Perform a review of a safety-class or safety-significant SSC including walking down the associated surveillance requirements and LCO/LCS.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

## Nuclear safety specialists shall demonstrate a working-level knowledge of 10 CFR 830.203, Unreviewed Safety Question Process and DOE Guide 423.1-1, with respect to its impact on Department nuclear safety.

- Discuss the purpose of the Unreviewed Safety Question process.

The unreviewed safety question (USQ) process allows contractors to make physical and procedural changes and to conduct tests and experiments without prior DOE approval if the proposed change can be accommodated within the existing safety basis.

Discuss the reasons for performing an Unreviewed Safety Question determination.

A USQ is expected to be implemented using contractor procedures that ensure that proposed changes to physical characteristics or operating procedures are adequately evaluated relative to the approved safety basis, and that those proposed changes determined to involve USQs are brought to the attention of DOE for review and approval before changes are made.  A proposed change or test involves a USQ if

the probability or consequences of an accident or malfunction of equipment important to safety could be increased

the possibility of a different type of accident than previously evaluated in the DSA could be introduced

margins of safety could be reduced

Define the following terms:

Discrepant as-found condition

Potential inadequacy in the safety analysis

Proposed change

### Discrepant As-Found Condition

A discrepant as-found condition is a situation where the actual physical configuration of equipment important to safety in the facility does not match the DSA.  This may result from an error in the DSA or an error in the facility configuration.

### Potential Inadequacy in the Safety Analysis (PISA)

A PISA is a condition in which the safety basis may be inadequate or the physical condition may not be accurate because the safety analysis may not match the current physical configuration of the facility or the safety analysis may be inappropriate or may contain errors.

### Proposed Change

A proposed change is a suggested modification to the configuration of a facility.

Define the conditions for an Unreviewed Safety Question.

The conditions that require a USQ are listed below:

Temporary or permanent changes in the facility

Temporary or permanent changes in the procedures

Tests or experiments not described in the existing DSAs

Discovery of potential inadequacies in the existing safety analyses

Describe the responsibilities of contractors authorized to operate defense nuclear facilities for the performance of safety evaluations.

The contractor responsible for a hazard category 1, 2, or 3 DOE nuclear facility must obtain approval from DOE for the methodology used to prepare the documented safety analysis for the facility unless the contractor uses a methodology approved by DOE.

The documented safety analysis for a hazard category 1, 2, or 3 DOE nuclear facility must, as appropriate for the complexities and hazards associated with the facility

describe the facility (including the design of safety SSCs) and the work to be performed;

provide a systematic identification of both natural and man-made hazards associated with the facility;

evaluate normal, abnormal, and accident conditions, including consideration of natural and man-made external events, identification of energy sources or processes that might contribute to the generation or uncontrolled release of radioactive and other hazardous materials, and consideration of the need for analysis of accidents which may be beyond the design basis of the facility;

derive the hazard controls necessary to ensure adequate protection of workers, the public, and the environment; demonstrate the adequacy of these controls to eliminate, limit, or mitigate identified hazards; and define the process for both maintaining the hazard controls current at all times and controlling their use;

define the characteristics of the safety management programs necessary to ensure the safe operation of the facility, including (where applicable) quality assurance, procedures, maintenance, personnel training, conduct of operations, emergency preparedness, fire protection, waste management, and radiation protection.

With respect to a nonreactor nuclear facility with fissionable material in a form and amount sufficient to pose a potential for criticality, the DSA must define a criticality safety program that

ensures that operations with fissionable material remain subcritical under all normal and credible abnormal conditions

identifies applicable nuclear criticality safety standards

describes how the program meets applicable nuclear criticality safety standards

Describe the actions to be taken by a contractor upon identifying information that indicates a potential inadequacy of safety analyses or a possible reduction in the margin of safety as defined in the Technical Safety Requirements.

Because an inadequacy in the safety analyses has the potential to call into question information relied on for authorization of operations, DOE requires the contractor to do the following:

Take appropriate action to place or maintain the facility in a safe condition.

Expeditiously notify DOE when the information is discovered.

Perform a USQ determination and submit the results promptly.

Complete an evaluation of the safety of the situation and submit it to DOE before removing any operational restrictions implemented to compensate for the analytical discrepancy.

The third bulleted item, above, means that the USQ determination should be prepared promptly and the results submitted promptly.  This is also intended to mean that the time frame after initial notification of DOE until submittal of the USQ determination results should be on the order of hours or days, not weeks or months.  If a USQ is determined to be present, the evaluation of the safety of the situation will require not only DOE’s review but also its approval of resulting changes before any operational restrictions are removed.

Discuss the qualification and training requirements for personnel who perform safety evaluations.

Implementing procedures should establish the personnel training and qualifications needed to perform the USQ process.  These include required educational background, years and/or types of work experience, knowledge of the facility, understanding of DOE requirements related to the facility safety basis (including the USQ process), and familiarity with the facility-specific safety basis.  All personnel responsible for preparing, reviewing, or approving USQ documents should receive training on the application of Section 830.203, including any facility-specific procedures. The recommended interval for retraining is every two years.  The contractor should maintain a list of those personnel who are currently qualified to perform the USQ process.

Discuss the actions to be taken if it is determined that a Potential Inadequacy in the Safety Analysis is involved.

If the safety analysis is found to have a potential inadequacy, the following actions must be taken:

Take appropriate action to place or maintain the facility in a safe condition.

Expeditiously notify DOE when the information is discovered.

Perform a USQ determination and submit the results promptly.

Complete an evaluation of the safety of the situation and submit it to DOE before removing any operational restrictions implemented to compensate for the analytical discrepancy.

Discuss the following terms as they apply to unreviewed safety questions:

Categorical exclusions

Prior unreviewed safety question determinations

Inconsequential changes

Margin of safety

Design/evaluation basis accidents

Important to safety

Safety basis

Restoration modification

Evaluation of safety

Unreviewed safety question

Justification for continued operations

### Categorical Exclusions

A categorical exclusion is valid when answers to the seven questions listed in section 3.3 of DOE G 424.1-1A, Implementation Guide for Use in Addressing Unreviewed Safety Question Requirements, would be “no” for every credible variation within the category.

### Prior Unreviewed Safety Question Determinations

Prior USQ determinations are USQs performed on facilities that were not previously part of the review process.

### Inconsequential Changes

Inconsequential changes are changes made to a facility or procedure that do not affect the safety basis.

### Margin of Safety

A margin of safety is defined by the range between two conditions.  The first is the most adverse condition estimated or calculated in safety analyses to occur from an operational upset or family of related upsets.  The second condition is the worst-case value known to be safe, from an engineering perspective.  This value would be expected to be related to the condition at which some accident prevention or mitigation action is taken in response to the upset or accident, not the actual predicted failure point of some component.

### Design/Evaluation Basis Accidents

Design/evaluation basis accidents are postulated accidents that evaluate normal, abnormal, and accident conditions that might be associated with the generation or release of radioactive or other hazardous materials.

### Important to Safety

Important to safety, with reference to SSCs, means those engineered features whose function is to prevent or mitigate category 2 event sequences.

### Safety Basis

The safety basis is comprised of the documented safety analysis and hazard controls that provide reasonable assurance that a DOE nuclear facility can be operated safely in a manner that adequately protects workers, the public, and the environment.

### Restoration Modification

Restoration modification refers to the restoration or modification of any equipment that may affect the safety basis.

### Evaluation of Safety

Evaluation of safety is the review of conditions that affect the safety of a system, facility, or component, and includes an evaluation of all components important to safety.

### Unreviewed Safety Question

A USQ exists in a situation where the following criteria are present:

The probability of the occurrence or the consequences of an accident or the malfunction of equipment important to safety previously evaluated in the documented safety analysis could be increased.

The possibility of an accident or a malfunction of a different type than any evaluated previously in the documented safety analysis could be created.

A margin of safety could be reduced.

The documented safety analysis may not be bounding or may be otherwise inadequate.

### Justification for Continued Operations

The justification for continued operations is the proposal to continue operations at a nuclear facility during long-term modifications or during decommissioning operations.

Discuss the responsibilities of the contractor associated with Unreviewed Safety Question summaries and the USQ procedure.

Contractors should develop procedures that provide detailed guidance for the performance of the USQ process, including procedures for screening and for developing the USQ determinations.  The procedures should:

define the purpose of the process;

set forth the process applicability;

provide definitions of appropriate terms, include screening criteria, as appropriate, and the basis for their application;

include detailed guidance on what must be considered and evaluated when performing or reviewing a USQ determination;

define the required qualifications and responsibilities of personnel performing and reviewing USQ determinations;

include documentation requirements for each USQ determination.

Describe DOE’s responsibilities when not agreeing with a negative determination.

DOE can declare that a USQ exists as part of its oversight responsibility of the USQ process.  Such a declaration might result from a disagreement with a contractor’s negative USQ determination or might result from a condition for which the contractor has not done a USQ determination.  When DOE declares a USQ, it is because DOE believes it should be involved in the review and approval of the situation to fulfill its responsibilities.

Discuss why the application of the graded approach does not apply to the USQ process.

The graded approach is applied to the USQ process only indirectly.  During the hazards analysis and safety analysis processes, equipment is classified as safety-class, safety-significant, “other” safety, or non-safety.  Once these classifications are established, they are used to indicate how much effort should be applied.  However, no steps of the USQ process can be eliminated based on such grading.  In some situations, attempts to apply the graded approach to the USQ process have resulted in inadequate USQ determinations.  The graded approach may give a rough indication of how much justification or basis information should be provided when explaining the answers to each of the seven USQ determination criteria.  More elaborate and thorough basis information would be expected for changes to safety equipment than for non-safety equipment.  In any case, the justification for the answers to the USQ determination criteria needs to be defensible.

Review a USQ Determination including walking down the proposed change/potential inadequacy.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

## Nuclear safety specialists shall demonstrate a familiarity level knowledge of the functional interfaces between safety system software components and the system level design.

- Identify how system-level requirements are established and then assigned to hardware, software, and human components of a digital instrumentation and control system.

A review of Software Requirements Engineering, edited by Thayer & Dorfman, IEEE Computer Society Press, 1997, should be conducted to determine requirements per DOE N 203.1.

Identify the typical requirements that define functional interfaces between safety system software components and the system-level design, as described in standards such as ANSI/IEEE 830, IEEE Guide to Software Requirements Specifications, and IEEE 7-4.3.2, Standard Criteria for Digital Computers in Safety Systems of Nuclear Power Generating Stations.  Identify where this information is documented.

A review of ANSI/IEEE 830 and IEEE 7-4.3.2 is required to compare how they integrate with DOE N 203.1

Identify the specific records that must be maintained and the requirements for maintaining these records to document the development of safety system software.

The records management system should have schedules for records retention and disposition in accordance with the requirements of DOE O 200.1, Information Management Program.

Review a development project for safety system software.  Explain how the functional interfaces between components and the system-level design were established and controlled.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the relationships between the problems being addressed by safety analysis and design codes, the design requirements for the codes, and the components of the codes.

- Identify how functional requirements and applicability of safety analysis and design computer codes are defined, documented, and controlled relative to modeling and data assumptions, design constraints, sizing and timing conditions, and input/output parameters.

Software used for safety analysis should come from the approved toolbox of software or DOE must approve a new software type if used.  The software must meet the criteria of DOE G 200.1-1, Software Engineering Methodology.

Review a development project for safety analysis or design software.  Explain how the problem being addressed by the software was translated into functional requirements, how the requirements were established and controlled, and how the code was reconciled with the original problem.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Discuss the DOE toolbox codes (reference http://tis.eh.doe.gov/techstds/toolbox_codes.html), their strengths, weaknesses and other factors governing their appropriate use and the applicable DOE standards and guides for modeling their phenomena.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of Department of Energy (DOE) Policy 450.4, Safety Management System Policy, and Policy 450.5, Line Environment, Safety and Health Oversight, as applied to nuclear safety.

- Discuss the fundamentals of Integrated Safety Management and their direct application to nuclear safety.

Following are the six components of the DOE safety management system:

Objective

Guiding Principles

Core Functions

Mechanisms

Responsibilities

Implementation

The purpose of DOE Policy 450.5 is to set forth the Department’s expectations for DOE line management environment, safety, and health (ES&H) oversight and for the use of contractor self-assessment programs as the cornerstone for this oversight.  An effective and efficient oversight program can be realized when a vigorous contractor self-assessment program is in place, similar to those used in successful companies.  DOE line oversight and contractor self-assessments together ensure that field elements and contractors are adequately implementing the DOE Safety Management System.  As a complement to DOE line oversight, the Department’s Office of Environment, Safety, and Health (EH) provides safety policy, enforcement, and independent internal oversight functions.

- Describe the key elements of an effective contractor self assessment nuclear safety program.

A robust, rigorous, and credible contractor ES&H self-assessment program linked to the DOE safety management system is in place, which includes elements that address the following:

Performance measures and performance indicators

Line and independent evaluations

Compliance with applicable requirements (rules, regulatory standards, contract terms)

Data collection, analysis, and corrective actions

Continuous feedback and performance improvement

The results and conclusions of the contractor self-assessments are available to DOE.

- Discuss the following nuclear safety assessments/surveillance activities:

Determination of assessment/surveillance requirements

Operation/area/site office and contractor notification

Assessment/surveillance agenda

### Determination of Assessment/Surveillance Requirements

A determination of assessment/surveillance requirements is a periodic, value-added appraisal of sufficient frequency and duration to confirm the contractor’s safe performance of work and the effectiveness of the self-assessment program.  A cost-effective appraisal meeting the intent of this policy might need to be no more than 2 weeks in duration and no more than once a year at each site.

### Operation/Area/Site Office and Contractor Notification

DOE uses the analysis of contractor self assessment results, performance measures, and operational awareness as input to scoping the annual appraisal.  Appraisals by non-line organizations, such as EH, or external organizations, such as the Environmental Protection Agency and state agencies, are fully considered and not ordinarily duplicated.  The appraisals are conducted primarily by DOE employees.  Issues identified but unresolved during a periodic appraisal are referred to local DOE personnel for further examination.

### Assessment/Surveillance Agenda

The scope of periodic appraisals, including additional areas of review, is determined by field elements with input from Headquarters and the contractor.  DOE uses the analysis of contractor self assessment results, performance measures, and operational awareness, as input to scoping the annual appraisal.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the following criticality safety-related American National Standards Institute/American Nuclear Society (ANSI/ANS) standards:

ANSI/ANS-8.1, Nuclear Criticality Safety in Operations with Fissionable Materials Outside Reactors

ANS-8.3 (ANSI N-16.2), Criticality Accident Alarm System

ANS-8.5 (ANSI N-16.4), Use of Borosilicate-Glass Raschig Rings as a Neutron Absorber in Solutions of Fissile Material

ANSI/ANS-8.7, Guide for Nuclear Criticality Safety in the Storage of Fissile Materials

ANS-8.15, Nuclear Criticality Control of Special Actinide Elements

ANS-8.19, Administrative Practices for Nuclear Criticality Safety

- Describe the contents, requirements, and relationship among the above American National Standards Institute/American Nuclear Society Standards.

A review of applicable ANSI and ANS standards should be completed to fully comprehend all requirements.

- Discuss the applicability of the above American National Standards Institute/‌American Nuclear Society Standards to the Department facilities and processes.

A review of the ANSI and ANS standards along with a review of DOE O 420.1A, DOE-STD-3009, DOE-STD-1027, and DOE-STD-3007 is required to determine the applicability of the standards to Department facilities and processes.

- Discuss the role of the Department nuclear safety specialists in implementing the requirements of these Standards.

The nuclear safety specialist provides technical oversight and independent review of the facility implementing the above mentioned standards.

- Define the following terms associated with nuclear criticality safety:

Criticality incident

Double contingency principle

Geometry control

Nuclear criticality safety

Significant quantity of fissionable material

Temporary exemption

### Criticality Incident

Criticality incident refers to the release of energy as a result of accidentally producing a self sustaining or divergent nuclear fission chain reaction.

### Double Contingency Principle

The double contingency principle requires that process designs shall incorporate sufficient factors of safety to require at least two unlikely, independent, and concurrent changes in process conditions before a criticality accident is possible.  In all cases, no single failure shall result in the potential for a criticality accident.

### Geometry Control

Geometry control refers to the passive engineering control by which container equipment design limits fissionable material dimensions and the spacing between adjacent equipment.  Reliance on geometry control shall be the first priority.

### Nuclear Criticality Safety

Nuclear criticality safety is the prevention or termination of inadvertent nuclear criticality and protection against injury or damage due to an accidental nuclear criticality.  Generally, prevention is preferred.

### Significant Quantity of Fissionable Material

Significant quantity of fissionable material refers to the minimum mass of fissionable material for which control of at least one parameter is required to ensure subcriticality under all normal and credible abnormal conditions.

### Temporary Exemption

A temporary exemption is a short term release from a criticality safety requirement.

Discuss the Management and Operating (M&O) Contractor responsibilities for the following in relation to criticality safety activities:

Criticality safety evaluations

Monitoring

Surveillance

Transportation

Storage

### Criticality Safety Evaluations

M&O contractors responsible for nuclear facilities are required to perform and document detailed nuclear criticality safety analyses.  The facility SAR shall contain a criticality safety section including the following:

Detailed descriptions of all equipment and facilities in which a criticality hazard may exist

Descriptions of all the fissionable materials and processes to be used including maximum quantities, and collection, handling, and transportation procedures

Analysis of all criticality scenarios and their safety control parameters

Descriptions of all criticality alarm systems (CAS) and emergency procedures

### Monitoring

M&O contractors shall establish monitoring programs to prevent accumulation of fissionable materials in process and storage equipment, pipes, and ventilation systems.

### Surveillance

M&O contractors must perform reviews and implement corrective measures that shall be in place in order to avoid any possible criticality hazards.

### Transportation

Requirements for transportation in DOE Order 5480.24 shall be applicable when materials are transferred from one operation to another within a facility, and from one on-site location to another.  Contractors must follow an approved on-site transportation safety manual.

### Storage

Requirements in DOE O 461.1 shall be complied with regarding off-site shipment of fissionable material.  DOE O 460.1 shall apply for the storage and safe transportation of weapon components and special assemblies shipped in national defense.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the following Department of Energy (DOE) Orders, Technical Standards, and Notice:

DOE-STD-3011, Guidance for Preparation of Basis for Interim Operation (BIO) Documents

DOE-STD-3014, Accident Analysis for Aircraft Crash into Hazardous Facilities

US NRC Guide 1.70, Standard Format and Content of Safety Analysis Reports of Nuclear Power Plants

29 CFR 1910.120, Safety and Health Programs, Work Plans, Health and Safety Plan

DOE-STD-1163, Integration of Multiple Hazard Analysis Requirements and Activities

DOE-STD-3016, Hazards Analysis Reports for Nuclear Explosive Operations

DOE O 460.1B, Packaging and Transportation Safety

DOE Guide 460.1-1, Implementation Guide for Use with DOE Order 460.1A,

Packaging and Transportation Safety

DOE O 461.1, Packaging and Transportation of Materials of National Security Interest

DOE Manual 461.1-1, Packaging and Transfer of Materials of National Security Interest Manual

Secretary of Energy Notice (SEN) SEN-35-91, Nuclear Safety Policy

- Describe the contents, requirements, and relationship between the above technical standards, and Secretary of Energy notice.

It is DOE policy that the general public be protected such that no individual bears significant additional risk to health and safety from the operation of a DOE nuclear facility above the risks to which members of the general population are normally exposed.  The purpose of the documents listed above is to establish the basic nuclear safety policy from which specific safety rules, orders, standards, and other requirements shall follow.  DOE facilities will be designed, constructed, operated, and decommissioned to assure the protection of the public, workers, and the environment.

The scientific, engineering, and technical knowledge and ability of DOE and its contractor personnel directly determine the Department’s ability to achieve its safety policy.  Potential hazards associated with nuclear operations dictate that DOE and contractor personnel possess technical competence, commitment, discipline, and high standards of professional and personal excellence.  Organizations responsible for DOE nuclear activities shall have the ability to recruit, train, and qualify personnel who possess these attributes for job specific positions.

Adherence to appropriate national and international standards in the design, construction, operation, and decommissioning of DOE’s nuclear facilities and activities is necessary for the successful implementation of the Department’s nuclear safety policy.  Standards proven through years of experience and accepted by professional and technical societies shall be used wherever applicable.  Yet no matter how carefully conceived and properly developed, technical standards cannot address all eventualities.

Therefore, DOE contractors must critically assess the standards in use at DOE facilities to assure that they remain consistent with the latest information arising from operational experience and developments in science and engineering.  Where standards do not exist or where existing standards do not suffice, appropriate DOE nuclear safety standards shall be developed and adopted.

- Describe the role of nuclear safety specialists with respect to the requirements in these orders, standards, and Secretary of Energy notice.

In striving to reach safety goals, DOE nuclear facilities and activities shall be designed, constructed, operated, and decommissioned with a) appropriate barriers to prevent or minimize potential radioactive releases, b) engineered safety features to minimize potential releases, and c) procedural controls to mitigate the effects of potential releases.  These goals shall be addressed for both new and existing facilities.  Proposed modifications to existing facilities to achieve these goals shall be prioritized along with other proposed modifications based on their safety significance.  DOE shall pursue the evolution of additional potential safety goals for plant and co-located workers to support enhanced safe operations of its facilities.  The Nuclear Safety Specialist ensures that all safety considerations taken are adequate to meet DOE goals.

- Determine whether aircraft crashes pose an acceptable or unacceptable hazard to safety of nuclear facilities.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

- Discuss the phenomena of aircraft crashes as a mechanism for releasing toxic materials.

For information on this topic, review section D.2 of http://www.eh.doe.gov/techstds/standard/std3014/std3014.pdf.

- Discuss the phenomena to which packaging is designed to withstand transportation accidents and the relationship to accident severity.

Packaging is designed to withstand the conditions listed below.

Heat

Packaging must withstand an ambient temperature of 38°C (100°F) in still air, and insulation according to the following table:

Insulation Data

| Form and location of surface | Total insulation for a 12-hour period (g cal/cm2) |
| --- | --- |
| Flat surfaces transported horizontally |
|  | Base | None |
|  | Other surfaces | 800 |
| Flat surfaces not transported horizontally | 200 |
| Curved surfaces | 400 |

### Cold

Packaging must withstand an ambient temperature of -40°C (-40°F) in still air and shade.

### Reduced External Pressure

Packaging must withstand a reduced external pressure of 25 kPa (3.5 lbf/in2) absolute.

### Increased External Pressure

Packaging must withstand an increased external pressure of 140 kPa (20 lbf/in2) absolute.

### Vibration

Packaging must withstand vibration normally incident to transport.

### Water Spray

Packaging must withstand a water spray that simulates exposure to rainfall of approximately 5 cm/h (2 in/h) for at least 1 hour.

### Free Drop

Packaging must withstand between 1.5 and 2.5 hours after the conclusion of the water spray test, a free drop through the distance specified below onto a flat, essentially unyielding, horizontal surface, striking the surface in a position for which maximum damage is expected.

Criteria for Free Drop Test (Weight/Distance)

| Package weight | Free drop distance |
| --- | --- |
| Kilograms | (Pounds) | Meters | (Feet) |
| Less than 5,000 | (Less than 11,000) | 1.2 | (4) |
| 5,000 to 10,000 | (11,000 to 22,000) | 0.9 | (3) |
| 10,000 to 15,000 | (22,000 to 33,100) | 0.6 | (2) |
| More than 15,000 | (More than 33,100) | 0.3 | (1) |

### Corner Drop

Packaging must withstand a free drop onto each corner of the package in succession, or in the case of a cylindrical package onto each quarter of each rim, from a height of 0.3 m (1 ft) onto a flat, essentially unyielding, horizontal surface.  This test applies only to fiberboard, wood, or fissile material rectangular packages not exceeding 50 kg (110 lbs) and fiberboard, wood, or fissile material cylindrical packages not exceeding 100 kg (220 lbs).

### Compression

For packages weighing up to 5000 kg (11,000 lbs), the package must be subjected, for a period of 24 hours, to a compressive load applied uniformly to the top and bottom of the package in the position in which the package would normally be transported.  The compressive load must be the greater of the following:

the equivalent of 5 times the weight of the package

the equivalent of 13 kPa (2 lbf/in2) multiplied by the vertically projected area of the package

### Penetration

Packaging must withstand the impact of the hemispherical end of a vertical steel cylinder of 3.2 cm (1.25 in) diameter and 6 kg (13 lbs) mass, dropped from a height of 1 m (40 in) onto the exposed surface of the package that is expected to be most vulnerable to puncture.  The long axis of the cylinder must be perpendicular to the package surface.

Tests on packaging for hypothetical accident severity must be conducted as detailed below.

### Free Drop

Packaging must withstand a free drop through a distance of 9 m (30 ft) onto a flat, essentially unyielding, horizontal surface, striking the surface in a position for which maximum damage is expected.

### Crush

Packaging must withstand subjection to a dynamic crush test by positioning the specimen on a flat, essentially unyielding horizontal surface so as to suffer maximum damage by the drop of a 500-kg (1100-lb) mass from 9 m (30 ft) onto the specimen.  The mass must consist of a solid mild steel plate 1 m (40 in) by 1 m (40 in) and must fall in a horizontal attitude.  The crush test is required only when the specimen has a mass not greater than 500 kg (1100 lb), an overall density not greater than 1000 kg/m3 (62.4 lb/ft3) based on external dimension, and radioactive contents greater than 1000 A2 not as special form radioactive material.  For packages containing fissile material, the radioactive contents greater than 1000 A2 criterion does not apply.

### Puncture

Packaging must withstand a free drop through a distance of 1 m (40 in) in a position for which maximum damage is expected, onto the upper end of a solid, vertical, cylindrical, mild steel bar mounted on an essentially unyielding, horizontal surface.  The bar must be 15 cm (6 in) in diameter, with the top horizontal and its edge rounded to a radius of not more than 6 mm (0.25 in), and of a length as to cause maximum damage to the package, but not less than 20 cm (8 in) long.  The long axis of the bar must be vertical.

### Thermal

Packaging must withstand being fully engulfed, except for a simple support system, in a hydrocarbon fuel/air fire of sufficient extent, and in sufficiently quiescent ambient conditions, to provide an average emissivity coefficient of at least 0.9, with an average flame temperature of at least 800°C (1475°F) for a period of 30 minutes, or any other thermal test that provides the equivalent total heat input to the package and which provides a time averaged environmental temperature of 800°C.  The fuel source must extend horizontally at least 1 m (40 in), but may not extend more than 3 m (10 ft), beyond any external surface of the specimen, and the specimen must be positioned 1 m (40 in) above the surface of the fuel source.  For purposes of calculation, the surface absorptivity coefficient must be either that value which the package may be expected to possess if exposed to the fire specified or 0.8, whichever is greater; and the convective coefficient must be that value which may be demonstrated to exist if the package were exposed to the fire specified.  Artificial cooling may not be applied after cessation of external heat input, and any combustion of materials of construction, must be allowed to proceed until it terminates naturally.

### Immersion of Fissile Material

For fissile material subject to 10 CFR 71.55, in those cases where water inleakage has not been assumed for criticality analysis, package must withstand immersion under a head of water of at least 0.9 m (3 ft) in the attitude for which maximum leakage is expected.

### Immersion of All Packages

A separate, undamaged specimen must be subjected to water pressure equivalent to immersion under a head of water of at least 15 m (50 ft).  For test purposes, an external pressure of water of 150 kPa (21.7 lbf/in2) gauge is considered to meet these conditions.

## Nuclear safety specialists shall demonstrate a familiarity-level knowledge of the Price-Anderson Amendments Act of 1988 and its relationship to subparts A and B of 10 CFR 830.

- Describe the purpose and scope of the Price-Anderson Amendment Act.

The Price Anderson Amendment Act (PAAA) of 1988 provides incentives for DOE contractors to abide by nuclear facility safety and operations requirements as set forth by DOE in such documents as 10 CFR 830.  The 10 CFR 830 regulatory requirements are intended to revise and supplement the existing provisions in DOE Orders for nuclear safety and will provide a more direct means to implement the civil penalty provisions of the PAAA.  The PAAA provides a reimbursement incentive to DOE contractors (and their subcontractors and suppliers) for conducting activities that involve source, special nuclear, or byproduct material in response to public liability penalties associated with the consequences of those activities.

- Discuss the Act’s applicability to the Department’s nuclear safety activities.

The intent of this act is that it will enhance compliance with such rules as 10 CFR 830, including programs that contribute to an effective and safe work environment at nuclear facilities.

- Describe the indemnity that DOE offers to contractors.

The PAAA also made DOE contractors (and their subcontractors and suppliers) subject to civil penalties for violations of DOE rules and regulations or orders related to nuclear safety.

- Discuss the requirements associated with the topics below, as they are affected by the rulemaking aspect of the Price-Anderson Amendment Act (PAAA):

Quality assurance requirements

Safety basis requirements

### Quality Assurance

DOE-STD-3009 helps identify quality assurance requirements to ensure compliance with the PAAA.

### Safety Basis Requirements

The PAAA is the rule that drives the requirements for creating a safety basis. As the PAAA is updated, the requirements for the safety basis may need to be updated.

Discuss the role of Department nuclear safety specialists with respect to implementing the requirements of the Price-Anderson Amendment Act.

The nuclear safety specialist ensures that all aspects of 10 CFR 830 are implemented at any given site.  The nuclear safety specialist performs independent reviews and audits to determine that the contractor is implementing all aspects of the act.

## Nuclear safety specialists shall demonstrate a working-level knowledge of the requirements in Department of Energy (DOE) Technical Standard DOE-STD-3009-94, Preparation Guide for U.S. Department of Energy Nonreactor Nuclear Facility Safety Analysis Reports and DOE-STD-3010, Airborne Release Fractions/Rates and Respirable Fractions for Nonreactor Nuclear Facilities.

- Discuss the conceptual basis and process for preparation of a facility/activity documented safety analysis.

The safety management programmatic requirements identified in 10 CFR 830 form the boundaries within which the safety analysis is performed and represent the means of assuring safe operation of the facility.  Hazard analysis and accident analysis are performed to identify specific controls and improvements that feed back into overall safety management.  Consequence and likelihood estimates obtained from this process also form the bases for grading the level of detail and control needed in specific programs.  The result is documentation of the safety basis that emphasizes the controls needed to maintain safe operation of a facility.

The level of detail provided in the DSA depends on numerous factors.  Applying the guidance for the graded approach in DOE-STD-3009 will assist the preparer in establishing an acceptable level of detail.  The foundation for effectively preparing a DSA is the assembly and integration of an experienced preparation team.  The size and makeup of the team depend on the magnitude and type of facility hazards and the complexity of the processes that are required to be addressed in the DSA.  In determining the makeup of the preparation team, careful consideration should be given to the key hazard analysis activity.  In general, the safety analysis base team should include, at a minimum, individuals experienced in process hazard and accident analyses, facility systems engineers, and process operators.  Individuals with experience in specific subject matter such as nuclear criticality, radiological safety, fire safety, chemical safety, or process operations may be needed in the hazard analysis on a regular or as needed basis.  Such individuals will typically be necessary in the development of programmatic DSA chapters as well.  Consistent, accurate exchange of information among the team members is at least as important as the makeup of the team itself.  This can be assured through meaningful integration of the required tasks.

Once team makeup is determined, base information needed to support DSA development is gathered.  Maximum advantage should be taken of pertinent existing safety analyses and design information (i.e., requirements and their bases) that are immediately available, or can be retrieved through reasonable efforts.  Other information arises from existing sources such as process hazards analyses (PrHAs), fire hazards analyses (FHAs), explosive safety analyses, health and safety plans (HASPs), environmental impact statements (EISs), etc.  The need for additional or specific information becomes apparent throughout the hazard analysis process.  The remaining key steps for efficient completion of the safety analysis and the DSA development process are listed below:

Identify the DSA project functions using project information and ensure the team matches the functions that are required.

Perform hazard analysis to provide facility hazard classification, evaluate worker safety and defense in depth, and identify unique and representative accidents to be carried forward to accident analysis.  Safety-significant SSCs and TSRs are designated in hazard analysis as well.

Perform an accident analysis and assess the results to identify any safety-class SSCs and accident specific TSRs based on comparison of accident consequences to the Evaluation Guideline.

Develop the chapters for the DSA by providing information necessary to support the results of the safety analysis.  These chapters detail the results of the analysis, describe the facility and the safety SSCs, and the safety management programs that relate to the facility safety basis.

- Discuss the following in relation to the preparation of the Documented Safety Analysis:

Worker safety

Defense-in-depth

Programmatic commitments

Technical safety requirements (TSRs)

Structures, systems, and components (SSCs)

Hazard analysis

Accident analysis

Application of the graded approach

Safe harbor methods

### Worker Safety

Workers, typically those in close proximity to operations, are the population principally at risk from potential consequences associated with hazard category 2 and 3 facilities.  The DOE recognizes, via 10 CFR 830, the importance of including worker safety in safety analyses by specifically noting the worker as a population of concern.  Developing a conceptual basis for the methodology used in 10 CFR 830 requires answering the fundamental question of how worker safety is most appropriately addressed in the DSA.  The Occupational Health and Safety Administration (OSHA) has published 29 CFR 1910.119, Process Safety Management of Highly Hazardous Chemicals.  The purpose of this regulation is defined by OSHA in summary fashion as, “employees have been and continue to be exposed to the hazards of toxicity, fires, and explosions from catastrophic releases of highly hazardous chemicals in their workplaces.  The requirements in this standard are intended to eliminate or mitigate the consequences of such releases.”  Many of the topics requiring coverage in this federal regulation, such as design codes and standards, process hazard analysis, human factors, training, etc., are directly parallel to the requirements in 10 CFR 830.  DOE O 440.1 and the OSHA standard address the issue of worker safety from process accidents by requiring the performance of hazards analyses for processes (exclusive of standard industrial hazards) in conjunction with implementation of basic safety programs that discipline operations and ensure judgments made in hazard analyses are supported by actual operating conditions.  These requirements effectively integrate programs and analyses into an overall safety management structure without requiring quantitative risk assessment.  This integration and the basic concepts of process safety management (PSM) described by OSHA regulations and the manuals and codes of practice described in DOE O 440.1 are philosophically accepted as appropriate for DSAs.  This standard effectively merges PSM principles with traditional DSA precepts.

### Defense in Depth

Defense in depth as an approach to facility safety has extensive precedent in nuclear safety philosophy.  It builds in layers of defense against release of hazardous materials so that no one layer by itself, no matter how good, is completely relied upon.  To compensate for potential human and mechanical failures, defense in depth is based on several layers of protection with successive barriers to prevent the release of hazardous material to the environment.  This approach includes protection of the barriers to avert damage to the plant and to the barriers themselves.  It includes further measures to protect the public, workers, and the environment from harm in case these barriers are not fully effective.  The defense-in-depth philosophy is a fundamental approach to hazard control for nonreactor nuclear facilities even though they do not possess the catastrophic accident potential associated with nuclear power plants.  In keeping with the graded-approach concept, no requirement to demonstrate a generic, minimum number of layers of defense in depth is imposed.  However, defining defense in depth as it exists at a given facility is crucial for determining a safety basis.  Operators of DOE facilities need to use the rigorous application of defense-in-depth thinking in their designs and operations.  Such an approach is representative of industrial operations with an effective commitment to public and worker safety and the minimization of environmental releases.  For high-hazard operations, there are typically multiple layers of defense in depth.  The inner layer of defense in depth relies upon a high level of design quality so that important SSCs will perform their required functions with high reliability and high tolerance against degradation.  The inner layer also relies on competent operating personnel who are well trained in operations and maintenance procedures.  Competent personnel translate into fewer malfunctions, failures, or errors and, thus, minimize challenges to the next layer of defense.  In the event that the inner layer of defense in depth is compromised from either equipment malfunction (from whatever cause) or operator error and there is a progression from the normal to an abnormal range of operation, the next layer of defense in depth is relied upon.  It can consist of (1) automatic systems, or (2) means to alert the operator to take action or manually activate systems that correct the abnormal situation and halt the progression of events toward a serious accident.  Mitigation of the consequences of accidents is provided in the outer layer of defense in depth.  Passive, automatically or manually activated features (e.g., containment or confinement system, deluge systems, filtered exhaust), and/or safety management programs (i.e., emergency response) minimize consequences in the event that all other layers have been breached.  The contribution of emergency response actions to minimizing consequences of a given accident cannot be neglected as they represent a truly final measure of protection for releases that cannot be prevented.  Structures, systems, or components that are major contributors to defense in depth are designated as safety-significant SSCs.

### Programmatic Commitments

Program commitments (e.g., radiation protection, maintenance, quality assurance) encompass a large number of details that are more appropriately covered in specific program documents (e.g., plans and procedures) external to the DSA.  The cumulative effect of these details, however, are recognized as being important to facility safety, which is the rationale for a top-level program commitment becoming part of the safety basis.  The importance of the program commitments, which can be incorporated in TSRs as administrative controls, cannot be overestimated.  The safety basis, however, includes only the top-level summary of program elements, not the details of the program or its governing documents.  Inspection discrepancies in a program would not constitute violation of the safety basis unless the discrepancies were so gross as to render premises of the summary invalid.  By virtue of application of the graded approach, the majority of the engineered features in a facility will not be identified in the categories of safety-class or safety-significant SSCs even though they may perform some safety functions.  However, such controls noted as a barrier or preventive or mitigative feature in the hazard and accident analyses must not be ignored in managing operations.  Such a gross discrepancy would violate the safety basis documented in the DSA even if the controls are not designated safety-class or safety-significant, because programmatic commitments extend to these SSCs as well.  At a minimum, all aspects of defense in depth identified must be covered within the relevant safety management programs (e.g., maintenance, quality assurance) committed to in the DSA.  The details of that coverage, however, are developed in the maintenance program as opposed to in the DSA.  Facility operators are expected to have noted the relative significance of these engineered features and have provided for them in programs, in keeping with standard industrial practice, based on the importance of the equipment.  It is the fact of coverage that is relevant to the facility safety basis.  The details of this programmatic coverage (i.e., exact type of maintenance items and associated periodicities) are not developed in or part of the DSA.  One overall commitment made in a DSA is that the contractor will not change the facility configuration underlying the documented safety basis without implementing and completing the USQ process.  However, situations do occur where a USQ process is not necessary.  For example, a stipulation to have a radiation protection program in the administrative control section of the TSR is a commitment; however, changes to specific program provisions do not require going through the USQ process.  DOE facilities that use and rely on site-wide, safety support services, organizations, and procedures, may summarize the applicable site-wide documentation provided its interface with the facility is made clear.

### Technical Safety Requirements

Descriptions result in the definition of functional requirements and associated performance criteria used to derive TSRs.  TSRs are safety controls developed in accordance with the precepts of 10 CFR 830.  TSR commitments encompass the following.  TSRs comprise: (1) SLs, (2) operational limits consisting of LCSs and LCOs and associated SRs, (3) ACs, (4) use and application provisions, (5) design features, and (6) bases appendix.  Based on the results of hazard and accident analysis, TSRs are designated for (1) safety-class SSCs and controls established on the basis of application of the evaluation guideline, (2) safety-significant SSCs, (3) defense in depth in accordance with the screening criteria of DOE G 423.1-1, and (4) safety management programs for defense in depth or worker safety.  The bases appendix provides the linkage to the DSA.  It is important to develop TSRs judiciously.  TSRs should not be used as a vehicle to cover the many procedural and programmatic controls inherent in any operation.  Excessive use of TSR limits to manage operations will result in distortion of the regulatory structure DOE is attempting to develop and will dilute the emphasis intended for the most critical controls.  SLs should be limited in number and designated with caution.  They should, however, receive coverage in the administrative control section of TSRs at a minimum.  Judgment should be used to determine what controls warrant use of operational limits.  When TSR administrative controls are used for purposes other than generic coverage of safety management programs, descriptions should be sufficiently detailed that a basic understanding is provided of what is controlled and why.  Beyond safety-significant SSCs designated for worker safety and their associated TSR coverage, additional worker safety issues should be covered in TSRs only by administrative controls on overall safety management programs.

### Structures, Systems, and Components

Descriptions result in the definition of functional requirements and associated performance criteria used to derive SSCs.  The rule defines safety-class designation for SSCs that are established on the basis of application of the evaluation guidelines.  This designation carries with it the most stringent requirements (e.g., enhanced inspection, testing and maintenance, and special instrumentation and control systems).  Appendix A of DOE-STD-3009 provides guidance for implementing the evaluation guideline to classify SSCs as safety-class SSCs.  This category of SSCs is provided to ensure that important SSCs will be given adequate attention in the DSA and facility operations programs.  Safety-significant SSCs are those of particular importance to defense in depth or worker safety as determined in hazard analysis.  Control of such SSCs does not require meeting the level of stringency associated with safety-class SSCs.  The evaluation guideline is not used for designating safety-significant SSCs.  Safety-class SSCs are designated to address public risk, which makes a dose guideline at the site boundary a useful tool.  Safety-significant SSCs address risk for all individuals within the site boundary as well as additional defense in depth for the public, making a dose guideline at any one point an artificial distinction distorting the process of systematically evaluating SSCs.  TSRs covering SSCs ensuring defense in depth should generally correlate with safety-significant SSC designation for defense in depth, but exact one-to-one correlation is not required.

### Hazard Analysis

The initial analytical effort for all facilities is a hazard analysis that systematically identifies facility hazards and accident potentials through hazard identification and hazard evaluation.  The focus of the hazard analysis is on thoroughness and requires evaluation of the complete spectrum of hazards and accidents.  This largely qualitative effort forms the basis for the entire safety analysis effort, including specifically addressing defense in depth and protection of workers and the environment.  Basic industrial methods for hazard analysis, its interface with more structured quantitative evaluations, and the basis for both have been described in references such as the American Institute of Chemical Engineers Guidelines for Hazard Evaluation Procedures (1992).  These guidelines have been accepted by OSHA as the standard for analytical adequacy in characterizing commercial chemical processes that perform the same type of unit operations conducted at DOE nonreactor nuclear facilities.  The largely qualitative techniques described in the above reference on hazard analysis provide methodologies for comprehensive definition of the accident spectrum for workers and the public.  The basic identification of hazards inherent in the process provides a broad, initial basis for identification of safety programs needed (e.g., radiation protection, hazardous chemical protection).  The hazard analysis then moves beyond basic hazard identification to evaluation of the expected consequences and estimation of likelihood of accidents, an activity that in no way connotes the level of effort of a probabilistic or quantitative risk assessment.  Throughout the evaluation process, preventive and mitigative SSCs and pertinent elements of programmatic controls are identified.  This identification also establishes functional requirements for SSCs, which will subsequently delineate the technical information (i.e., response parameters), needed to establish performance criteria.  The DSA summarizes these requirements and criteria for safety-class and safety-significant SSCs only.  Refinement of the information obtained in hazard evaluation leads to overall definition of defense in depth, worker safety, and environmental protection.  The most significant aspects of defense in depth and worker safety are subject to designation as safety-significant SSCs and coverage by TSRs.  Other items noted are encompassed by the details of safety management programs (e.g., procedures, training, maintenance, quality assurance), which can be captured in top-level fashion in TSR administrative controls.  The hazard evaluation conducted to assess the accident spectrum associated with hazards germane to the DSA indicates the adequacy of programmatic efforts and provides input to programmatic activities whose discipline provides a significant margin of safety.  The process outlined above is self grading for analytical effort.  Analytical effort can be limited to a simple, resource efficient hazard analysis geared to facility needs, unless events are noted that are of sufficient complexity to require more detailed, quantitative evaluations to understand the basis for safety assurance.  Implicit in this methodology is the statement of DOE-STD-1027 that the largely qualitative level of effort in hazard analysis is appropriate and sufficient for accident analysis of Hazard Category 3 facilities.  It is again noted that the hazard analysis effort is not a quantitative risk assessment.  Preparers cannot expect the level of detail associated with a quantitative risk assessment in a hazard analysis, as the hazard analysis is focused on systematically assessing what can go wrong in a facility as opposed to deriving mathematical expressions of risk.  The final purpose of hazard analysis is to identify a limited subset of accidents to be carried forward to accident analysis.  Identification of DBAs in safety analysis and use of DBAs is appropriate in defining a facility safety basis derivative DBAs.

### Accident Analysis

The complete spectrum of accidents is examined in hazard analysis.  A limited subset of accidents, (i.e., DBAs and derivative DBAs) that bound “the envelope of accident conditions to which the operation could be subjected” is carried forward to accident analysis where safety-class SSCs are designated by comparison of accident consequences to the evaluation guideline.  These scenarios are the accidents requiring formal definition.  Information obtained from specific accidents or representative accidents enveloping many small accidents are used to specify functional requirements for safety-class SSCs.  An accident analysis is performed for the bounding accidents.  Accident analysis in this standard refers to the formal quantification (i.e., all assumptions identified and justified and individual computations presented or summarized) of accident consequences.  The general binning estimates used in hazard analysis are adequate and representative of the level of effort desired for frequency determination.  Accordingly, accident analysis need only document the basis used in hazard analysis for assigning accident likelihood to two orders-of-magnitude bins.  The quantified consequences are compared to the numerical evaluation guideline for the purpose of identifying safety-class SSCs and any accident-specific assumptions requiring coverage by TSRs.

### Application of the Graded Approach

The use of a graded approach for the effort expended in safety analysis and the level of detail presented in associated documentation is prescribed in 10 CFR 830.  The graded approach applied to DSA preparation and updates is intended to produce cost-efficient safety analysis and DSA content that provide adequate assurance to the DOE that a facility has acceptable safety provisions without providing unnecessary information.  As described in 10 CFR 830, the graded approach adjusts the magnitude of the preparation effort to the characteristics of the subject facility based on seven factors:

The relative importance to safety, safeguards, and security

The magnitude of any hazard involved

The life-cycle stage of a facility

The programmatic mission of a facility

The particular characteristics of a facility

The relative importance of radiological and non-radiological hazards

Any other relevant factor

The rule provides for developing the DSA based on judgment of the facility in relation to these seven factors.  For example, simple hazard category 3 facilities or facilities that have a short operational life may only require a limited but adequate analysis documented to a level less than that required for a hazard category 2 facility.  In addition, facilities with short operational lives should consider the appropriateness of using DOE-STD-3011 to meet the requirements of 10 CFR 830.  On the opposite end of the spectrum, a complex hazard category 1 facility that is just going into operation requires extensive analysis and highly detailed documentation.  The application of the graded approach may allow for much simpler analysis and documentation for some of these facilities.  For facilities of little hazard, or hazards at the hazard category 3 level, for which only a modest reduction of risk is required, the DSA may be simple and short.  In such cases all of the topics for the DSA listed in this standard may not be necessary, and with proper technical bases, some topics may be omitted or reduced in the detail that would otherwise be required of hazard category 1 or 2 facilities.  Thus, with application of the graded approach, DSAs for hazard category 3 facilities or facilities with short operational lives will normally require more simplified DSA analysis and documentation.

### Safe Harbor Methods

Safe harbor methodologies are methodologies for DSA development that have already been approved by DOE for use in specific circumstances.  Table 2 of appendix A to subpart B of 10 CFR 830 identifies the list of safe harbor methodologies.  Any other methods not listed in this table require DOE approval before they can be used.

Discuss the relationship between the safe harbor methods for a DSA in 10 CFR 830 Appendix A and the requirements for a DSA in 10 CFR 830.204 with regard to completeness.

The documents identified in Appendix A of 10 CFR 830 are the documents that DOE has identified as being able to meet the criteria for completeness in regards to completing a DSA.  Section 830.204 of 10 CFR 830 specifies the DSA requirements as listed below:

Describe the facility (including the design of safety SSCs) and the work to be performed.

Provide a systematic identification of both natural and man-made hazards associated with the facility.

Evaluate normal, abnormal, and accident conditions, including consideration of natural and man-made external events, identification of energy sources or processes that might contribute to the generation or uncontrolled release of radioactive and other hazardous materials, and consideration of the need for analysis of accidents which may be beyond the design basis of the facility.

Derive the hazard controls necessary to ensure adequate protection of workers, the public, and the environment, demonstrate the adequacy of these controls to eliminate, limit, or mitigate identified hazards, and define the process for maintaining the hazard controls current at all times and for controlling their use.

Define the characteristics of the safety management programs necessary to ensure the safe operation of the facility, including quality assurance, procedures, maintenance, personnel training, conduct of operations, emergency preparedness, fire protection, waste management, and radiation protection.

With respect to a nonreactor nuclear facility with fissionable material in a form and amount sufficient to pose a potential for criticality, define a criticality safety program that:

ensures that operations with fissionable material remain subcritical under all normal and credible abnormal conditions

identifies applicable nuclear criticality safety standards

describes how the program meets applicable nuclear criticality safety standards

Describe the objectives of requiring accident analyses in safety basis documents.

The accident analysis is used to quantify the hazard analysis and to bin accidents by order of magnitude.  This is done to have relative values to compare to the evaluation guidelines that define limits allowable for both workers and the public.

Identify and discuss the use of the source term five factor formula in accident analyses.

The source term five-factor formula is identified below:

Source Term = MAR * DR *ARF * RF * LPF

where:

MAR = material at risk (curies or grams)

DR = damage ratio

ARF = airborne release fraction (or airborne release rate for continuous release)

RF = respirable fraction

LPF = leakpath factor

### Material at Risk (MAR)

The MAR is the amount of radionuclides (in grams or curies of activity for each radionuclide) available to be acted on by a given physical stress.  For facilities, processes, and activities, the MAR is a value representing some maximum quantity of radionuclide present or reasonably anticipated for the process or structure being analyzed.  Different MARs may be assigned for different accidents as it is only necessary to define the material in those discrete physical locations that are exposed to a given stress.  For example, a spill may involve only the contents of a tank in one glovebox.  Conversely, a seismic event may involve all of the material in a building.

### Damage Ratio (DR)

The DR is the fraction of the MAR actually impacted by the accident-generated conditions.  A degree of interdependence exists between the definitions of MAR and DR.  If it is predetermined that certain types of material would not be affected by a given accident, some analysts will exclude this material from the MAR.  The DR is estimated based upon engineering analysis of the response of structural materials and materials of construction for containment to the type and level of stress/force generated by the event.  Standard engineering approximations are typically used.  These approximations often include a degree of conservatism due to simplification of phenomena to obtain a useable model, but the purpose of the approximation is to obtain, to the degree possible, a realistic understanding of potential effects.

### Airborne Release Fraction (ARF)

The ARF is the coefficient used to estimate the amount of a radioactive material suspended in air as an aerosol and thus available for transport due to physical stresses from a specific accident.  For discrete events, the ARF is a fraction of the material affected.  For mechanisms that continuously act to suspend radionuclides (e.g., aerodynamic entrainment/resuspension), a release rate is required to estimate the potential airborne release from postulated accident conditions.  Generally, accident release rates (ARRs) are based upon measurements over some extended period to encompass most release situations for a particular mechanism.  The rates are average rates for the broad spectrum of situations and, as such, the most typically meaningful time unit to reflect average conditions is 1 hour.  There is evidence that in some situations (e.g., aerodynamic entrainment of sparse powder deposits on a heterogeneous surface), the rate of release is not uniform with time.  Even in the situations where the rates are relatively uniform, the source is depleted by the removal of particles from the surface by aerodynamic forces, and the amount of material airborne decreases with time unless the source is continuously replenished.  The ARFs are based primarily upon experimentally measured values for the specific material (e.g., plutonium, uranium, mixed fission products) or surrogates subjected to the particular type of stress under controlled conditions.  Attention is given to the parameters, if known, that may have a significant influence upon suspension by the specific mechanism and the uncertainty in the measurement as indicated by the variability of the results.

### Respirable Fraction (RF)

The RF is the fraction of airborne radionuclides as particles that can be transported through air and inhaled into the human respiratory system and is commonly assumed to include particles 10-µm Aerodynamic Equivalent Diameter (AED) and less.  Other definitions of “respirable particles” have been presented by various groups at different times.  The British Medical Research Council adopted a definition in 1952 classifying particles with a terminal velocity equal to that of a 5-m diameter as “respirable dust.”  The U.S. Atomic Energy Commission defined “respirable dust” as insoluble particles that are part of inhaled dust which penetrate to the non-ciliated portions of the gas exchange region, and with a 50 percent respirable cut-size of 3.5-m AED.  The American Conference of Governmental Industrial Hygienists has adopted a definition that is almost identical, differing only in the 2 m fraction allowed.  The U.S. Environmental Protection Agency defines “inhalable dust” (particles penetrating the upper respiratory airway and entering the thorax) with a 50 percent cutoff at 15-m AED.  The International Standards Organization—Europe defines “inhalable dust” as particles entering the nasal or oral passages with a 50 percent cut-size of 10-m AED.  Accordingly, use of a 10-m AED cut-size for respirable particles is considered conservative, and may even be overly conservative since the mass is a cube function of particle diameter.  The size of a particle is a function of the measurement technique used.  If the method used is optical/electron microscopy or spectrometry, particle size is a projected diameter measured by the plane that intercepts the light/electron beam or reflection from light scattered by the particle.  The size represents the two-dimensional area intercepting the beam and, as with all projections of three dimensions into two, can result in considerable distortion.  Projected diameter approximates the Geometric Diameter (Dg).  Dg is also approximated by sieving where the size measurement is termed geometric/linear/least linear diameter.  The measurement represents the smallest dimension of the particle that will pass through the openings in the sieve.

### Leakpath Factor (LPF)

The LPF is the fraction of the radionuclides in the aerosol transported through some confinement deposition of filtration mechanism.  There can be many LPFs for some accident conditions (e.g., the fraction transported from the package, such as a shipping container, to the cell or enclosure; the fraction leaked from the enclosure, cell, or glovebox to the operating area around the enclosure or room; the fraction leaked from the room to the building-atmosphere interface).  Where multiple leakpaths are involved, their cumulative effect is often expressed as one value that is the product of all leakpath multiples.  The LPF is a calculated or standard value based upon (1) established relationships between the size of the particulate material, airborne transport mechanisms, and losses by deposition mechanisms, or (2) specified filtration efficiencies.

Given an accident scenario, determine a reasonably bounding estimate of the airborne release fraction (ARF) and respirable fraction (RF), material at risk (MAR), leak path factor (LPF) and damage ratio (DR) to determine the product (MAR x ARF x RF x DR x LPF).

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Identify and discuss the methods, conventions and data sources used in developing estimates of the five factors for use in accident analyses.

In most cases, the ARFs and RFs for conditions bounded by the experimental parameters can be defined to one significant digit.  The parameter definition process has focused on estimating reasonable bounding values because of the limited quantity and variability of the data.  The use of the word “reasonable” is an acknowledgement that the only definitive bounds are ARFs and RFs of 1.0, which can always be postulated if enough synchronous, extreme localized conditions are assumed.  Such extreme synchronicity is neither an expected condition nor a practically useful model of reality.  The NRC has commented on this subject in a survey of nonreactor nuclear facility release potential and historical experience.  A key element in defining bounding values from the data understands the physical entrainment mechanisms at work, their potential variability, and the inherent limits of such mechanisms.  Median and average values are estimated for some data.  These estimates are made solely for the purpose of providing perspective on potential conservatism and should not be used as a basis for an ARF statistical distribution.  The generation and suspension of particles is the result of the interaction of multiple physiochemical variables that have not been completely characterized as the majority of the experiments performed were designed in an attempt to reflect reasonably bounding conditions for specific industrial situations of concern.  Accordingly, the data obtained are more accurately characterized as selected points from multiple distributions against multiple parameters than as different values from a common distribution.  Even if this point is neglected, there are still practically intractable problems in attempting to generate statistical distributions.  While the data are presumed to be bounding for the purpose intended, it is largely unknown whether the data values are truly 90th percentile, 99th percentile, 99.9th percentile, etc.  Further, in many cases it is considered likely that accident specific ARFs are actually distributed in a highly irregular manner (i.e., multi-modal or truncated distributions).  Assuming a typical distribution (i.e., log-normal, Poisson) using standard deviations will produce seriously distorted values that may have little or nothing to do with reality.  The available data do, however, cover a range of conditions that typify the energy sources associated with nonreactor nuclear facilities.  The data cover a more complete range of phenomenological concerns than the data upon which nuclear reactor source terms have been estimated.  In general, scaling effects, while not to be trivialized, are less of an issue with this data than with comparable reactor source term estimation data.  The NRC has already accepted a considerable amount of this information as a basis for source term estimation in NUREG-1320, Nuclear Fuel Cycle Facility Accident Analysis Handbook.  DOE-HDBK-3010-94 serves a similar function for DOE.  The values for ARFs and RFs taken from experimental measurements are reasonably well defined.  It is noted, however, that they are dependent upon the types and levels of stress imposed, the initial state (physical form, chemical composition, particle size distribution, degree of dispersion of the material-of-concern), and the response of the material-of-concern and other materials present.  The applicability of the experimental conditions to the complete spectrum of processes and potential accident conditions is, however, uncertain.  For this reason, the discussions of the data have tried to indicate where typical industrial accident phenomena (e.g., fires, explosions, spills) are considered covered by the data.  The estimates of ARFs and RFs applicable to various accident-generated mechanisms for the suspension of radioactive materials are based upon experimental data for specific types and levels of stresses/ force.  Care must be used in applying the ARFs/ARRs to ensure that the values chosen truly reflect the type and level of stress/force postulated for the event.  For instance, the suspension of powder from a surface (commonly termed resuspension) is not applicable to situations where the powder is dropped into flowing gas in a dispersed fashion.  Before the ARFs and RFs presented can be properly applied, the conditions imposed and the response of critical items must be evaluated.  Many standard methods are applicable (e.g., the rupture pressure of tanks and piping based upon the material of construction, the thickness, the temperature and pressure).  In other cases (e.g., the blast energy from the deflagration of flammable gas and oxidant mixtures in the free volume above the materials), however, standard engineering calculational methods are not available and interpretation of information and data (e.g., the fraction of the heat of combustion of reactants that translates into the shock wave) is required.  Once the forces and conditions imposed upon the material for dispersion/fragmentation and suspension are identified, the applicable ARF and RF can be selected.  In most cases, precise correspondence between the event conditions and experimental conditions during the measurement of the ARFs and RFs is not found.  For conservative analysis, the data are applicable if the measurement conditions exceed those calculated for the event (e.g., if the fall distances for spilled powders or liquids with characteristics like the materials used in the experiments are equal to or less than the experimental distance of 3 m).  In most cases, extrapolation beyond the experimental data is valid for a limited range beyond the maximum (a factor of 2 to 5 dependent on the slope of the experimental data and the range of conditions covered in the experimental study) imposed in the experimental study.  Models are available for the calculation of ARFs and RFs for some phenomena (e.g., free-fall spill of powders and liquids - Ballinger et.  al., 1988; PULF formula for fragmentation by brittle fracture - Sandia, 1987).  Care should be used in any extrapolation, however, to avoid producing obviously inappropriate answers.  This caution is particularly apt if calculations are being used to influence facility or process design.  A final emphasis is necessary regarding application of this data.  As developed for the NRC and DOE, it has never been intended to be used as absolute proof of anything.  Special attention has been given to understanding suspension phenomena, ranges of relevant parameters covered in experimental studies, artifacts or limitations of the data that may have been induced by experimental conditions, and possible effects of relevant parameters that may not have been controlled or monitored.  As noted, this has resulted in development of bounding ARFs and RFs.  The purpose of developing these values was (1) to better understand the potential bounding hazards presented by nonreactor nuclear facilities, and (2) to provide information to support general bases of decision making.  The first purpose has been fulfilled by use of this information in the Defense Programs Safety Survey Report.  This use has supported previous NRC estimates that the bounding consequence potential for nonreactor nuclear facilities is significantly less than commercial nuclear power plants, or large commercial chemical plants as well.  In domino fashion, this conclusion has reemphasized the use of the term “general bases” in the second purpose.

Identify and discuss methods/codes used to determine the environmental dispersion and delivered doses from accidental releases of hazardous materials.

| Type of Facility Analyzed | Method of Analysis |
| --- | --- |
| Low-Complexity Operations | Use Hazard Analysis |
| Single-Failure Electro-Mechanical Systems | Use Failure Modes and Effects Analysis (FMEA) |
| Systems with Redundant Barriers or Requiring Multiple Failures | Use Event Tree Analysis (ET) |
| Large, Moderately Complex Processes | Use Fault Tree Analysis (FT) |
| Complex Fluid Processes | Use Hazard and Operability Studies (HAZOP) |
| High-Complexity Facilities | Use Integrated Event Tree and Fault Tree Techniques (ETs/FTs) |

To date, six codes have been identified as toolbox codes:  ALOHA, CFAST, EPICODE, GENII, MACCS2, and MELCOR.  A general description of each code is provided along with the respective code owner.  The link Software Quality Assurance Central Registry provides a complete description of the software.

Discuss the effect of prevailing weather, building wake effects, and plume buoyancy upon the magnitude and distribution of doses from hazardous releases into the atmosphere.

Each code type takes into account the way values are affected by weather, building configuration, and their distribution in an accident.

Identify and discuss the treatment of uncertainty and the realistic effects in accident analyses.

To analyze a “worst case,” the uncertainty and realistic effects do not directly affect the analysis; the overall worst case is used, which lacks any real credibility of being a realistic approach.

Identify the purpose and relationship between Chapters 3, 4, and 5 and the technical safety requirements of the documented safety analysis.

Chapter 3 of the DSA is the hazard analysis and accident analysis section, and chapter 4 is the Safety SSC section, which identifies controls that are derived from the hazard and accident analysis.  Chapter 5 is the TSR, which identifies the SSCs that need to provide the greatest protection and the requirements for these controls.  They are all linked from need to creation to implementation and monitoring.

Complete a review of a hazards analysis including walking down the scope of work area.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Complete a review of an accident analysis including walking down the accident scenario.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

## Nuclear safety specialists shall demonstrate a working-level knowledge of NSTP-2003-1 that describes the relationship between human factors/human performance and institutional programs that support the safety analysis.

- Identify and discuss aspects of person-machine interface that can degrade or enhance the safety performance of personnel.

The principals of human performance improvement are listed below:

Even people working their best may make mistakes.

Error-likely situations are predictable, manageable, and preventable.

Individual behavior is influenced by organizational processes and values.

People achieve high levels of performance based largely on the encouragement and reinforcement received from leaders, peers, and subordinates.

Events can be avoided by understanding the reasons mistakes occur and applying the lessons learned from past events.

Identify and discuss how written procedures are conducive to reliable or unreliable performance of activities important to safety.

Written procedures are conducive to performance of activities important to safety when they are developed using the following objectives:

Address procedures with a clear, logical sequence of tasks that make them understandable to the user.  Procedures must provide all the information individuals need to perform the task.

Communicate policies for procedure use and adherence.  Guidance for use of specific procedures should identify those tasks or evolutions for which continuous in-hand use or strict adherence is required.

Verify the integrity of defenses, especially for tasks important for nuclear safety.  The number and strength of defenses, such as multiple safeguards, equipment trains, physical barriers, supervision, and procedures, are related to the potential safety-related consequences of errors.

Alert workers and supervisors to key tasks/decision points.  Elevate the attention of individuals by incorporating appropriate cues.

Incorporate appropriate information into procedures from applicable source documents, such as the plant design documents and plant-specific safety analysis.

Detail prerequisites and initial conditions.  Carefully consider the location of this information in the procedures so that the intent of each procedure is understood.

Define nomenclature used in the procedures.

Describe only one action in each procedure step.

Provide individual signoffs for selected critical steps.  One signoff should apply to only one action.  Separate signoffs should be provided for independent verifications.

- Identify and discuss how personnel training programs can be conducive to safety or prone to error.

All personnel should be trained on proper implementation of all ACs, not just for those that are deemed necessary for job requirements.  There shall be a training implementation matrix to ensure training is adequate and complete.  If training is not updated and monitored, training may be missed by employees and any updates to TSRs may be overlooked.

- Identify and discuss how staffing and qualification of operational personnel are conducive to safe versus unsafe operations.

To ensure safe operations, all personnel must be able to perform their assigned tasks and be trained on all TSR requirements.  The training must include updates/changes to TSRs along with addressing any additional TSR requirements.  Training should be adequate to ensure complete compliance with TSRs to minimize any unsafe operations due to performance of TSRs.

- Identify and discuss the influence of management and organizational factors upon safety of operations.

Management and organizational factors must foster a work environment that promotes excellence.  The following way to conduct business can be implemented to improve, or to minimize the degradation of, the human/machine interface:

Communicate accurately and frequently.

Anticipate error-likely situations.

Check others’ work and monitor progress among each other as work is performed.

Practice critical thinking.

Follow approved procedures.

Stop the task and collaborate with others when unfamiliar or unanticipated conditions arise.

- Identify and discuss the methods used to estimate the probability of significant mistakes made by personnel and the relationship to probabilistic risk assessment.

The following references describe human factors in risk assessment:

Excellence in Human Performance, INPO, September 1997.

Putting the Human into Hazard Assessment, Helen Rycraft, BNFL, a paper presented at the 2003 annual meeting of the Energy Facilities Contractors Group (EFCOG) Safety Analysis Working Group, Salt Lake City, June 2003.

- Identify and discuss the methods for assessing the reliability of administrative controls contained in TSRs and facility programs.

The following references provide guidance on the development of effective and reliable ACs:

Excellence in Human Performance, INPO, September 1997.

Guidelines for the Conduct of Operations at Nuclear Power Plant Stations, Institute of nuclear power operations, INPO 01-002, May 2001.

## Nuclear safety specialists shall demonstrate a working-level knowledge of assessment techniques (such as the planning and use of observations, interviews, and document reviews) to assess facility performance, report results of assessments, and follow up on actions taken as the result of assessments.

- Describe the role of nuclear safety specialists in the assessment of government owned contractor operated (GOCO) facilities.

The role of nuclear safety personnel is to ensure that safety requirements necessary for a practical safeguarding of applicable DOE facilities and personnel are being adequately implemented.  Practical safe work procedures include training of skilled and unskilled personnel who work in an area where work is performed with nuclear material.  For exposure to nuclear material, safety measures shall protect personnel against both normal operations and emergency situations.  In addition, only qualified persons who are capable of working safely in nuclear facilities and are familiar with the proper use of special precautionary techniques, personal protective equipment, TSRs, and operating procedures may perform work with nuclear material.  Nuclear safety personnel perform DOE line management oversight of their assigned facilities to ensure that

the contractor is operating facilities safely and efficiently (i.e., within the boundaries of those controls invoked in the facility authorization basis);

the contractor’s management system is effectively controlling conduct of operation as related to nuclear safety;

effective lines of communication between DOE and its operating contractors are maintained during periods of normal operation, and following reportable events, in accordance with DOE Orders and requirements.

- Describe the assessment requirements and limitations associated with the interface with contractor employees.

As assessment requirements and limitations associated with the interface of nuclear safety personnel and contractor employees vary from site to site, the local qualifying official will evaluate the completion of this competency.

- Discuss the essential elements of a performance-based assessment including:

Investigation

Fact finding

Exit interview

Reporting

Follow-up

Closure

### Investigation

It is important to begin the investigation as soon as an assessment is called for to ensure that data is not lost.  The information that should be collected consists of conditions before, during, and after operation of the facility; personnel involvement; environmental factors; and other information having relevance to the operation of the facility.

### Fact Finding

Once all the data has been collected, the data should be verified to ensure accuracy.  The investigation may be enhanced if some physical evidence is retained.  Establishing a quarantine area, or the tagging and segregation of pieces and material, should be performed for failed equipment or components.  The basic need is to determine the direct, contributing, and root causes so that effective corrective actions can be taken that will prevent recurrence.  Some areas to be considered when determining what information is needed include

activities related to the operations of the facility

initial or recurring problems

hardware (equipment) or software (programmatic-type issues) associated with the facility

recent administrative program or equipment changes

physical environment or circumstances

Some methods of gathering information include conducting interviews and collecting statements.  Interviews must be factual.  Preparing questions before the interview is essential to ensure that all necessary information is obtained.  Interviews should be conducted, preferably in person, with those people who are most familiar with the system.  Individual statements could be obtained if time or the number of personnel involved makes interviewing impractical.  Interviews can be documented using any format desired by the interviewer.  Consider conducting a walk-through of the system or facility as part of the interview if time permits.

### Exit Interview

Assessments can gain value from an exit interview.  This interview is used primarily to present the assessment summary and provide the assessed organization an opportunity to verify the factual accuracy of assessment results.  To facilitate this, assessors should be prepared to provide detailed supporting information for those results (ideally, a draft assessment report should be available at this time).  This interview also offers an opportunity for the assessed organization to present its management position and any plans for addressing the results.  Reasonable time should be allowed to discuss any concerns, but this interview should not be used to argue the assessment agenda or methodology.

### Reporting

Review of reports and documents helps develop the foundation for identifying weaknesses and areas that are of concern to an auditor.

Review relevant documents or portions of documents as necessary and reference their use in support of facility operation.  Record appropriate dates and times associated with the occurrence on the documents reviewed.  Examples of documents include the following:

Operating logs

Correspondence

Inspection/surveillance records

Maintenance records

Meeting minutes

Computer process data

Procedures and instructions

Vendor manuals

Drawings and specifications

Functional retest specification and results

Equipment history records

Design basis information

Safety analysis report (SAR)/technical specifications

Related quality control evaluation reports

Operational safety requirements

Safety performance measurement system/occurrence reporting and processing system (SPMS/ORPS) reports

Radiological surveys

Trend charts and graphs

Facility parameter readings

Sample analyses and results (chemistry, radiological, air, etc.)

Work orders

### Follow-Up

After a reasonable period of time has elapsed, follow-up activities should be performed to verify the effectiveness of the corrective actions and how they were implemented.  The verification should, at a minimum, sample the corrective actions to determine whether the problem/issue to be addressed has been resolved.  The organization’s reporting systems (e.g., noncompliance tracking system, occurrence reporting and processing system, external oversight reports and regulatory violations, performance indicators) should be reviewed for evidence of the problem (or a similar problem) recurring.  The same techniques used to conduct assessments may be used for verifying corrective actions; however, there are several common ways to verify the implementation of corrective actions, including the following:

Reassessment of the deficient areas

Review of new or revised quality-affecting documents such as manuals, procedures, and training records

Verification during the next scheduled assessment

Verification by conducting a surveillance covering the areas of concern

### Closure

Contractors send a letter to the directives management group (DMG) requesting closure and stating that the corrective actions in the implementation plan have been completed.  Any ongoing activities specified in the letter must be noted.  The DMG coordinates approval of the closure with the appropriate division of primary interest and the contracting officer’s representative.

Management responsible for the activities assessed is also responsible for the development of effective corrective action of the problem areas or deficiencies discovered during the assessment.  At a minimum, the corrective action should address

measures to correct each deficiency

identification of all root causes for significant deficiencies

determination of the existence of similar deficiencies

corrective actions to preclude recurrence of like or similar deficiencies

assignment of corrective action responsibility

completion dates for each corrective action

For independent assessments, the proposed corrective action should be reviewed for concurrence by the assessment team leader.  This will help ensure that the planned actions will be effective in resolving the problem areas and deficiencies reported by the assessment team.

Describe the following assessment methods and the advantages or limitations of each method:

Document review

Observation

Interviews

### Document Review

Document review is used extensively during an assessment to substantiate the information obtained during interviews and observation.  During the course of an assessment, questions may arise concerning what is heard and seen.  The review of documents, including logs, procedures, work orders, and other data provides a method for answering these questions and validating the assessment results.  The drawback of document review is that the accuracy of the records cannot be ascertained by review alone.  This technique should be combined with interviews, observation, inspection, and/or performance testing to complete the picture of performance.  Records and documents should be selected carefully to ensure they adequately characterize the program, system, or process being assessed.

### Observation

Observation, the viewing of actual work activities, is often considered the most effective technique for determining whether performance is adequate.  Assessors should understand the effect their presence has on the person being observed and convey an attitude that is helpful, constructive, positive, and unbiased.  The primary goal during observation is to obtain the most complete picture possible of the performance, which should then be put into perspective relative to the overall program, system, or process.

### Interviews

Interviews provide a means to verify the results of observation, document review, inspection, and performance testing.  In addition, interviews allow the responsible person to explain and clarify those results.  The interview helps to eliminate misunderstandings about program implementation and provides a venue where apparent conflicts or recent changes can be discussed and the organization and program expectations can be described.  Tools developed during assessment planning are used to prepare for the interview.  Assessors should also prepare questions in advance to keep the interview focused.

Describe the action to be taken if the contractor challenges the assessment findings and explain how such challenges can be avoided.

Disputes over the assessment findings, the corrective action plan or its implementation (such as timeliness or adequacy) must be resolved at the lowest possible organizational level.  The organization that disagrees with the disposition of a given issue may elevate the dispute for timely resolution.  The organization that disagrees with the disposition of a given issue must elevate the dispute in a step-wise manner through the management hierarchy.  The dispute must be raised via a deliberate and timely dispute resolution process that provides each party with equal opportunity for input and a subsequent opportunity to appeal decisions up to the Secretary of Energy, if necessary.

## Nuclear safety specialists shall demonstrate a working-level knowledge of the Department of Energy (DOE)/facility contract provisions necessary to provide oversight of a contractor’s operations.

- Describe the role of nuclear safety specialists in contractor oversight.

The nuclear safety specialist is an outside auditor and provides regulatory oversight for the contractor facility.  The nuclear safety specialist approves the facility safety basis and ensures compliance with the safety basis.

- Compare and contrast the following:

The Department of Energy’s expectations of a Management and Operating (M&O) contractor

A Management and Operating contractor’s expectations of the Department of Energy

The expectations that the M&O contractor and DOE have of each other are identified in the contract that the M&O contractor and DOE agree upon.  The contract sets forth what DOE expects in regard to nuclear safety as part of their oversight.  The contractor gets the structure outlining how DOE oversight is given and maintained at a facility.

Identify the key elements and features of an effective Department of Energy and Management and Operating contractor relationship.

Agreements in Principle (AIPs) outline the general points of understanding or boundaries between DOE and other parties, including M&O contractors.  AIPs set forth the macro-level agreements, and lay out the foundation for more specific detailed negotiations on the finer points of the covenant.  AIPs are often precursors to memorandums of understanding (MOUs), memorandums of agreement (MOAs), or actual contracts.

An MOU is a written agreement broadly stating basic understandings of tasks and describing a method for performing these tasks between the Department and other Governmental entities, the private sector, and educational institutions.  A MOU is not a binding contract, nor can it be used to obligate, transfer, or commit funds.  Interagency Agreements (IA), not MOUs, are used for monetary exchanges between DOE and other federal agencies.

An MOA is an explicit agreement between DOE and its contractors in the management and operations of a facility, site, or organization.

Describe the responsibility nuclear safety specialists have associated with contractor compliance under the Price-Anderson Amendments Act.

Nuclear safety personnel should play an active role in the negotiation and approval of management agreements that affect nuclear facilities.  Additional responsibilities include

reviewing applicable agreements to ensure the safety basis is not altered;

if a safety consideration is involved, reviewing the proposed agreement and making recommendations to the approval authority on the necessary requirements;

supplying information on applicable laws, regulations, and Orders to those negotiating contract requirements.

Describe the role of nuclear safety specialists in the cost-plus-award fee process.

The nuclear safety specialist ensures that the contractor meets all the requirements of the contract.  They ensure that all nuclear safety issues are addressed to the satisfaction of the DOE.

Explain the responsibilities of nuclear safety specialists for DOE O 442.1A, Employee Concerns Program, and the identification, reporting, reviewing, and documentation of employee concerns.

The nuclear safety specialist is to look into any concerns brought by DOE employees or contractors in regard to employee, public, and environmental safety.  Any issue addressing safety from nuclear material will be investigated thoroughly and any issues, concerns, or problems identified will be dealt with immediately and the cognizant DOE officials will be notified.

Describe the differing professional opinions process used in your office.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

## Nuclear safety specialists shall demonstrate a working-level knowledge of problem analysis principles and the techniques necessary to identify problems, potential causes, and corrective action(s) associated with nuclear safety issues at DOE Defense Nuclear Facilities.

- Describe and explain the application of problem analysis techniques including the following:

Root cause analysis

Causal factor analysis

Change analysis

Barrier analysis

Management oversight risk tree analysis

### Root Cause Analysis

Root cause analysis is an analysis method that includes the following basic steps:

Identify the problem.  Remember that actuation of a protective system constitutes the occurrence but is not the real problem; the unwanted, unplanned condition or action that resulted in actuation is the problem to be solved.  For an example, dust in the air actuates a false fire alarm.  In this case, the occurrence is the actuation of an engineered safety feature.  The smoke detector and alarm functioned as intended; the problem to be solved is the dust in the air, not the false fire alarm.  Another example is when an operator follows a defective procedure and causes an occurrence.  The real problem is the defective procedure; the operator has not committed an error.  However, if the operator had been correctly trained to perform the task and, therefore, could reasonably have been expected to detect the defect in the procedure, then a personnel problem may also exist.

Determine the significance of the problem.  Were the consequences severe?  Could they be next time?  How likely is recurrence?  Is the occurrence symptomatic of poor attitude, a safety-culture problem, or other widespread program deficiency?  Base the level of effort of subsequent steps of your assessment upon the estimation of the level of significance.

Identify the causes immediately preceding and surrounding the problem.

Identify the reasons why the causes in the preceding identification step existed, working your way back to the root cause (the fundamental reason that, if corrected, will prevent recurrence of this and similar occurrences throughout the facility and other facilities under your control).  This root cause is the stopping point in the assessment of causal factors.  It is the place where, with appropriate corrective action, the problem will be eliminated and will not recur.

### Causal Factor Analysis

Causal factor analysis is used for multi-faceted problems or long, complex causal factor chains.  Cause and effects diagrams describe the time sequence of a series of tasks and/or actions and the surrounding conditions leading to an event.  The event line is a time sequence of actions or happenings while the conditions are anything that shapes the outcome and ranges from physical conditions (such as an open valve or noise) to attitude or safety culture.  The events and conditions as given on a chart describe a causal factor chain.

### Change Analysis

Change Analysis looks at a problem by analyzing the deviation between what is expected and what actually happened.  The evaluator essentially asks what differences occurred to make the outcome of this task or activity different from all the other times this task or activity was successfully completed.  This technique consists of asking the questions: What? When? Where? Who? How?  Answering these questions should provide direction toward answering the root-cause determination question: Why?  Primary and secondary questions included within each category will provide the prompting necessary to thoroughly answer the overall question.  Some of the questions will not be applicable to any given condition.  Some amount of redundancy exists in the questions to ensure that all items are addressed.  Several key elements to be addressed include the following:

Consider the event containing the undesirable consequences.

Consider a comparable activity that did not have the undesirable consequences.

Compare the condition containing the undesirable consequences with the reference activity.

Set down all known differences whether they appear to be relevant or not.

Analyze the differences for their effects in producing the undesirable consequences.  This must be done with careful attention to detail, ensuring that obscure and indirect relationships are identified (e.g., a change in color or finish may change the heat transfer parameters and consequently affect system temperature).

Integrate information into the investigative process relevant to the causes of, or the contributors to, the undesirable consequences.

Change analysis is a good technique to use whenever the causes of the condition are obscure, you do not know where to start, or you suspect a change may have contributed to the condition.  Not recognizing the compounding of change (e.g., a change made five years previously combined with a change made recently) is a potential shortcoming of change analysis.  Not recognizing the introduction of gradual change as compared with immediate change also is possible.  This technique may be adequate to determine the root cause of a relatively simple condition.  In general, though, it is not thorough enough to determine all the causes of more complex conditions.

### Barrier Analysis

There are many things that should be addressed during the performance of a Barrier Analysis.  The questions listed below are designed to aid in determining what barrier failed, thus resulting in the occurrence.

What barriers existed between the second, third, etc.,  condition/situation and the second, third, etc., problem?

If there were barriers, did they perform their functions? How?

Did the presence of any barriers mitigate or increase the occurrence severity? Why?

Were any barriers not functioning as designed? Why?

Was the barrier design adequate? How?

Were there any barriers in the condition/situation source(s)? Did they fail? Why?

Were there any barriers on the affected component(s)? Did they fail? Why?

Were the barriers adequately maintained?

Were the barriers inspected prior to expected use?

Were any unwanted energies present? Why?

Is the affected system/component designed to withstand the condition/situation without the barriers? How?

What design changes could have prevented the unwanted flow of energy? Why?

What operating changes could have prevented the unwanted flow of energy? Why?

What maintenance changes could have prevented the unwanted flow of energy? Why?

Could the unwanted energy have been deflected or evaded? How?

What other controls are the barriers subject to? How?

Was this event foreseen by the designers, operators, maintainers, anyone?

Is it possible to have foreseen the occurrence? How?

Is it practical to have taken further steps to have reduced the risk of the occurrence?

Can this reasoning be extended to other similar systems/components?

Were adequate human factors considered in the design of the equipment?

What additional human factors could be added? Should be added?

Is the system/component user friendly?

Is the system/component adequately labeled for ease of operation?

Is there sufficient technical information for operating the component properly? How do you know?

Is there sufficient technical information for maintaining the component properly? How do you know?

Did the environment mitigate or increase the severity of the occurrence? How?

What changes were made to the system/component immediately after the occurrence?

What changes are planned to be made? What changes might be made?

Have these changes been properly and adequately analyzed for effect?

What related changes to operations and maintenance have to be made now?

Are expected changes cost effective? Why? How do you know?

What would you have done differently to have prevented the occurrence, disregarding all economic considerations (as regards operation, maintenance, and design)?

What would you have done differently to have prevented the occurrence, considering all economic concerns (as regards operation, maintenance, and design)?

Barrier analysis is a systematic process that can be used to identify physical, administrative, and procedural barriers or controls that should have prevented the occurrence.  This technique should be used to determine why these barriers or controls failed and what is needed to prevent recurrence.

### Management Oversight Risk Tree Analysis

Management oversight risk tree (MORT) analysis is used to prevent oversight of the identification of causal factors.  It lists, on the left side of the tree, specific factors relating to the occurrence, and on the right side of the tree, the management deficiencies that permit specific factors to exist.  The management factors all support each of the specific barrier/
control factors.  Included is a set of questions to be asked for each of the factors on the tree.  As such, it is useful in preventing oversight and ensuring that all potential causal factors are considered.  It is especially useful when there is a shortage of experts to ask the right questions.  However, because each of the management factors may apply to the specific barrier/control factors, the direct linkage or relationship is not shown but is left up to the analyst.  For this reason, events and causal factor analysis and MORT should be used together for serious occurrences: one to show the relationship, the other to prevent oversight.

Describe the following types of investigations and discuss an example of the application of each:

Type A

Type B

A complete description of each type of investigation can be found in DOE G 225.1A-1.

Compare and contrast immediate, short term, and long term actions taken as the result of problem identification or an occurrence.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Given a nuclear safety event and/or occurrence data, apply problem analysis techniques and identify the problems and how they might have been avoided.

Note:  This is a performance-based competency.  The ability to complete this competency must be observed by a qualifying official.

Describe various data gathering techniques and the use of trending/history when analyzing problems.

Methods used in data gathering at facilities may include those listed below.

### Walkthroughs

A walkthrough of a facility is performed to observe operations, system configurations, and physical conditions.

### Interviews

Conducting interviews of management, operators, technicians, and engineers at a facility gives an analyst an idea of the overall operations and level of knowledge at the facility.

### Document Review

A review of documentation is performed to ensure that all requirements are being met.  This review encompasses all requirements for the safety basis.

Trending/history is used to quantify accident scenarios, calculate failure rates, or identify faulty equipment due to a history of high failure.

# Selected Bibliography and Suggested Reading

10 CFR 261 “Identification and Listing of Hazardous Waste.” July 1, 2004.

10 CFR 830 “Nuclear Safety Management.” January 10, 2001.

10 CFR 835 “Occupational Radiation Protection.” January 1, 2004.

29 CFR 1910 “Occupational Safety and Health Standards.” July 1, 2004.

29 CFR 1910.35 “Compliance with NFPA 101-2000, Life Safety Code.” November 7, 2002.

29 CFR 1910.120 “Hazardous Waste Operations and Emergency Response.” July 1, 2004.

29 CFR 1960 “Basic Program Elements for Federal Employee Occupational Safety and Health Related Matters.” July 1, 2004.

48 CFR 970.5204-2 “Laws, Regulations, and DOE Directives.” October 1, 2004.

48 CFR 970.5223-1 “Integration of Environment, Safety, and Health into Work Planning and Execution.” October 1, 2004.

Defense Nuclear Facilities Safety Board.  Recommendation 92-2.  1992.

ISO 14001 Environmental Management Systems.  International Organization for Standardization, 1996.

Office of Management and Budget.  OMB Circular A-119, Federal Participation in the Development and Use of Voluntary Consensus Standards and in Conformity Assessment Activities.  February 10, 1998.

U.S.  Congress.  Clean Air Act. 1993.

U.S.  Congress.  Clean Water Act. 1977.

U.S.  Congress.  Comprehensive Environmental Response, Compensation, and Liability Act-Superfund Act.  1980.

U.S.  Congress.  Emergency Planning and Community Right-to-Know Act.  1986.

U.S.  Congress.  Federal Facilities Compliance Act.  1992.

U.S.  Congress.  National Environmental Policy Act.  1969.

U.S.  Congress.  National Technology Transfer and Advancement Act.  1995.

U.S.  Congress.  Price-Anderson Amendments Act.  1988.

U.S.  Congress.  Resource Conservation and Recovery Act.  1976.

U.S.  Congress.  Superfund Amendment Reauthorization Act.  1974.

U.S.  Congress.  Toxic Substances Control Act.  1976.

U.S.  Department of Energy.  DOE Guide 420.1-1, Nonreactor Nuclear Safety Design Criteria and Explosive Safety Criteria Guide for Use with DOE O 420.1 Facility Safety.  March 28, 2000.

U.S.  Department of Energy.  DOE Guide 421.1-2, Implementation Guide for Use in Developing Documented Safety Analyses to Meet Subpart B of 10 CFR 830.  October 24, 2001.

U.S.  Department of Energy.  DOE Guide 423.1-1, Implementation Guide for Use in Developing Technical Safety Requirements.  October 24, 2001.

U.S.  Department of Energy.  DOE Guide 424.1-1, Implementation Guide for Use in Addressing Unreviewed Safety Question Requirements.  October 24, 2001.

U.S.  Department of Energy.  DOE Guide 450.3-1, Documentation for Work Smart Standards Applications: Characteristics and Considerations.  February 1, 1997.

U.S.  Department of Energy.  DOE Manual 231.1-2, Occurrence Reporting and Processing of Operations Information.  August 19, 2003.

U.S.  Department of Energy.  DOE Order 414.1B, Quality Assurance.  April 29, 2004.

U.S.  Department of Energy.  DOE Order 420.1A, Facility Safety.  May 20, 2002.

U.S.  Department of Energy.  DOE Order 433.1, Maintenance Management Program for DOE Nuclear Facilities.  June 1, 2001.

U.S.  Department of Energy.  DOE Order 435.1, Radioactive Waste Management.  August 28, 2001.

U.S.  Department of Energy.  DOE Order 451.1B, National Environmental Policy Act Compliance Program.  September 28, 2001.

U.S.  Department of Energy.  DOE Order 460.2A, Departmental Materials Transportation and Packaging Management. December 22, 2004

U.S.  Department of Energy.  DOE Order 461.1A, Packaging and Transfer or Transportation of Materials of National Security Interest. April 26, 2004

U.S.  Department of Energy.  DOE Order 5490.19, Conduct of Operations for DOE Facilities.  October 23, 2001.

U.S.  Department of Energy.  DOE Policy 411.1, Safety Management Functions, Responsibilities, and Authorities.  January 28, 1997.

U.S.  Department of Energy.  DOE Policy 450.4, Safety Management System Policy.  October 15, 1996.

U.S.  Department of Energy.  DOE-HDBK-1010-92, DOE Fundamentals Handbook, Classical Physics.  April 1999.

U.S.  Department of Energy.  DOE-HDBK-1013/2-92, DOE Fundamentals Handbook, Instrumentation and Control, volume 2 of 2.  April 1999.

U.S.  Department of Energy.  DOE-HDBK-1016/1-93, DOE Fundamentals Handbook, Engineering Symbology, Prints, and Drawings, volume 1 of 2.  April 1999.

U.S.  Department of Energy.  DOE-HDBK-1019/1-93, DOE Fundamentals Handbook, Nuclear Physics and Reactor Theory, volume 1 of 2.  April 1999.

U.S.  Department of Energy.  DOE-HDBK-1019/2-93, DOE Fundamentals Handbook, Nuclear Physics and Reactor Theory, volume 2 of 2.  April 1999.

U.S.  Department of Energy.  DOE-STD-1020-2002, Natural Phenomena Hazards Design and Evaluation Criteria for Department of Energy Facilities.  January 2002.

U.S.  Department of Energy.  DOE-STD-1027-92, Hazard Categorization and Accident Analysis Techniques for Compliance with DOE Order 5480.23, Nuclear Safety Analysis Reports.  December 2002.

U.S.  Department of Energy.  DOE-STD-1104-96, Review and Approval of Nuclear Facility Safety Basis Documents (Documented Safety Analysis and Technical Safety Requirements).  May 2002.

U.S.  Department of Energy.  DOE-STD-1098-99, Radiological Control.  June 2004.

U.S.  Department of Energy.  DOE-STD-1183-2001, Nuclear Safety Standard.  April 2004.

Nuclear Safety Specialist

Qualification Standard

Reference Guide

September 2005