FINAL

COMMUNICATIONS SITE PLAN

KIMBERLY PEAK

ELY FIELD OFFICE

Prepared by the United States Bureau of Land Management

Ely Field Office

State of Nevada

Approved by: _____/s/ Jeff Weeks___________________________    December 18, 2002

Assistant Field Manager, Nonrenewable Resources	Date

KIMBERLY PEAK COMMUNICATIONS

I.	INTRODUCTION	3

A.	Terms and Definitions	3

B.	Purpose	4

C.	Site Description	4

D.	Area Served	4

E.	Access	4

F.	Site History and Development	5

II.	AUTHORITY AND DIRECTION	6

A.	Authority	6

B.	Relationship to Communications Site Lease	6

III.	GENERAL RESPONSIBILITIES	6

B.	The Bureau of Land Management retains the responsibility for:	6

C.	Facility Owners and Facility Mangers (or their designated representatives) are responsible for:	7

D.	FCC and NTIA/IRAC are responsible for:	7

IV.	AUTHORIZED USES AND USERS WITHIN A FACILITY	8

A.	Exclusive Use of a Facility By a Single User	8

B.	Use by Multiple Users	8

V.	FEES	8

VI.	General Operation and Maintenance Direction	9

A.	Unique Resource Considerations at this Communication Site	9

B.	Wiring and Grounding	9

C.	Communications Equipment	9

D.	Cables and Transmission Line (Wave Guides)	11

E.	Radiation	12

F.	Utilities-Availability of and Requirements for:	12

G.	Sanitary Facilities	13

H.	Security And Law Enforcement	13

I.	Site Maintenance	14

J.	Inspections	15

K.	Fire Prevention and Hazard Reduction Requirements	15

L.	Access Maintenance and Restrictions	15

VII.	CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION	16

M.	Construction Methods and Resource Protection	17

N.	Construction Inspection	18

O.	New or Remodeled/Expanded Buildings	19

P.	New or Remodeled/Expanded Towers	20

VIII.	SITE ASSOCIATION/ADVISORY GROUP	20

IX.	APPENDICIES	21

A.	Site Map	21

B.	Authorized Facilities	21

C.	Site Photographs	21

D.	Inspection Checklist	21

INTRODUCTION

## Terms and Definitions

The terms used in this communication site plan conform to the definitions listed in the October 27, 1995, Federal Register notice “Fee Schedule for Communications Uses on Public Lands” and clarifications provided in Bureau of Land Management Handbook 2860-1.  In the event of a conflict, between the plan and these sources, the Federal Register notice and the Bureau of Land Management Handbook will govern.

The words “lease” and “lessee” as used in this plan refer to the relationship between the Bureau of Land Management and the communications use leaseholder.  The words “customer” and “tenant” refer to the relationship between the lessee and the occupants in the lessee’s facilities.

LEASE – An authorization issued to a communication facility owner or facility manager, allowing for the use of Public Lands to construct and or operate a communications facility and unless specifically prohibited, to sublease to occupants in that facility.

LEASEHOLDER OR LESSEE – Facility Owner/Facility Manager

CUSTOMER – Entities that pay a facility owner, facility manager or tenant for communications services and are not re-selling or broadcasting communications services to others

TENANT – A communications user who rents space in a communications facility and operates communication equipment for the purpose of re-selling, or broadcasting communications services to others for profit.

COMMUNICATIONS SITE – An area of public land designated through the land and resource management planning process.  A communications site may be limited to a single communications facility, but most often encompasses more than one.  Each site is identified by name; usually a local prominent landmark, such as Kimberly Peak Communications Site.

FACILITY MANAGER – The holder of a Bureau of Land Management communications use authorization who leases space for other communication users.  A facility manager does not directly provide communications services to third parties.

FACILITY OWNER – Individual, commercial activities, organizations, or agencies that, owns a communication facility on Federal land; own and operate their own communications equipment; and hold a communication use authorization.

NON-BROADCAST – This category includes Commercial Mobile Radio Service (CMRS), Facility Managers, Cellular Telephone, Private Mobile Radio Service (PMRS), Microwave, Local Exchange Network, and Passive Reflector.

BROADCAST – This category includes Television Broadcast, AM and FM Radio Broadcast, Cable Television, Broadcast Translator, Low Power Television, and Low Power FM Radio.

## Purpose

This plan is intended to be used by Bureau of Land Management officials, administering communication uses at Kimberly Peak, existing lessees, and applicants desiring a lease or a lease amendment.  The plan will be kept updated by amending pages or sections of the plan rather than issuing a revised edition of the plan.  When a revision is necessary, the plan will be amended by letter from the Assistant Field Manager, Nonrenewable Resources (AFM) enclosing a copy of revised pages or sections.  The amendments will be consecutively numbered.

Overall management direction for the administration of communications sites is outlined in the U.S. Code of Federal Regulations (CFR’s) and the BLM Handbook and applicable.  Specific direction for site management planning on designated communications site is contained in BLM Handbook 2860-1.  Primary regulations and policy pertaining to issuance of special-use authorizations by the Bureau of Land Management are found in Title 43, Code of Federal Regulations (CFR), Sections 2801- 2803 and BLM Handbook 2860-1

The 1983 Egan Resource Area’s Land and Resources Management Plan currently does not specifically address communications uses.  A comprehensive district-wide RMP/EIS is scheduled to begin later in 2002 and 2003.  This RMP will recognize and designate the Kimberly Peak communications site for mixed low-power, non-broadcast and broadcast uses.  Primary management of the current site is to assure historical two-way radio, point-to-point microwave, cellular, TV translators, and low power broadcast.

No communications site plan has ever been prepared for this site.  This plan has technical standards for better management of the Kimberly Peak communications site.  This plan governs development and management of Kimberly Peak and will be modified in the future as needs and conditions warrant.  Any future such uses must be designed, installed, operated, and maintained to be compatible and not interfere with the primary uses.

## Site Description

The site is located on a peak identified as Kimberly Peak which is located in the Ely District approximately 16 air miles northwest of Ely, Nevada in portions of Sections 27, T. 17 N., R. 61 E. MDM at approximately 39º 18’ 52” North Latitude and 115º 04’ 19” West Longitude.  The elevation on top of the Kimberly Peak Communication Site is approximately 9200 feet above mean sea level (msl).  The site is divided into three clusters of facilities.  A site map is provided as Appendix A.

## Area Served

This site primarily does not serve an RMA, Ranally Metro Area.  The largest community served is Ely, Nevada.  The population of Ely as of the 2000 Census is 4,041.  This information will be used for fee determination.

## Access

Full public right of way access to Kimberly Peak is from US Highway 50, about 10 miles west of Ely then 6.5 miles on a native material road.

## Site History and Development

Kimberly Peak and the surrounding area have been used for mining and exploration for decades.  The southern portion is on lands withdrawn for USAF radar and communications purposes (NEV-45154).  The buildings on this site are currently not being utilized and are deteriorating.  Plans are being considered to maintain some of these structures and utilize them. The saddle between the south and north peaks is utilized by Nevada Bell for microwave relay since 1974.  One additional small two-way radio repeater grant issued to Ameslco Minerals (Amselco -> Kennecott -> USMX -> Placer Dome -> WPEM) was authorized just south of the Nevada Bell facility in the saddle in 1982.  The Air Force also constructed facilities on the north peak under a right-of-way grant in 1966.  The BLM added two-way radio repeater equipment to the north peak in 1972.  The remaining facilities have all been developed at the north Kimberly Peak site.  Other uses include on the North site include White Pine County, Nevada Division of Lands, County Communications, Inc, two Cellular telephone providers, and an National Public Radio FM station.

- Goals and Objectives of Site Management Plan

1.	Kimberly Peak Site will be managed as a mixed broadcast and non-broadcast communication site.

2.	Communication equipment on Kimberly Peak Site will be managed to reduce the RF hazard to be within the Public Standard as defined by the FCC.

3.	The site will be systematically developed to maximize the number of compatible uses while ensuring safety and protection of resources.  Development of new towers or buildings within each of the authorized owner’s facilities will be authorized only after their respective tower or building space area is filled to near capacity.

4.	Present a program for future growth, development and operation with the site.

5.	Help fulfill the public need for adequate communication sites.

6.	Protect the interests of leaseholders and site users by preserving a safe and electronically “clean” environment.

7.	Encourage the efficient development and use of space and facilities within the designated site, subject to the Agency goal to provide the best possible public service at reasonable cost.

8.	Achieve visual quality objectives by requiring design standards that are unobtrusive and utilizing earth tone colors and non-reflective surface material and stringent site maintenance requirements.

9.	Describe the Agency policy for authorizing road use and maintenance.

10.	Establish the framework for a User’s Association, which could provide recommendations to the BLM authorized officer when there are two or more lessees.

11. New facilities will be developed only after the appropriate site specific NEPA analysis and coordination with current lease holders and users.  This future development must also be consistent with the Ely District RMP when approved.

12. This Communications Site Plan shall be amended as necessary to be consistent with the Revised Ely District RMP when it is approved.

AUTHORITY AND DIRECTION

## Authority

Bureau of Land Management authority to authorize communications uses on public land (administered by the BLM) is granted by the Federal Land Policy and Management Act of 1976, 90 Stat. 2776 (43 U.S. C. 1761-1771) and is reflected in Title 43, Code of Federal Regulations (CFR), Sections 2801- 2803 and WO IB 98-23.

Bureau of Land Management authority for communications site management planning is contained in Bureau of Land Management Handbook 2801-1, Plan of Development.  Direction on, and policy for communication use authorizations is contained in Bureau of Land Management Manual (BLM Manual) section 2860.

Authority for the issuance of authorizations and/or licenses for the transmission and reception of electronic radiation for communication purposes is granted by Congress and administered by the Federal Communications Commission (FCC) and/or the National Telecommunication and Information Administration – Interagency Radio Advisory Committee (NTIA/IRAC).

## Relationship to Communications Site Lease

This site plan will be incorporated into all leases issued for this communications site and must be used in conjunction with the lease. PROVISIONS OF THE SITE PLAN ARE ENFORCED THROUGH THE LEASE. Each lessee is expected to include the requirements of the lease and the site plan into any documents, which describe the business relationship between the lessee and the lessee's tenants and customers. The lessee is responsible for enforcing those provisions

GENERAL RESPONSIBILITIES

## A.  The Bureau of Land Management retains the responsibility for:

Issuing and amending leases to facility owners and facility managers, only for the areas actually occupied by the authorized improvements.  Granting occupancy and use of Public Lands rest exclusively with the Bureau of Land Management Title 43 CFR Sections 2801- 2803.  The issuance of a FCC license (authorization), or frequency assignment, does not authorize occupancy of Public Lands.

- Approving any new/modified facility(ies) at the site.

- Approving amendments to leases to qualified buyers of facilities on the site.

## B.  Facility Owners and Facility Mangers (or their designated representatives) are responsible for:

- Complying with their authorization and all sections of this Site Management Plan.

- Insuring that all new facilities, expansions, or improvements are consistent with the Ely District planning documents; any environmental document(s)/decisions for the site; and, this Site Plan.

- Ensuring facilities/equipment not complying with Federal/State/local laws/regulations/ ordinances will be removed or modified within one year of the approval of this plan.  Any modification need pre-approval by the Bureau of Land Management.

- Keeping all facilities within the established limits of their authorized area.

- Each Facility Owner and Facility Manager, or applicant for a new facility, will provide the Bureau of Land Management, with the name, address and phone number for a local contact person.  The Facility Owner and Facility Manager and the contact person may be the same individual.  The contact person will be available for emergencies and will have the authority to make decisions about construction issues, facility maintenance and all equipment within the facility.

- Under the Facility Owner/Manager Lease or Special-Use Permit:

  - Facility Owners and Facility Managers are authorized to rent building/tower space to tenants and/or customers without prior written approval from the Bureau of Land Management.

  - Tenants and/or customers using a facility covered by a Facility Lease/special-use permit will not have separate Bureau of Land Management permits to authorize the use.

  - Facility Owners and Facility Managers are responsible for complying with the terms and conditions of the Facility Lease or their valid Special-Use Permit.  Facility Owner/Managers are also responsible for ensuring that their tenants and customers are in compliance with the terms and conditions of the Lease or permit, and applicable FCC or NTIA/IRAC license terms and conditions.

  - The Facility Owner and Facility Manager may not place any unreasonable restrictions on tenants and/or customers, or potential tenants and/or customers.

- Facility Owners/Managers will ensure that all communications equipment is properly installed, operated, and maintained.

- Facility Owners/Managers will ensure that all communication equipment meets ANSI, FCC and Bureau of Land Management regulations, guidelines and standards concerning radiation limitations.

  - Monitoring radiation levels at their facility and;

  - Immediately correcting any radiation levels that are, or could be a hazard to human health.

- Each Facility Owner and Facility Manager must provide a certified copy of their use and the category of use along with the current phone numbers and addresses of all tenants and customers as of September 30th each year.  This report is due by October 15th.

## C.  FCC and NTIA/IRAC are responsible for:

The responsibilities of the FCC and NTIA/IRAC are frequency management.  Correcting interference problems is the responsibility of the affected licensees.  The FCC and NTIA/IRAC are not normally responsible for the resolution of conflicts when the licensees or agencies are operating within the limits of the authorizations.

AUTHORIZED USES AND USERS WITHIN A FACILITY

## Exclusive Use of a Facility By a Single User

Several facilities currently have no tenants or customers.  Unless unexpected demand occurs, these facilities will be allowed to remain as single users facilities at the Kimberly Peak Site.

## Use by Multiple Users

Use of new facilities and improvements by more than one user will be required.  Site applicants will take the lead in this area and design their proposals to accommodate multiple uses of facilities and improvements.  This includes multiple use of buildings, towers, solar generating systems, back-up generators, grounding systems, fuel containers, access ways and parking areas.

Due to the limited development space at the site, new facilities, or major modifications to existing facilities, must be designed to accommodate additional users even if other users are, or could be, competitors.

Clustering and consolidating of uses is required for multiple uses wherever feasible.  Examples would be locating all solar panels, fuel tanks, and/or battery storage vaults in a single area, or co-locating these improvements as close together as possible.

Facility Owners and Facility Managers are not required to lease facility space to others if they can prove to the authorized Bureau of Land Management officer that:

- Space is not available;

- The use is incompatible with the existing facilities;

- Additional space is needed by the facility owner/manager;

- Additional users would violate system security needs; or,

- Potential interference is not resolvable.

FEES

The Bureau of Land Management will charge Facility Owners and Facility Managers annual fees based on the Fee Schedule for Communications Uses on Public Lands as adjusted annually.  These fees will be fair market value for the use of Public Lands.  Since this site is not within an established RMA, Ranally Metro Area, the population zone of less than 25,000 will be used for these calculations unless specifically agreed by the authorizing officer.

Fees that Facility Owners and Facility Managers may charge their tenants and “customers” are to be:

1.	Reasonable and commensurate with the uses and occupancy of the facilities and services provided to tenants and “customers” and

- Consistent with, and not in excess of, other fees for similar facilities.

General Operation and Maintenance Direction

## Unique Resource Considerations at this Communication Site

- There are no currently identified special resource coordination considerations with on-site or adjacent resource values.  Should special conditions arise through the RMP/EIS process, this plan will be amended accordingly.

## Wiring and Grounding

1.	All equipment is to be installed within existing buildings and on equipment racks that are grounded and shielded.  Grounding is to be installed in accordance with accepted standards.

2.	All electrical wiring and grounding must meet the “National Electrical Code” and applicable estate codes.  All permanent wiring shall be installed in metallic conduit.  Surge protection shall be installed on all power distribution panels.

3.	Every effort will be made to protect the equipment from lightning damage.  Lightning protectors should be used on all coaxial cable connection to equipment enclosures.  Gas gap and MOV protectors should be used on all control/audio and power lines.

4.	Each building is to have its own separate grounding system for all users in that structure.  Wherever practical, interconnection of individual grids and/or the simultaneous placement of a large sized copper ground wire with any new grounding systems that are buried on the site will be encouraged.

5.	Grounding shall be installed in accordance with accepted practices and standards such as the Bell Standards.  Grounding using bentonitic clays is currently the only approved method for chemical grounding.  Other types of chemical grounding will require completion of NEPA documentation by the applicant prior to consideration for approval by the AFM.

## Communications Equipment

Equipment Ownership

All equipment shall be labeled with:

- The owner’s name;

- Transmitter frequency(ies);

- A valid FCC, or IRAF, authorization;

- Transmitting power output(s); and

- A current 24-hour phone contact number.

Transmitting Equipment

All transmitters will have protective devices, designed into or externally installed, to prevent interference to other users.  All transmitters will meet FCC licensing requirements.

The re-radiation of intercepted signals from any unprotected transmitter and its associated antenna system will be prevented by the use of appropriate filters (wide band and narrow band broadcast transmitters).

The direct radiation of out-of-band emissions (i.e. noise or spurious harmonics) will be reduced to a level such that they may not be identified as a source of interference as defined in the FCC Rules and Regulations (e.g. Part 90.209(e)).  If site noise (electromagnetic noise) becomes an issue, noise threshold limits will be established, and amended into the Site Plan.

All transmitters not in immediate use and not specifically designated as standby equipment shall be removed.  Loads connected to circulators are to be capable of dissipating the total power output of the transmitter.

Receiving Equipment

A bandpass device (cavity, crystal filter, etc.) is recommended at the input of all receiving devices.  Cavity filters, or other protective device, may be used at receiver inputs to reduce interference.

Where duplexing is used, use of the notch type device should be avoided.  In situations where a notch type device is used, a bandpass filter must be used with the transmitter.

Tower

- Generally only one tower is authorized for each facility owner.  Facility Owners and Facility Managers may obtain permission to construct the second tower only after submitting evidence that demonstrates that their existing tower(s) is/are completely filled and full use has been made of combining systems.

- All towers will be left unpainted, if they are dull, galvanized steel.  If paint is required, the Bureau of Land Management will approve only non-reflective colors from the Munsell Soil Color Chart, Standard Environmental Colors.  The exception is when the FCC requires red/white striping.

- No lights beacons or strobes will be allowed on towers (including antennas) less than 200 feet high.

Antennas

            - Whenever, the maximum antenna/tower height will be less than 200 feet.

            - Microwave (dish) antennas (other than ground mounted satellite dishes) will be limited to a maximum of ten (10) feet in diameter.  Smallest diameter dishes are preferred if technically feasible.

            - All antennas must meet all OSHA safety standards.  If an antenna exceeds FCC public or occupations standards, it will be remedied within 24 hours after measures are taken or isolated (e.g., fencing, signing, relocation, lowering power levels are all possible remedies).  Ground measurements of RFR levels will be taken before mitigation measures are implemented.

            - Color(s) for dish antennas, or covers, must be pre-approved by the Bureau of Land Management.  White dish antennas and/or covers will not be approved.  Existing white dishes and covers must be repainted or replaced as repairs or replacement become necessary.

            - Antennas will be treated for low to non-reflectance.

            - High-powered omni-broadcast antennas placed on tapered towers will be placed with the least face width feasible.

            - Low-powered transmit and receive antennas will be located close to the ground.

Interference

The responsibility for correcting interference problems is a matter for resolution between the permit/lease holder of the facility(ies), the user causing the interference, and the affected party(ies).  Generally, the first users on a site have seniority with respect to the resolution of interference complaints.  Senior holders have an obligation to maintain their equipment to industry standards, to operate their systems in accordance with the terms of both the FCC license and NTIA/IRAC frequency authorization, and to comply with the Bureau of Land Management authorization.  New users on a site must correct, at their expense, interference problems that they create.  They must cease operation of the suspect equipment until the problem is corrected.  If interference problems cannot be resolved or corrected within a reasonable time, the new use that is causing the interference may be terminated and the equipment removed.

The Bureau of Land Management does not have authority for correcting interference problems, but can act as a mediator to help all affected parties.  Interference problems should be coordinated with the FCC or NTIA/IRAC whichever is appropriate.

Interference with law enforcement and/or emergency communications must be corrected immediately.  The operation of equipment covered by this Site Plan shall not interfere with United Sates Government radio or electronic operations already in existence on public land within two (2) miles of the site to which this authorization refers.  The user causing this interference, shall, at its own expense, take all action necessary to prevent or eliminate such interferences.  If it does not eliminate such interference within ten (10) days after receipt of notice from the Bureau of Land Management to do so, this use will be terminated.

If electromagnetic noise becomes an issue, noise thresholds will be established and amended to this Plan.

## Cables and Transmission Line (Wave Guides)

All new cabling will be jacketed and shielded and shall either be flexible or semi-rigid type (with the exception of rigid wave guide and rigid transmission line for high power TV broadcasters).  Existing substandard cables will be upgraded as repairs or replacement become necessary.

Cables will be properly installed and will be strapped and fastened down.  Use of ports at building entrance points will be kept to a minimum by use of combiners.

When attaching cables onto a tower, conduits should be used and cable runs should be equally divided among all tower legs.

All transmission lines (wave guides) are to be supported in accordance with manufacturer’s specifications.

Double shielded braided, or solid shielded cable will be used.  No RG-8 type cable is permitted.  No connector-type adapters will be used on transmission lines.  Only correct connectors that will mate to connected devices are to be used.

Conduits will be shared when they service common areas and will be buried where possible.

## Radiation

All communications uses must meet ANSI, FCC and Bureau of Land Management regulations guidelines and standards concerning radiation limitations.

Monitoring radiation levels at the site is the responsibility of all site users and will occur at intervals to comply with FCC regulations and guidelines.  A copy of the monitoring report will be provided to the Bureau of Land Management within 30 days of its completion.

Onsite RFR measurements will be taken using appropriate equipment that can adequately measure both on-tower and on the ground levels before mitigation measures related to RFR are implemented.

Security fences with RFR notice signs are required around areas that exceed public use levels.    Raising higher power transmitting antenna on the tower or adding a taller tower may be necessary to eliminate RFR hazards.  Reducing power may also be required if other alternatives are not feasible. All fencing location and design or new tower construction must be pre-approved by the Bureau of Land Management.   On the North site single facility fencing will not be permitted.  If fencing is determined to be necessary, a single perimeter fence with a single access gate must be designed and maintained to serve the entire peak.

Warning signs will be in English and Spanish and will comply with ANSI C95.2 color, symbol, and content conventions.  Contact information including name and telephone number will also be included on warning signs.

Lowering power levels for on-tower access during maintenance will be coordinated between effected users.

Any identified RFR radiation problems that are, or could be, a human health hazard must be corrected within 24 hours after measurement tests have been completed or be removed from the site by the site user(s).  If the proposed corrective action involves any new ground disturbance, it must be pre-approved by the BLM.

## Utilities-Availability of and Requirements for:

Commercial Electrical Power

Commercial power is provided to the site under permit to Mt Wheeler Power.  The distribution line and portions of the service drops are aerial.  Future service drops or modifications will be buried.

Telephone Service

There is no hardwire service provided to this site.

If this service is every deemed necessary, site users will pay for the cost of:

- The necessary resource surveys and reports for service connections; and

- The cost of constructing service connections.

For visual reasons, overhead utility poles may not be authorized.

Fuel Tanks

All facility owners are responsible for providing fuel storage (propane and diesel) and emergency power for their tenants.  No tenants will be authorized to have separate fuel tanks and/or generators. Each facility owner will preferably consolidate fuel storage into a tank large enough in size to accommodate all tenants.  At a minimum, tanks will be grouped together in a consolidated area adjacent to their facilities.  All fuel, storage tanks (e.g. LPG, propane and diesel) must meet current fire department, Federal, State and County safety and hazardous materials requirements.

- All tanks will be:

a.	Signed in red letters, “SMOKING OR OPEN FLAME PROHIBITED WITHIN 20 FEET”;

b.	In conformance with National Fire Protection Association (NFPA) requirements; and,

c.	Painted an approved color, or screened by an enclosure to blend in with the natural environment.  If an enclosure is used, it must be pre-approved and painted an approved color from the Munsell Soil Color Chart, Standard Environmental Colors.

2.	Diesel tanks will also be:

a.	Enclosed in Bureau of Land Management and fire department approved secondary containment vaults that are painted a Bureau of Land Management approved color from the Munsell Soil Color Chart, Standard Environmental Colors.

b.	Constructed with underground fuel lines.  Fuel line must be constructed of black, treated pipe and fittings, and must be posted.

## Sanitary Facilities

1.	Plans for any new sanitary facilities must be pre-approved by the Bureau of Land Management.  If it is determined by the Bureau of Land Management that the users need such facilities, they will be provided by the applicant/holder in a manner and location satisfactory to the Bureau of Land Management and within the requirements of the County Health Department.

## Security And Law Enforcement

The County Sheriff’s Department is the key law enforcement agency for the area.  They are responsible for most civil and criminal matters.  The Bureau of Land Management will be responsible for enforcing matters related to uses of BLM lands (e.g. resource protection issues).

Patrolling and policing for security purposes is the holder’s responsibility.  If holders desire to have the protection of extra fencing, Bureau of Land Management approval must be obtained first.  To reduce visual clutter and efficiently utilize existing space, fencing groups of buildings will be encouraged.

No gates are currently on the access road.  If fencing is deemed necessary, the location of the fence and gates must be approved in advance by the BLM and must be adequate for Bureau of Land Management and County Fire Department access needs.

Fencing

1.	All fences must meet health and safety requirements.

2.	All fence locations and design require Bureau of Land Management pre-approval.  The standard fencing type will be chain-link (i.e. cyclone)

3.	The standard fence height will be eight (8) feet.

4.	Fencing will be designed and of a type to minimize interference issues.

5.	Fences will be signed with RFR notices if RFR is above public levels.

6.	All cyclone-type fencing materials will be galvanized.

## Site Maintenance

The objective of maintenance activities is to present a clean, neat, and orderly appearance at the site and have all of the authorized improvements safe for workers and the public.  All users will keep up the overall appearance of the site.

Miscellaneous debris remaining after any construction and/or equipment installation, removal or modification, is not only a hazard, but can cause interference or intermodulation problems.  In particular, all loose wire or metal objects are to be removed from the site.

The users of the Site will remove all graffiti within 10 working days of finding it.  If graffiti is on natural features (e.g. rocks), the graffiti will be removed in a method approved by the Bureau of Land Management.

Holders will not be permitted to leave or dispose of trash, garbage or cut brush on BLM administered lands.  No outside trash or litter containers will be provided.  Site users (i.e. holders) will remove litter from the site as it is produced.

Policing of litter in common areas (i.e. areas between buildings and developed sites) is the shared responsibility of those holders bordering these areas.

During construction and/or maintenance, paintbrushes will not be cleaned off on the rocks around the site and excess materials (e.g. cement) will be removed from BLM administered land.

Peeling paint on buildings and/or towers will be re-painted within thirty (30) days of discovery.

## Inspections

Unless waived in writing by the Bureau of Land Management, the holder is to provide, annually, a certified inspection of the facilities and equipment covered by the authorization.  The inspection will include technical review that should assure that authorized equipment is operating within the specifics of this Site Plan, the FCC authorization, ANSI Standards, and the manufacturer’s specifications.  In addition, the inspection should assure that the authorized equipment is secure, free of rust, properly grounded, and otherwise properly operated and maintained.  This inspection should also review general good "housekeeping". A copy of the inspection report, certified by a telecommunication specialist, is to be provided to the Bureau of Land Management within 30-days of completion.  Appendix D provides an example of the inspection checklist.

The Bureau of Land Management may also conduct periodic reviews to monitor for authorization compliance.

## Fire Prevention and Hazard Reduction Requirements

Facility owners and managers will be required to maintain to mineral soil, a minimum of (30) feet clearance around their buildings and a minimum of then (10) feet clearance around any propane tanks.  Identified threatened, endangered, or sensitive plant species must remain within the minimum clearance areas.

Smoking is prohibited while walking in flammable vegetation.

The roof structure shall be kept reasonably clear of leaves, twigs, and other debris at all times.

No explosive will be stored at this site.  Flammable materials shall be stored in conformance with the requirements of local fire regulations.  Flammables will be placed in closed containers and stored away from sources of ignition and combustible materials.  If flammables are stored within a building, the building will be locked, properly signed and well ventilated.

Maintain approved spark arresters on all internal combustion engines.

At least one (1) U.L. rated 4 B:C dye chemical fire extinguisher is required inside each building.  Prior to each June, fire extinguisher(s) shall be inspected and refilled, if necessary.

Any fire will be immediately reported to “911”, the nearest Bureau of Land Management Station or County Sheriff.

Bureau of Land Management Officers will make periodic fire prevention inspections.  They will call to your attention any lack of compliance with the above regulations, plus any other existing hazards.  Compliance with these inspections is required within the time limits specified.

## Access Maintenance and Restrictions

Roads

The primary access road is all on public lands on a graded road from US Highway 50 approximately 10 miles west of Ely.  The last 6.5 miles has guard rails on the upper portion which were originally constructed when the site was actively utilized by the Air Force.  The entire road is on public lands administered by the BLM.  A road maintenance agreement with appropriate blading, drainage and water bar maintenance standards will be developed between the BLM and site users.

Holders who damage or disturb the access road, or any associated structures, such as ditches, culverts, roadside vegetation, signs and/or underground utilities or facilities, will be required to repair the road to conditions equal to or superior to those prior to any damage or disturbance.

Interior Site Driveways/ Parking Areas

Roads within the communications site will be the responsibility of the site users.  Interior roads will be planned and approved during establishment of new facilities.  Interior roads will be maintained in a manner to allow only one entrance to the site.  The intent is to discourage off-road vehicle use in and around the site.

Road Closures

Roads on public land are subject to periodic closures to entry during periods of extreme fire danger, inclement weather, or wet roads.  Authorized site users may use the site during these general closures, if advance approval is obtained from the Bureau of Land Management.

CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION

In addition to the responsibilities listed in Section III, New Facility Owners and Facility Managers are responsible for:

1.	Submitting a complete application to the Ely Field Office prior to any new construction, or modifications to existing improvements  (ATTN: “Realty Specialist”).  The application must include:

a.	A copy of the approved Site Plan Base Map showing all of the proposed (new) facilities including structures, towers, and auxiliary equipment;

b.	Completed drawings/plans prepared by a registered engineer and approved by the Bureau of Land Management;

c.	Identification of any microwave beam paths, a plot of their azimuth(s), and their proposed elevation(s) on the tower;

d.	All proposals must include documentation that shows that proposed facilities will not be obstructing, or interfering with, any existing fixed point to point antennas, omni directional broadcast antennas, or microwave beam paths in the directions of primary population targets.  Proposed beam path needs must be shown on Site Plan Base Map; and,

e.	Any needed recommendations, changes or modifications to their original proposal, based on any required resource surveys and/or reports.

2.	Demonstrating that their proposals will not cause undue interference with any existing uses before the Bureau of Land Management can approve new facilities.  In addition, it is the applicant’s responsibility to show that any new facilities will make the most efficient use of the limited amount of space at the site.

3.	Showing their proposals will provide for future users without additional construction are encouraged.

4.	For providing engineering and geotechnical investigations for development of specific foundation designs and grading plans.

5.	For providing an Erosion Control Plan prior to construction activities.  At a minimum, the Erosion Control Plan must include: sediment control, stipulations that cut/fill slopes will be graded and contoured to prevent erosion and/or excessive runoff, and recommendations for temporary erosion control measures, (e.g. netting, silt fences, swales, and/or sediment collection areas).

6.	Coordinating with other Federal (e.g., FCC and FAA), State and County agencies and obtain all required approvals and/or permits.

7.	Providing 30-day notice to all facility owners/managers at the site, as well as the Bureau of Land Management, of all new frequencies proposed for the site.  A completed BLM technical data sheet or equivalent must be sent with the 30-day notice to allow for comment of potential interference.  This would be for new frequencies for themselves and their tenants.

8.	Insuring that all written approvals have been obtained from the Bureau of Land Management prior to construction.  In addition:

a.  Directional broadcast antennas (e.g. translators) will only be protected within the arch between their licensed 3 dB point.

b.   New and/or modified facilities will not obstruct existing fixed point-to-point antennas or omni-directional broadcast antennas in directions of primary population targets.

## Construction Methods and Resource Protection

Plans submitted by an applicant for any new construction or modifications shall specify provisions for soil rehabilitation measures including, but not limited to, soil replacement and stabilization and for proper handling of runoff from buildings, parking area, access roads, and undeveloped common areas.

During construction, the following methods and resource protection measures will be required to minimize impacts:

1.	Identify, avoid and protect sensitive resource area, as identified by the Bureau of Land Management.

2.	Compliance with the Erosion Control Plan.

3.	During construction and/or maintenance, paintbrushes will not be cleaned off on rocks around site and no marks of any kind (including survey) marks will be permitted on rocks.

4.	Minimize ground disturbance and vegetation removal as much as possible during construction activities.  All ground-disturbing activities require Bureau of Land Management pre-approval.

5.	Any extensive cut and fill slopes will be re-vegetated with native vegetation as soon as possible after construction.  All re-vegetation requires Bureau of Land Management pre-approval for possible NEPA evaluation and seed mixture type.

6.	 No grading material will be cast off during construction/reconstruction activities. Excess soil can be used for fill material on road and/or building/tower pads.

7.	Temporary, on-site storage of construction materials will require pre-approval by the Bureau of Land Management.

8.	Construction materials and supplies, except for hazardous materials (see number 10. below) may be left unattended at the construction site at the end of each workday, but at the owner’s risk.

9.	Hazardous materials, including, but not limited to all fuels, oils, and lubricants are not to be left unattended at the site at any time.  During construction, these materials are to be removed from the site at the end of each workday, or temporarily stored inside a locked and signed building until the following workday.

10.	All surplus construction materials and/or waste debris must be removed from the site no later than thirty (30) days after construction has been completed.

11.	Any earth moving or heavy equipment (e.g. dozers, graders, cranes, backhoes, etc.) leaving the designated roadway and/or approved parking area(s) to perform authorized activities at the site, will be washed off prior to being brought onto public lands to prevent the introduction and spread of noxious weeds into the area.

## Construction Inspection

1.	All new construction, reconstruction, or major modification shall conform to the established technical standards and accepted engineering practices (i.e., the Uniform Building Code).

2.	Any construction inspections required by other applicable agencies are the responsibility of the holder.  Copies of completed inspections are to be provided to the Area Manager, either as they occur or as part of the final as built plan.  Inspection information shall become a permanent part of the proponent’s special-use file.

3.	The Holder agrees that corrective work detailed in Bureau of Land Management, or other agency required compliance inspections, would be completed by the scheduled completion date.  If the Holder disagrees or has questions about specific items, the Holder must contact the Bureau of Land Management in order that the disagreement or item may be resolved.

4.	A final set of as-built plans will be submitted to the AFM within 90 days of acceptance of structure (if contracted) or of completion date.

## New or Remodeled/Expanded Buildings

- Any new buildings must be designed to accommodate multiple users along with fitting into the physical environment as defined in a site-specific environmental analysis developed at the time of the proposal.

- Buildings are required to be one-story, flat roofed.  The roof must be metal or covered with metal to be fire resistant.  Roofs can be equipped with antenna support structures, such as poles and railings that can extend up to 25-feet above ground level.

- Facility Owners and Facility Managers are encouraged to construct the interior of their buildings in a modular fashion, so that they can:

a.	Sublease sections to others;

b.	Provide tenants and customers with internal separation and security;

c.	Reduce physical interference; and

d.	Increase management effectiveness.

- The following materials are approved for construction of new facilities (i.e. buildings)

#### a.	Floors – Concrete slab with drainage.

b.	Walls – Concrete block, metal or pre-fabricated concrete.

c.	Roof – Metal, or concrete, if painted to eliminate shiny surfaces, or other fireproof material as approved by the Bureau of Land Management.  Proposals for wooden roofs will not be approved.

d.	Partitions – If it is felt partitions are necessary in buildings, ensure they are constructed with fire resistant material (e.g., concrete block, reinforced concrete, or properly grounded expanded metal.

e.	Color – Proposed color for use on all exterior building surfaces must be pre-approved by the Bureau of Land Management. The goal of the color selection for the facilities is to make the building as inconspicuous as possible and make buildings located on the skyline look inconspicuous when viewed from a distance.  The intent is to reduce or eliminate glare from reflective and/or illuminated surfaces such as windowpanes, sheeting and reflective paints.  Non-reflective, Bureau of Land Management approved earth tone colors will be used on equipment buildings; refer to the Munsell Soil Color Chart, Standard Environmental Colors

- Building entry lights must:

a.	Only light the immediate area in the vicinity of the door;

b.	Be motion activated and have a limited time duration (e.g., 3-5 minutes); and

c.	Have a shielded beam that is pointed at the building door.

Requests for all-night (i.e. “dusk-to-dawn”) lighting, or entry lighting that would be visible from outside of the site will not be approved.

## New or Remodeled/Expanded Towers

- All new construction, reconstruction, and modifications to towers will be pre-approved by the Bureau of Land Management prior to implementation.

- It is the applicant/holder’s responsibility to assure that a new, or modified, structure will not unduly interfere electronically or physically with any existing equipment at the site.  Towers must be spaced, so as to prevent ground level radiation and/or interference problems.  This must be clearly demonstrated in writing to the Bureau of Land Management prior to issuance of a lease, permit, or amendment.

- All new towers will comply with current structural and safety specifications and design standards, including safety-climbing devices.  Towers should be as narrow and “open” as safety and structural integrity allow.  New towers should be designed using maximum wind, snow, and/or tower loading anticipated for the site.

- All towers greater than 100-feet in height will be tapered to minimize visual concerns.

SITE ASSOCIATION/ADVISORY GROUP

A Site Users’ Association may be desirable at this site.  If formed for the Kimberly Peak Communication Site in the future, it would be responsible for participation in an access road maintenance agreement, maintenance and upkeep of internal roads and parking areas.  The Site Association will also be responsible for ensuring cooperation between users for on-tower access.  A Site Safety officer would be identified within the Site Association. The Site Association would be expected to develop an RFR Plan/Agreement and recommend measures to reduce interference issues (e.g., through use of filters).

The goal of the Site Association will also be to maximize the effective use of the site.  The objective of a sanctioned association will be to represent all site users as a group when dealing with the Ely Resource Area on matters relating to the Site administration.  The association will be able to work in cooperation with the Bureau of Land Management to identify problems or opportunities and make recommendations to the Bureau of Land Management for any changes in management strategies at the site.  The association could also provide input to the Bureau of Land Management regarding the future addition of equipment and facilities at the site.  While the advice and recommendations of the association would not be binding on the Bureau of Land Management, the Bureau of Land Management could use the input for administration of the site.  The Bureau of Land Management would be a member of such a group and would help jointly develop the charter (i.e., the ground rules).

In absence of a formal Site Association, the Bureau of Land Management may utilize a Site Advisory Group that can make suggestions and/or recommendations to specific problems associated with the administration of the site.

APPENDICIES

## Site Map

## Authorized Facilities

## Site Photographs

## Inspection Checklist

APPENDIX A

SITE MAP

(See associated AutoCad Map on this website)

APPENDIX B

LEASEE FACILITY TABLE

(See associated User’s Table on this Website)

|  | Auth # | Use | Building | Tower | Access/Parking | Other |
| --- | --- | --- | --- | --- | --- | --- |
| USAF | N-00325 | FAM | 8’x 10’ | 65’ guyed | Access and parking |  |
| Country Comm | N-037740 | CMRS | 8’x 18’ trailer | 13’ mast, antenna on USAF twr | Access and parking |  |
| WP County | N-46062 | PMRS | 7.5’x 12’ | On USAF | Access and parking |  |
| BLM | N-46696 | PMRS | 8’x 10’ | 65’ lattice | Access and parking |  |
| Western Wireless | N-58026 | CEL | 10’x 20’ | 100’ lattice | Access and parking | Propane generator |
| White River Ranch | N-76268 | PMRS | 3’x 3’ | Mast | Access and parking |  |
| Nevada Bell | N-6401 | MIC | 27’x 21.5’ | 70’ lattice Wood pole | Access and parking | Fence Vault |
| Placer Dome | N-31982 | PMRS | 4’x 6’ | 20’ guyed | Access and parking |  |

APPENDIX C

SITE PHOTOGRAPHS

(See associated Facility Photos on this Website)

APPENDIX D

INSPECTION CHECKLIST

COMMUNICATIONS SITE INSPECTION CHECKLIST

EXAMPLE

Site Name  Big Mountain                	Date  5/26/92

Inspector(s) Name   James Holder

I.  Site Inspection.  Each communications site should be inspected at least once each year.  Inspections should include a careful examination of:

1.  Power Systems

a. Power lines - (10ft. clearance from average snow level)

b. Solar Array

c. Generators-Fuel Storage

d. Batteries

- Safety venting

- eye wash

- goggles

e. Wiring

f. Protection (fuses)

2.  Grounding

a. Building

b. Antenna system

c. Equipment

d. Lightning Protection

e. Standby Power

3.  Conformance to

a. Equipment Manufacturers Specifications.

- Installation

- Maintenance

b. Conditions of Permit

c. Safety Standards

d. Specification of Site Plan

e. Specification of Site Design

f. Conditions of License or Authorization

4.  Structures

a. Towers

b. Buildings

c. Cable Trays

5.  Electromagnetic Environment

a. Site Noise Level

- Ambient (noise floor) (General Electric ECP-877A)

- Transmitter produced

b. Effective Receiver Sensitivity

c. Electromagnetic Radiation Safety

- Levels (ANSI C95.1 - 1982)

- Signing

- Fencing

6.  Housekeeping

a. Internal

b. External

COMMUNICATIONS TOWER INSPECTION CHECKLIST

Tower Owner        James Holder                                 Date of Inspection  5/26/92

Name of Inspector(s)  Joe Technician & James Holder

| TOWER | YES | NO |
| --- | --- | --- |
| Bent or fractured cross members? Loose or missing bolts? Broken or cracked welds? Signs of unusual stress? Twisted or distorted tower? Signs of rust, pitting, rot, etc.? Does the tower need paint or repair? | X X | X X X X X |

Condition of galvanizing:   GOOD

Condition of paint (faded, peeling, etc.):  PAINT IS PEELING

Condition of cat walk:    GOOD

Condition of climbing pegs or steps:   GOOD

Condition of fall safety system:    GOOD

NOTES:  James Holder has contacted Service R Us to plan to paint tower.

Painting to start on 6/10/92___________________________________________

| GUY WIRES | YES | NO |
| --- | --- | --- |
| Broken guy wire strands? Any rust or deterioration noted? |  | X X |

Guy wire connections; preforms         clamps         both    X

Conditions of thimbles and shackles:   GOOD

Condition of preforms and/or cable clamps:   GOOD

NOTES:   General maintenance completed last year._____________________________

______________________________________________________________________________

______________________________________________________________________________

| GROUNDING SYSTEM | YES | NO |
| --- | --- | --- |
| Grounding clamps, straps or wires, broken or torn? Connections clean and secure? Lighting rod at the top of the tower? Signs of arcing? Gradual curves in grounding wires? Transmission line lightning-loop secure at the bottom of the tower? | X X X | X X X |

Condition of antenna grounding:   GOOD

Condition of transmission line grounding kits at the top and bottom:    GOOD

NOTES:   MAINTENANCE COMPLETED LAST YEAR._________________________

_____________________________________________________________________________

_____________________________________________________________________________

| ANTENNA AND TRANSMISSION LINES | YES | NO |
| --- | --- | --- |
| Antennas stable? Bolts and connectors secure? Connections to transmission weather sealed transmission line brackets/wire ties secure? Signs of transmission line slippage? Waterproof jacket unbroken transmission line secured at 3 ft. intervals? Hoist Grip secure? Gradual Curves in transmission line? | X X X X X X X |  |

Condition of antenna mounting hardware:   VERY GOOD

Physical damage to antenna and line (dents, cracks):  NONE

NOTES:   ____________________________________________________________

_____________________________________________________________________

_____________________________________________________________________

ACTION ITEMS:  PAINTING TOWER - TO BE COMPLETED 6/2________

______________________________________________________________________

______________________________________________________________________