May 6, 2004

SUBJECT:	National Environmental Policy Act (NEPA) Review for Property Transfer,

Demolition and Construction of New Cereal Crops Laboratory Madison,

Wisconsin

TO:	Hugene Fields, Project Manager, Facilities Engineering Branch

FROM:	Adrianna Hewings, Director, Midwest Area

As requested, Jerry Roberts, Area Engineer (AE), Caryl Romine, Area Safety and Health Manager (ASHM), Ralph Jesse, Area Environmental Protection Specialist (AEPS) and I have reviewed the subject related environmental and design documents.  Utilizing NEPA and ARS guidelines, the proposed land transfer, demolition and construction projects were examined for environmental issues based on known conditions and information available to us as of this date.  Reasonable effort was made to review and verify all information whenever possible.

Our findings and recommendations are based upon:

•	the Aries Consulting Group, Inc. Phase I Environmental Site Assessment prepared for

CUH2A, Inc. dated March 2003;

•	the Aries Consulting Group, Inc. Phase II Environmental Site Assessment prepared for

CUH2A, Inc. dated June 2003;

•	the CUH2A, Inc. 95% Design Submittal dated April 2, 2004; and

•	discussions with ARS Location personnel (David Peterson and Jean Weinbrenner).

FINDING 1:

Chlorinated Solvents have been detected in subsurface soils and groundwater at concentrations above the Wisconsin Department of Natural Resources (WDNR) contaminant limits on the subject property.  Twenty-one Leaking Underground Storage Tanks (LUSTs) have been recorded within a 1 mile radius.  During the 1998 removal of Underground Storage Tanks (UST) at the University of Wisconsin Power Plant (505 Walnut Street), chlorinated solvents and fuel oil were released to soil.  Aries Consulting Group, Inc. (Aires) performed an analytical assessment and reported the presence of chlorinated solvents, specifically dichloroethylene, trichloroethylene and tetrachloroethylene plus Gasoline and Diesel Range Organics (GRO / DRO) contaminants such as benzene, toluene ethylbenzene and xylenes in either soil and/or groundwater samples with only tetrachloroethylene exceeding the 5 µg/L WDNR contaminant level.  Levels exceeding cleanup objectives were noted in both up-gradient and down-gradient wells.  Aries reported that an interview with a WDNR representative revealed the presence of the chlorinated solvents and GRO / DRO contaminants are a regional problem of an unknown source.  The WDNR does not

National Environmental Policy Act (NEPA) Review – Madison, Wisconsin	Page 2

believe the contaminants are the result of a release from the neighboring University of Wisconsin Power Plant (even through contaminants from that spill have escaped property boundaries) or a release on the subject property.  The EPA has removed the site from the CERCLIS cleanup list and designated the property No Further Remedial Action Planned (NFRAP).  No further action recommended.

FINDING 2:

Following the transfer of property, 2 buildings will require demolition.  Aries performed an assessment of buildings 502 and 504 for asbestos, lead and polychlorinated biphenyls (PCBs).  Materials evaluated included paint, thermal insulation, lab countertops, floor tiles and mastic, drywall and joint compounds, ceiling tiles, and plaster ceilings and walls.  Asbestos containing building materials were discovered in both buildings.  In accordance with the National Emission Standards for Hazardous Air Pollutants (NESHAP) friable asbestos must be removed prior to demolition.  The Design And Construction Project Manual thoroughly addresses the processes required to abate the asbestos prior to building demolition.  No further action recommended.  Lead Based Paint (LBP) was discovered in building 502.  Aries reported the lead levels are less than the contractor release criteria established by the Department of Housing and Urban Development (HUD).  Even though the HUD guidelines do not directly apply to this project, they are scientifically valid and safe.  No further action recommended.  Polychlorinated biphenyls (PCBs) were not identified through testing.  The potential for PCB equipment to be present exist since both 502 and 504 were built prior to 1979 when electrical equipment such as transformers, capacitors, switches, voltage regulators and fluorescent light ballasts were cooled with heavy oils containing PCBs.  Aries performed an on-site inspection of pole-mounted and pad-mounted transformers and related electrical equipment and reported them to be in good condition and no leaks were noted.  The Design and Construction Project Manual addresses the processes required to remove PCB containing equipment prior to building demolition.  No further action recommended.  No further environmental assessment is requested for the subject project.

CONCLUSION:

Based upon the above findings, the MWA NEPA Review Team recommends an acceptance of the environmental assessment reports and recommends the transfer of the subject property from the USDA-Forest Service to the USDA-ARS with a Conditional Finding of No Significant Impact (FONSI) statement.  We recommend the transfer papers delineate the presence of exiting subsurface soil and groundwater contaminants and identify previous owner’s responsibility for future cleanup liability.

If you have comments or require additional information please contact either Caryl Romine at 309-681-6608 (cromine@mwa.ars.usda.gov) or Ralph Jesse at 309-681-6644 (ralph.jesse@mwa.ars.usda.gov).

cc:

T. Rupe, PS

D. Strub, AAO

D. Peterson, LC

J. Weinbrenner, LAO

J. Roberts, AE

C. Romine, ASHM

R. Jesse, AEPS