## LCOE - IGFC
Table 1. Levelized Cost of Electricity from advanced PC, IGCC, and IGFC power plants, with and without CO2 capture and storage
|  | Baseline power systems (no CO2 capture) | [6 empty] | Systems with CO2 capture, compression, and storage
|  | SCPC | GEE IGCC | Adv IGCC | Atm IGFC | Press IGFC |  |  | SCPC | GEE IGCC | Adv IGCC | Atm IGFC | Press IGFC
Information source |  | 1 | 1 | 2 | 3 | 4 |  |  | 1 | 1 | 2 | 3 | 4
Operating Parameters
Efficiency |  | 39.1% | 38.2% | 45% | 49% | 62% |  |  | 27.2% | 32.5% | 40.16% | 42.26% | 57.01%
Capacity factor (hr/yr/8760hrs) |  | 85% | 80% | 90% | 90% | 90% |  |  | 85% | 80% | 90% | 90% | 90%
% of power from steam cycle |  | 100% | 38.8% | 38.6% | 26% | 0% |  |  | 100% | 36.9% | 36.9% | 26% | 0%
O2 requirement (lbO2/lbdry coal)) |  | 0 | 0.89 | 0.89 | 0.8 | 0.52 |  |  | 0 | 0.89 | 0.89 | 0.8 | 0.52
% CO2 capture |  | 0% | 0% | 0% | 0% | 0% |  |  | 90% | 90% | 90% | 100% | 100%
Total CO2, kgCO2/kWh |  | 0.83162 | 0.85121 | 0.72259 | 0.6636 | 0.52446 |  |  | 1.1955 | 1.0005 | 0.80964 | 0.76937 | 0.5704
CO2 compression % inerts | [8 empty] | 0% | 0% | 0% | 6% | 6%
Parasitic load due to CO2 capture | [8 empty] | 11.9% | 5.7% | 4.839% | 6.736% | 4.994%
Cost Data | [6 empty] | Scaling Factors
Capital cost, $/kW net
Coal handling |  | 97 | 141 | 122.6711 | 114.1054 | 93.42 |  | 0.85 | 122 | 166 | 138.6667 | 132.7811 | 102.9622
ASU |  |  | 287 | 249.6923 | 212.1359 | 120.4271 |  | 0.85 |  | 342 | 285.6867 | 249.8615 | 134.3437
Gasifier |  |  | 426 | 382.9681 | 362.3459 | 310.954 |  | 0.65 |  | 498 | 433.9885 | 419.831 | 345.6259
Gas clean up |  | 229 | 203 | 176.6116 | 164.2794 | 134.4984 |  | 0.85 | 302 | 238.6031 | 199.315 | 190.8553 | 147.9946
Combustion turbine/fuel cell |  |  | 187 | 187.8378 | 407 | 550 |  | 0.85 |  | 238 | 238 | 471.8704 | 598.1851
Boiler |  | 510 | 0 | 0 | 0 | 0 |  | 0.65 | 660 | 0 | 0 | 0 | 0
HRSG |  | 65 | 89 | 88.6264 | 64.6105 | 0 |  | 0.8 | 70 | 99 | 99 | 74.8157 | 0
Steam turbine |  | 204 | 105 | 104.5317 | 74.7153 | 0 |  | 0.85 | 232 | 116 | 116 | 86.1416 | 0
CO2 capture |  | 0 | 0 | 0 | 0 | 0 |  | 0.65 | 752 | 175.3969 | 152.8519 | 0 | 0
CO2 compression |  | 0 | 0 | 0 | 0 | 0 |  | 0.85 | 85 | 68 | 56.8032 | 59.4882 | 46.1289
Other |  | 470 | 375 | 375 | 375 | 375 |  | n/a | 647 | 449 | 449 | 449 | 449
Total capital cost, $/kW net |  | 1575 | 1813 | 1687.939 | 1774.1925 | 1584.2995 |  |  | 2870 | 2390 | 2169.312 | 2134.645 | 1824.2405
Variable O&M, cents/kWH |  | 0.487 | 0.649 | 0.55093 | 0.50596 | 0.56496 |  |  | 0.936 | 0.809 | 0.52519 | 0.49907 | 0.54957
Fixed O&M, $/kW/yr |  | 25.175 | 35.28 | 35.28 | 52.9638 | 60.4166 |  |  | 37.375 | 43.74 | 43.74 | 60.5778 | 68.0306
Fuel cost, cents/kWh |  | 1.5707 | 1.6077 | 1.3648 | 1.2534 | 0.99058 |  |  | 2.2579 | 1.8897 | 1.5292 | 1.4532 | 1.0774
CO2 cost, cents/kWh |  | 2.4949 | 2.5536 | 2.1678 | 1.9908 | 1.5734 |  |  | 0.75314 | 0.63032 | 0.51008 | 0.30775 | 0.22816
LCOE |  | 8.8249 | 10.3536 | 8.7018 | 8.8059 | 7.81 |  |  | 11.6179 | 10.597 | 8.4796 | 8.303 | 7.2256
Table 2. Key inputs to the LCOE calculation for advanced PC, IGCC, and IGFC power plants
Key Inputs |  |  | Value |  |  | Source
Coal cost |  |  | 1.8 | $/Mmmbtu |  | 1. page 30
PC capital factor |  |  | 0.18599 | $/yr/$ |  | goal seek to give LCOE of 6.33 for no CO2 capture or cost shown on exhibit ES-7, ref 1
Gasification capital factor |  |  | 0.19481 | $/yr/$ |  | goal seek to give LCOE of 7.80 for no CO2 capture or cost shown on exhibit ES-7, ref 1
Fuel cell system cost |  |  | 550 | $/kW AC |  | program goal adjusted to 2007 dollars
Cost for emitted CO2 (w/ capture cases) |  |  | 30 | $/mtCO2 |  | 5. midrange allowance price under McCain/Leiberman (S.280)
Cost for emitted CO2 (no capture cases) |  |  | 30 | $/mtCO2 |  | 5. midrange allowance price under McCain/Leiberman (S.280)
Cost for CO2 transport and injection |  |  | 4 | $/mtCO2 |  | 1. consistent with 4mils/kWh estimate on page 13
Coal CO2 emissions factor |  |  | 95.3 | MMmtCO2/qbtu |  | 6. Table 6-1, coal for electric utility, 25.98 * (44/12)
CO2 compression load for SCPC |  |  | 0.0826 | kWh/kg CO2 |  | 1. case 12, SCPCwCO2, 46,900 kW / 1,252,440 lbCO2/hr *0.454 kg/lb
% of IGCC FO&M for comb turbine |  |  | 10% |  |  | engineering estimate
Fuel cell stack replacement cost |  |  | 175 | $/kW |  | program goal adjusted to 2007 dollars
Stack life |  |  | 5 | years |  | program goal
Discount rate for stack O&M |  |  | 10% |  |  | 1. page 52, exhibit 2-15
Catalytic gasifer, cat. make-up cost |  |  | 30 | cents/mmbtu coal |  | 7.
Table 3. Information sources for LCOE calculation for advanced PC, IGCC, and IGFC power plants
Information Sources
1 | Cost and Performance Baseline for Fossil Energy Plants, August 2007, DOE/NETL-2007/1281
2 | Systems analysis conducted by Noblis
3 | Systems analysis conducted by Eric Grol of NETL
4 | Systems analyses conducted by Dale Keairns of SAIC
5 | Energy Market and Economic Impacts of S. 280, the Climate Stewardship and Innovation Act of 2007,SR/OIAF/2007-04, July 2007
6 | Emissions of Greenhouse Gases in the United States 2002, EIA, Table 6-1
7 | Exxon Catalytic Coal Gasification Process Predevelopment Program. Final Project Report. Exxon Research and Engineering Co., Baytown, TX, FE236924, December 1978
Table 4. Equipment assumption for combustion turbine/fuel cell capital costs
Equipment Included in the Turbine/Fuel Cell Capital Cost Line Item
|  | SPC | GEE IGCC | Adv IGCC | Atm IGFC | Press IGFC
Combustion turbine |  | NA | x | x
Generator |  | NA | x | x
Accessories |  | NA | x | x
Syngas expander |  | NA |  |  | x | x
Fuel cell stack |  | NA |  |  | x | x
Rectifier |  | NA |  |  | x | x
Cathode blower |  | NA |  |  | x
Oxycombustor |  | NA |  |  | x | x
Anodegas expander |  | NA |  |  |  | x
Note on E20: NETLUser: assume red cap cost from increased eff offset by increased matl cost
Note on M20: NETLUser: assume red cap cost from increased eff offset by increased matl cost
Click here to fix/allow circular reference