November 21, 1997

Contract # TW-0928

SPECIAL SPECIFICATION

SECTION 16501-S

FLUORESCENT LUMINAIRES

Page

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK	2

1.02	REFERENCES	2

1.03	DEFINITIONS	3

1.04	SYSTEM DESCRIPTION	4

1.05	SUBMITTALS	4

1.06	DELIVERY, STORAGE, AND HANDLING	6

PART 2 - PRODUCTS

2.01	LUMINAIRES	6

2.02	BALLAST	8

2.03	LAMPS	10

PART 3 - EXECUTION

3.01	INSTALLATION	10

3.02	FIELD QUALITY CONTROL	11

APPENDIX A

A1.01	TABLES	12

SPECIAL SPECIFICATION

SECTION 16501-S

FLUORESCENT LUMINAIRES

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK

A.	Provide materials, equipment, accessories, and workmanship as specified on drawings. Make luminaire parts and components not specifically identified on the drawings, of materials most appropriate to their use or function, and resistant to corrosion and to thermal and mechanical stresses encountered in normal application and function of the luminaires.

B.	Provide luminaires of sizes, types, and ratings indicated, complete with, but not necessarily limited to, housings, lamps, starters and wiring. Provide each luminaire with lamps as specified. Specifications for luminaire components such as reflectors, lenses, lamps and ballasts shall be found elsewhere in this document.

1.02	REFERENCES

A.	Title 10, Code of Federal Regulations, Department of Energy

435	Energy Conservation Voluntary Performance Standards for New Buildings; Mandatory for Federal Buildings.

436	Federal Energy Management Programs.

B.	Illumination Engineering Society (IES) Lighting Handbook, 8th Edition

C.	American National Standards Institute (ANSI)

C78.1	For The Dimensional and Electrical Characteristics of Fluorescent Lamps.

C81.61	For Electrical Lamp Bases.

C81.63	For Gauges for Electrical Lamp Bases and Lampholders.

C82.1	For Ballast for fluorescent Lamps - Specifications.

C82.2	Fluorescent Lamp Ballasts - Methods of Measurement

C82.3	Reference Ballasts for Fluorescent Lamps

D.	National Fire Protection Association (NFPA)

70	National Electrical Code (NEC).

E.	National Energy Policy Act of 1992

F.	Underwriters Laboratories Inc.(UL)

1570	Fluorescent Lighting Fixtures.

935	Fluorescent Lamp Ballasts.

542	Lampholders, Starters, and Starter Holders for Fluorescent Lamps.

G.	National Electrical Manufacturers Association (NEMA)

LE-4	Recessed Luminaires Ceiling Compatibility

H.	MIL-STD-461

Requirements for the Control of Electromagnetic Interference Emissions and Susceptibility.

1.03	DEFINITIONS

A.	Ballast Efficacy Factor (BEF):  ratio of relative light output to power input in watts, at specified test conditions, expressed as a percent.

B.	Ballast Factor (BF):  ratio of a commercial ballast lamp lumens to a reference ballast lamp lumens, used to correct lamp lumen output from rated to actual.

C.	Coefficient of Utilization (CU):  ratio of  lumens from a luminaire calculated as received on the work-plane to the lumens emitted by the luminaires’ lamps.

D.	Color Rendering Index (CRI):  measure of the degree of color shift objects undergo when illuminated by the light source as compared with those same objects when illuminated by a reference source of comparable color temperature.

E.	Correlated Color Temperature (CCT):  absolute temperature of a blackbody whose chromaticity most nearly resembles that of the light source.

F.	Efficacy:  total luminous flux emitted by a lamp divided by the total lamp power input; expressed in lumens per watt.

G.	Efficiency:  lumens emitted by a luminaire divided by the lumens generated by the luminaires’ lamps.

H.	Lamp Current Crest Factor (LCCF):  ratio of peak lamp current to the root mean square (rms) lamp current. Higher LCCF contribute to a reduction in lamp life.

I.	Nationally Recognized Testing Laboratory (NRTL):  laboratory officially recognized by OSHA as having met the requirements stated in Appendix A, 29 CFR 1910.7.

J	Total Harmonic Distortion (THD):  harmonic distortion is the measure of magnitude of current harmonics as compared with the amplitude of the fundamental line frequency. Total Harmonic Distortion is the ration of the root mean square value of all harmonics to the root mean square value of the fundamental.

1.04	SYSTEM DESCRIPTION

A.	Design Requirements:

1.	Contractor shall provide interior luminaires and electrical components listed and labeled by a Nationally Recognized Testing Laboratory (NRTL). Lighting equipment shall comply with UL standards pertaining to interior luminaires including, but not limited to UL 1570 and UL 542.

2.	Contractor shall provide luminaires which comply with applicable requirements of the National Electrical Manufacturers Association (NEMA) LE4 pertaining to recessed luminaires and with NFPA 70, National Electrical Code, as applicable to construction and installation of interior building luminaires.

1.05	SUBMITTALS

A.	Product Data:

1.	Luminaire information shall be submitted where directed in Specification Section 01300-S and on all equipment furnished by the contractor with internal wiring and controls differing from the contract drawings or not shown on the contract drawings.

2.	Unless otherwise stated by SDR, Luminaires or other materials shall not be shipped, stored or installed until submitted shop drawings, samples, catalogue cuts, test data, certificates, or other material has been approved. Luminaire modifications shall be made in accordance with submittal comments.

B.	Shop Drawings:

1.	Shop drawings, samples, test data and certificates shall be submitted for SNL approval in accordance with submittal list and drawings. Submit samples at SNL's request, catalogue cuts, complete photometric data. Submit documentation detailing software or method used to determine all cost, on both fixture calculations and cost feasibility studies for substitutions. In addition, for all orders including substitutions, the following information shall be submitted:

a.	For fixture quantities of 100 luminaires (same type of luminaire) or more: photometrics shall be prepared by a Nationally Recognized Testing Laboratory (NRTL) for the same lamp/ballast combinations as specified per drawings. Photometric data shall be submitted with the specified lamp/ballast combination, at the time manufacturer's cuts are submitted. Photometric testing and reporting shall conform to IES LM - 41 procedures and include:  luminaire catalogue number, lamp type, ballast type, ballast factor, input watts, lumen distribution data, candela readings at 90(, 45(, and 0( to the luminaire and 10( increments for 0( to 180( vertical, candlepower distribution curves, lumen output data and spacing criteria.

1)	Substitutions shall be equal to or better than luminaires specified and include the same lamp lumens (avg. lamp values), color rendering, and be equal to or exceed maximum lamp life. Substituted ballast shall match or exceed BF and BEF of specified ballast. Substitute information shall include manufacture recommended external fuse size.

2)	Costs savings report shall include:  maintenance factor for group re-lamping; A/C cost savings; luminaire heat load contribution and heat cost savings; ballast replacement cost; group re-lamping cost; ballast factor for lamp/ballast combination, ballast efficacy factor, wattage per square foot for total area(s) where luminaire is being installed and projected payback period. Submit NRTL test data for ballasts verifying compliance with requirements for project specific lamp/ballast combinations. Cost analysis shall compare no less than 3 different luminaires and shall support decision for selecting luminaire of choice.

b.	For luminaire quantities less that 100 units:  Manufacturer's photometric data for fixtures specified, including matching lamp/ballast combination, shall be acceptable. Information shall include:

1.	Photometric testing and reporting conforming to IES LM - 41 procedures. Also include, luminaire catalogue number, lamp type, ballast type, ballast factor, input watts, lumen distribution data, candela readings at 90(. 45(. and 0( to the luminaire and 10( increments for 0( to 180( vertical, candlepower distribution curves, lumen output data and spacing criteria. Substitutions shall comply to same requirements as stated in 1.05 B.a.1. & 1.05 B.a.2.

c.	Shop drawings shall indicate materials, finishes, metal gauges, overall and detail dimensions, sizes, electrical and mechanical connections, fasteners, welds, joints, end conditions, and provisions for the work of others. Indicate complete details of luminaire including manufacturers catalogue numbers for sockets, ballasts, light shields, switches and type of wiring, and targeting and locking devices for adjustable luminaires. Standard catalogue cuts shall be supplemented by additional drawings if information or descriptions listed above are not included in the cuts.

d.	Contractor shall submit catalogue cuts of lamps and ballasts provided for each type luminaire.

2.	Submit lamp mortality curves. Curves shall show that less than 10% of lamps fail at 70% of rated life.

C.	Samples:

1.	For luminaire (100 or more for same luminaire), contractor shall submit 2 samples unless otherwise noted. Supply a completely operable luminaire with lamp(s), and 1-6' foot (1.8 m) long cord and plug for standard 120 volt service. For 277 volt luminaires, contractor shall provide 277/120 volt transformers if required by SNL.

a.	Contractor shall tag samples with project name and number, equipment number, and luminaire type. Contractor shall deliver samples to SNL representative for review. SDR shall notify Contractor to transport sample to work site after review has been completed. Transportation costs shall be at Contractor's expense. Contractor shall make luminaires identical with approved samples.

b.	Unapproved samples shall be returned to Contractor at Contractor's expense. Upon receipt of sample disapproval, Contractor shall immediately submit new samples that meet requirements as specified by drawings and /or specifications.

D.	All materials used shall not contain asbestos fibers.

1.06	DELIVERY, STORAGE, AND HANDLING

A.	Packing and Shipping:

1.	Luminaires and their components shall be delivered to job site fully assembled in accordance with approved shop drawings, samples and catalogue cuts.

2.	Exposed finishes shall be protected during manufacture, transport, storage, and handling. Delivered materials shall be identical to approved samples. Damaged materials shall be repaired and / or replaced as directed by SDR.

B.	Acceptance at Site:

1.	SDR has the right to refuse damaged luminaires, their accessories, and materials not approved by SNL submittal process. Costs for removing refused materials and re-supplying approved luminaires will be at Contractor's expense.

C.	Storage and Protection:

1.	Luminaires shall be stored under cover, above ground, in clean, dry areas, and shall be labeled as to type of  fixture, project number, and location to be installed.

2.	Contractor shall be responsible for all costs for transportation of fixtures (i.e., labor, vehicle, packing materials and pallets).

PART 2 - PRODUCTS

2.01	LUMINAIRES

A.	Luminaires shall comply as follows:

1.	Luminaires shall be provided with fluorescent lamps in quantity, type and wattage, and compatible with ballasts, as specified.

2	Contractor shall verify whether luminaires require air-return capability or are to be static.

3.	When specified, fluorescent luminaires shall have electromagnetic interference filters. Filters shall either be integral or external to the ballast, but must be integral to luminaire assemble. Provide one filter per ballast that suppress electromagnetic interference as required by MIL-STD-461.

4.	Luminaires shall meet applicable UL 1570 requirements. The appropriate UL label or listing, or NRTL label or listing, will be acceptable as evidence of compliance with UL 1570. Luminaires shall also comply with applicable National Electrical Code provisions, with energy efficiency requirements mandated by 10 CFR 435 and 436, including requirements mandated in the National Energy Policy Act of 1992.

5.	Luminaires shall be fully assembled when shipped from the factory.

6.	Plainly mark all luminaires for operation of specified lamps and ballasts and according to proper lamp type in accordance with UL Publication 1570 entitled "Standard for Safety - Fluorescent Lighting Fixtures". The following lamp characteristics should be noted:

a.	Lamp diameter code (T-8, T-10, T-12), with nominal lamp wattage.

b.	Start type (rapid start, instant start),

c.	Correlated color temperature (CCT) and color rendering index (CRI).

7.	Unless otherwise noted, use only completely concealed hardware. Latching on luminaire door frames shall be unobtrusive. Make luminaire free from light leaks by the inherent design of the body and frame. Bond gaskets, when used, to the luminaire metal. Use bottom re-lamping unless otherwise noted.

8.	Luminaire wiring:

a.	Provide wiring between fluorescent lampholders and associated operating and starting equipment in compliance with UL 1570 and NEC.

9.	Lampholders:

a.	Provide fluorescent luminaire lampholders that are white, constructed of heat resistant plastic. Lampholders shall comply with UL 542 and ANSI C81.

b.	Provide lampholders suitable for specified lamps, and position lamps in optically correct spacing and relationship to lenses, reflectors, filters, and baffles.

10.	Finishes:

a.	Provide reflective surfaces with a white baked enamel finish with a minimum reflectance of 86%.

11.	Lenses/ Louvers/ Trim:

a.	All lenses and louvers shall be held positively within door frames so hinging or motion of frame will not cause diffusing element to drop out. Trim shall be drawn to ceiling as tight as necessary, insuring complete contact of trim with ceiling surrounding luminaire.

b.	Unless otherwise specified, prismatic lenses shall be made of: clear virgin acrylic of nominal 0.125" (.32 cm) overall thickness for nominal 2' x 4' (60.96 cm x 121.92 cm) pieces; lens shall be composed of .1875"(.48 cm)  square female prismatic cones with non-convex prism faces of maximum 0.080" (20.32 cm) depth and aligned to 45( to length and width of lens panel; lens shall be a minimum of 7.5 oz. per square foot (.23 grams per square centimeter); shall be strain-free and uniform in appearance; shall have minimum of 80% visible transmittance.

12.	Reflectors:

a.	Aluminum reflectors and shielding media shall have a minimum thickness in accordance with current UL standard 1570 for ballast covers. Reflectors shall be absolutely free of tooling marks, spinning lines, and indentation marks caused by riveting or other assembly techniques. No rivets, springs or other hardware shall be visible after installation.

b.	Reflectors shall be free from blemishes, scratches, or indentations which would distort their reflective function.

c.	Any aluminum reflector, cone, or baffle, utilized in whole or in part, within bottom two inches of luminaries, shall have low iridescent coating to reduce rainbow effect from tri-phosphor lamps.

d.	Specular silver reflectors shall be comprised of unitized single piece construction for permanent mounting inside luminaire. A multi-piece reflector assembly shall only be considered if parts maintain fixed and accurate positioning in relation to lamps and housing, installation costs are not increased, and ballast access and luminaire maintenance is not compromised. Use a minimum reflector thickness of 0.020 inch (.05 cm) consisting of silver film laminated on aluminum or steel substrate. or high performance aluminum finish or multiple thin film coating. Material shall retain a minimum 93% specular reflectivity, 96% image clarity, and 95% total reflectivity for a minimum of 5 years, when cleaned as directed.

2.02	BALLAST

A.	Ballast for fluorescent fixture shall be "NRTL listed" comply with Safety Standard UL 935, "CBM" labeled and certified to meet ANSI 82.1 (electronic ballasts are not "CBM" labeled and excluded from requiring a CBM label).

B.	Ballast shall be rated as "high power factor" and shall be "Class P" with thermostatic (automatic resetting) type internal protection.

C.	Ballast for fluorescent luminaire shall be sound rated by the manufacturer and shall have a rating of "A" (20 - 24 db).

D.	Ballast rated for low temperature starting (temperatures around -20°F or  -29( C) shall be provided in fixtures mounted in cold rooms, unheated buildings, outdoors, or as indicated on drawings.

E.	Ballast mounted in fixed or permanently installed fluorescent fixtures shall be provided with an externally removable fuse holder and fuse in the input power line.

1.	The fuse holder shall be a BUSS type HLR, installed in the ballast compartment, such that the conductors are not exposed in lamp compartment or externally.

2.	Fuse shall be glass tube, dual element, time-delay type (Bussman "Fusetron" type GMF or equal).

3.	Fuse holder shall be mounted so that it can be removed either from outside fixture enclosure at fixture end or from inside the lamp compartment, without opening ballast compartment.

4.	Fuse size shall be  specified by manufacturer.

F.	Ballast shall be marked showing compatibility with Energy Saving Lamps.

G.	Ballast shall meet minimum efficiency and efficacy factors as specified in Appendix A.

H.	Ballast shall not contain polychlorinated biphenyl (PCBs).

I.	Total Line Current Harmonic Distortion shall not exceed 20%.

J.	Energy Savings Ballast shall also comply to the following:

1.	Energy saving ballast designed for F40/T-12/RS lamps shall be compatible  for use with both 40 watt and 34 watt lamps.

2.	Light output BF shall be no less than 0.95 when tested with 40 watt lamps and no less than 0.875 when tested with 34 watt lamps.

3.	Ballast(s) shall have an electronic component which cuts off power to lamp filaments of a rapid start lamp(s), once lamp(s) have started.

4.	Cathode voltage for rapid start lamps during starting shall be between 3.4 and 4.5v across a dummy load and between, 2.5 and 4.0v during operation as per ANSI C82.

5.	LCCF shall not exceed 1.7 when tested with 40 watt T-12 lamps, nor exceed 1.9 for 34 watt lamps, as per ANSI C82.1.

6.	Dimming ballast shall only be used on a dimming circuit designed expressly for cathode cut-out type ballast and shall not reduce lamp life.

K.	Electronic ballast shall also comply with the following:

1.	Ballast shall be specifically designed for the operation of lamps being installed in luminaire.

2.	Light output (BF) shall be between .85 and 1.0 when tested with a compatible full-wattage lamp (40W T-12 or 32W T-8).

3.	Ballast shall maintain light output (regulation of light output during lamp's average life span) so lumen output does not vary more than ± 5% for all 4-foot rapid start fluorescent lamps, in the proper lamp/ballast combination, within operating ranges of ± 10% of center voltage. (E.g.: 120V or 277V).

4.	Cathode voltage for rapid start lamps during starting shall be between 3.4 and 4.5V during operation per ANSI C82.1.

5.	Ballast shall have a frequency of operation of 20 kHz or greater and incorporate adequate 60 Hz filtering in order to operate with less than 5% flicker (maximum 0.20 Flicker Index) with any tri-phosphor lamp suitable for use with ballast.

6.	LCCF shall not exceed 1.7 when tested with 40W T-12 or T-8 lamps.

7.	Total Line Current Harmonic Distortion shall not exceed 15%.

L.	Dimmable Electronic Ballast shall also comply with:

1.	Ballast shall be high frequency, solid state type for adjustable light output control of fluorescent lamps.

2.	Ballast shall dim continuously from 100% to at least 20% of full light output without strobe effect or lamp flicker.

3.	BF shall not be less than .89 (± .025) at 100% output and not less than 0.15 when dimmed to 20% power (tested with 40W T-12 lamp).

4.	Total Line Current Harmonic Distortion  shall not exceed 20% throughout the dimming range.

5.	LCCF shall not exceed 1.7 throughout the dimming range.

6.	Ballast shall maintain full lamp filament heat during dimming or normal operation of lamps and capable of operating lamps at full output if dimming components fail.

2.03	LAMPS

A.	Lamps provided shall conform to ANSI C78.1.

B.	Unless otherwise specified, lamp phosphors shall be a composition which includes tri-stimulus or modified tri-stimulus rare earth phosphors, or contain phosphors allowing the lamp to render ] a CRI of not less than 69.

PART 3 - EXECUTION

3.01	INSTALLATION

A.	Install luminaires complete with lamps, parts, attachments, devices, hardware, hangers, cables, supports, channels, frames, brackets, fuse and fuse holder, and internal and external wiring as specified by drawings.

B.	Coordinate installation of luminaires with other trades to insure installations do not interfere with other work.

C.	Install luminaires plumb, square, and level with ceiling and walls, and in alignment with adjacent lighting fixtures. Unless otherwise specified, recessed luminaires flush mounting in ceiling grid shall secured in place using "Caddy Acoustical Tee Bar Clip" (Cat. No. 515) or similar.

D.	Luminaires weighing less than 56 lbs. shall have, in addition to the requirements outlined above, two No. 12 gage hangers connected from the fixture housing to the structure above as a seismic restraint.  These wires may be slack.  Luminaires weighing 56 lbs. or more shall be supported directly from the structure above by approved hangers.

ED.	Install luminaires, complete with lamps, with protective wrapping (plastic protective cover on parabolic insert or acrylic lens) in place.

FE.	Ground non-current carrying parts of electrical equipment in accordance with UL and NEC requirements. This includes bonding green wire to luminaire.

GF.	Conduit shall not be fastened to Tee Bar support hangers, but be supported by building steel, unistrut, or some channel installed for the specific purpose of supporting conduit.

HG.	New lamps shall be provided for each fluorescent fixture installed. Lamps shall be free of dirt and fingerprints.

3.02	FIELD QUALITY CONTROL

A.	Upon completion of installation of lighting fixtures, and after circuits have been energized, apply power and demonstrate capability and compliance with requirements. Correct or remove and replace malfunctioning units, then re-test to demonstrate compliance. Coordinate field tests with SDR.

1.	Lamps shall be fully operable, no burnt-out lamps. Burnt-out lamps shall be replaced by Contractor at Contractor's expense.

2.	When directed by SDR, remove any protective covering from luminaires. Clean all dirt, fingerprints and debris from lens, parabolic insert, lamps and lamp compartment.

END OF SECTION

APPENDIX A

A1.01	TABLES

A.	National Energy Conservation Standard for Fluorescent Lamp Ballasts table:

Application (lamps)

Ballast

Input Voltage

Total Nominal

Lamp Watts

Ballast

| Efficacy Factor (%) |
| --- |
|  | (1) F40T12 | 120 | 40 | 1.805 |
| (1) F40T12 | 277 | 40 | 1.805 |
| (2) F40T12 | 120 | 80 | 1.060 |
| (2) F40T12 | 277 | 80 | 1.050 |
| (2) F96T12 | 120 | 150 | 0.570 |
| (2) F96T12 | 277 | 150 | 0.570 |
| (2) F96T12/HO | 120 | 220 | 0.390 |
| (2) F96T12/HO | 277 | 220 | 0.390 |

B.	Exceptions:

1.	Dimming ballasts designed to operate at 0°F (-17(C) or less are exempted from these standards.

C.	Ballast Factor (BF):

1.	BF must meet or exceed the following:

a.	40 Watt or slim line must be 92.5% or greater.

b.	High Output lamps must be 95% or greater.

2.	BF must be determined by laboratory testing, not by calculations.

APPENDIX A

D.	Minimum Efficiency Standards table:

Lamp

Type

Nominal

Lamp Wattage

Minimum

CRI

Avg. Lamp

| Efficacy (LPW)* |
| --- |
|  | F40 | >35W | 69 | 75 |
| F40 | (35W | 45 | 75 |
| F40/U | >35W | 69 | 68 |
| F40/U | (35W | 45 | 64 |
| F96T12 | >65W | 69 | 80 |
| F96T12 | (65W | 45 | 80 |
| F96T12 | >100W | 69 | 80 |
| F96T12 | (100W | 45 | 80 |

*	Lumen per Watt Efficiencies

E.	Fluorescent lamps impacted by minimum efficiencies standards are:

1.	F40 bi-pin rapid-start straight lamps and U-shaped rated at 28 watts or more.

2.	F96/HO, high output lamps, 96 inches (2.44 m) in length, rapid start, 800 ma. types.

3.	F96, slim line 96 inches (2.44 m) in length, instant start, single pin of 52 watts or more.