# WBS SCOPE DESCRIPTION:

This scope of this Work Package (WP) includes the following work activities required to remove the BGRR bioshield:

- Construction of a contamination control enclosure and HEPA ventilation system and installation of material handling equipment.

- Isolation of utilities required for bioshield removal.

- Removal of interferences necessary for bioshield removal.

- Removal of the east and west sides of the air tight membrane (ATM), graphite restraining springs, and the experimental port expansion joints.

- Removal of the steel and concrete bioshield structure down to elevation 110’-0”.

- Removal of the pile 3” steel upper bedplate & sliding rails.

- Construction of a reinforced concrete cover over the opening on elevation 110’-0” where the bioshield was removed.

- Packaging and onsite transportation of waste to an interim staging area for offsite transportation and disposal.

- Performance of an as-left radiological survey of Building 701.

# Discussion

Removal of the bioshield will commence upon completion of preparatory work that is covered in WP 321. The following activities will be performed under this WP to complete the bioshield removal:

Contamination Control Envelope and HEPA Ventilation System

A contamination control enclosure will be constructed around the bioshield to support handling and packaging of removed bioshield sections and debris. This enclosure will be maintained at a negative pressure with respect to Building 701. Four (4), 6000-cfm HEPA fan units will be used to maintain the contamination control envelope at a negative pressure. Two (2) 6000-cfm HEPA fan units utilized during the BGD Filter and Liner Removal will be used in addition to two (2) newly purchased units. The HEPA fan units will discharge to the outside environment through a continuously monitored stack that will be constructed in accordance with BSA SBMS requirements.

Removal of the bioshield requires that structures and appurtenances that present a physical interference with the removal process first be removed, including utilities such as electrical and water lines. Additionally, the temporary HEPA ventilation system will be supplemented with portable HEPA ventilation units to provide airborne contamination control; provisions for four additional portable units are included in this work package. The following work activities will be performed in this Work Package:

Utility Isolation and Removal

All electrical conduits, service air system piping and components, and domestic water piping and components on the exterior surfaces of the bioshield will be removed.

Removal of Interferences

Balconies attached to the exterior surfaces of the bioshield will be removed. These balconies consist of steel framing, 4.5 inch poured concrete floor covered with ½ inch asphalt sealant, and floor tile (ACM).    The ACM floor tiles will be removed prior to demolition of the structures. The balconies are listed as follows:

- East – el. 114 ft

- East – el. 123 ft (partial)

- North – el. 118 ft

- North – el. 136 ft

- West – el. 118 ft

- West – el. 127 ft

- West – el. 136 ft

- Blue Room

- Sixteen (16) control rod drive mechanisms (CRDM) will be partially removed as necessary to allow access for bioshield removal. These mechanisms consist of structural steel framing and motor/drive skids mounted in two banks.  Each drive skid consists of an electric motor, drive unit (gear box), steel extension rod and lead shielded graphite sleeve. The lead and graphite was removed as part of an earlier remediation work package for Building 701.

Note: The CRDMs and associated hardware may be PCB contaminated as a result of historical hydraulic system leakage.

- The freight elevator adjacent to the bioshield will be removed. The elevator consists of a tower constructed of brick and steel, a conveyor car, steel lift cables and cast iron counter weights.

- The Chemo-Nuclear experimental loop will be partially removed and structurally supported prior to separation of system components integral to the biological shield.

Removal of Air Tight Membrane (ATM), Pile Restraining Springs, and Experimental Port Expansion Joints

During the removal of the graphite pile (WP 304), only the top portion of the ATM was removed to access the graphite blocks. This WP will remove the remaining east and west sides of the aluminum and steel ATM. The experimental port expansion joints and graphite restraining springs that span the space between the ATM and the bioshield will also be removed.

Bioshield Removal

The bioshield structure will be removed. The bioshield is comprised of a 4’ - 3” thick high-density concrete barrier surrounded by an inner and outer steel plate with a nominal thickness of 6” and 3”, respectively. The bioshield structure will be removed in its entirety down to elevation 110’-0”. The following work activities will be performed to remove the bioshield:

- Removal of the top plates.

- Removal of the neutron shield.

- Removal of the inner and outer steel plates that surround the concrete, including their size reduction for packaging, transportation and disposal.

- Removal of the reinforced concrete inside of the bioshield walls, including its size reduction for packaging, transportation and disposal.

- Removal of the pile upper bedplates and sliding rails.

- Removal and/or stabilization of loose radiological contamination in the Building 701 area associated with the removal of the bioshield – includes the remaining pile support structure within the bioshield footprint.

- Installation of a concrete enclosure of the biological shield footprint

- Perform an as-left radiological survey of the areas within Building 701 affected by the removal of the bioshield.

Removal of Loose Contamination and As-left Radiological Survey

Loose contamination, including miscellaneous contaminated objects that may have fallen on the pile bedplates will be removed and placed in the appropriate waste container. After completion of all work inside the bioshield cavity, a radiological survey will be performed to document the as-left condition.

Subcontractor Demobilization

Following biosheild removal, all temporary facilities and equipment will be dismantled, packaged and transported to the Waste Loading Area (WLA).

Waste Packaging and Onsite Transportation

The bioshield waste will be packaged in intermodal containers and removed from the BGRR facility and transported to the BNL WLA for interim staging. Onsite storage and offsite transportation are addressed in WP 323.

COMPLETION CRITERIA:

- Electrical isolations and interference removal necessary to remove the bioshield have been completed.

- The air tight membrane, restraining springs, and experimental port expansion joints have been removed.

- The bioshield has been removed in its entirety down to elevation 110’-0”.

- The pile support upper bedplates & sliding rails have been removed.

- A permanent reinforced concrete cover has been constructed on elevation 110’-0” over the opening where the bioshield was removed.

- The bioshield and associated secondary waste has been packaged, staged in the WLA, and ready for transportation to an approved disposal site.

- Loose radiological contamination in the Building 701 area associated with the removal of the bioshield has been removed and/or stabilized.

- All temporary equipment installed to remove the bioshield has been removed.

- An as-left radiological survey of the areas within Building 701 affected by the removal of the bioshield has been completed.

- A letter report certifying that the work activities required by this Work Package has been submitted to the Brookhaven Site Office.

ASSUMPTIONS, EXCLUSIONS, AND QUALIFICATIONS:

- Procedures, engineering, plans, training and special tooling for bioshield removal have been completed in Work Package 321.

- 15-inch support I-beams and lower bedplates will not be removed.

- Class A waste disposed of at Envirocare of Utah

- Schedule is based on a five-day 50-hour workweek.

- All waste will be shipped by rail.

- A packaging efficiency of fifty per cent (50%) is assumed for concrete and thirty five percent (35%) for interference materials. No bulking factor was assumed for segmented bioshield steel plates. Miscellaneous secondary waste (DAW) is estimated at 200 cubic yards from all work activities.

- Off-site transportation and disposal of bioshield waste is covered in Work Package 323.

- Post Removal Restoration of the BGRR facility is covered in Work Package 324.

BASIS OF ESTIMATE:

A bottoms-up estimate was prepared for the installation of temporary facilities and equipment, bioshield interferences and bioshield removal. Vendor estimates for materials, equipment and production rates were included in the estimate.

# ACQUISITION STRATEGY/ASSUMPTION:

BSA plans to award the biological shield contract as a DOE IDIQ contract. BSA and BSA BOA subcontractors will furnish all other project support personnel and resources.

WASTE DISPOSAL QUANTITIES:  (Provide quantities in cubic yards)

| Type of Material | Waste Type | Quantity | Planned Disposal Site |
| --- | --- | --- | --- |
| Graphite Debris | LLRW (NTS) | 5.0 yd3 | Nevada Test Site |
| Metal Structural Materials | LLRW (oversized debris) | 233 yd3 | Envirocare, Clive, UT |
| Metal / Metal Plate / Secondary Wastes | LLRW (standard debris) | 3470 yd3 | Envirocare, Clive, UT |
| Hazardous Materials (PCB contaminated components) | Hazardous | 3.5 yd3 | Onyx |
| Cadmium and Lead Coated Steel | Mixed Waste | 5.9 yd3 | Envirocare, Clive, UT |

SIGNIFICANT RISKS AND PROPOSED MITIGATION ACTIONS:

Significant WP 322 risks and proposed mitigation actions are as follows:

# Risk 322-1:  Production Rate Variability

Biological shield removal is a unique, one-of-a-kind project. The adaptation and deployment of removal technology, coupled with unforeseeable conditions inside of the bioshield can lead to considerable variability in actual production (i.e. removal) rates from those considered in the development of WP 322.  Production rate variances can result in considerable cost and schedule impacts.

Mitigation Actions

BSA is using a highly disciplined and methodical approach to biological shield removal. The design and qualification of special tools will be accomplished under rigorous requirements to ensure that the assumed production rates are achieved during the project.  The qualification of special tools and training of field personnel will use mock-ups to provide further that the assumed production rates are met.  Where required, tooling re-design and rework will be required before special tools are approved for use in the field. BSA will build hold points into the schedule to allow for process and equipment enhancements and acceleration of the project learning curve. Notwithstanding these mitigation actions, this remains a risk that can result in significant cost and schedule variances.

# Risk 322-2:  Bioshield Material Requiring Special Handling

BSA has assumed that all waste generated during the removal of the biological shield will not require shielded containers because of elevated radiation dose rates.  A significant increase in the anticipated dose rates will require shielded containers to meet Department of Transportation (DOT) resulting in significant cost and schedule impacts.

Mitigation Actions

BSA is modeling container dose rates on a conservative basis and the resulting dose rates will be factored into detailed work planning.  BSA’s use of a conservative approach to waste management planning, including procedure development and equipment availability, will provide additional assurance that the Baseline cost plan and schedule are achieved.

# Risk 322-3:  Generation of TRU Waste

It is not expected that bioshield removal will result in the generation of TRU waste.  However, unforeseeable waste articles located in bioshield crevices could result in unplanned TRU waste. This is an extremely low-probability risk.

Mitigation Actions

The Mitigation Actions included in WP 304 are sufficient to address this low-probability risk.

# Risk 322-4:  Project Impacts Attributable to Building 701 Contamination

Biological shield removal involves the removal of approximately 5000 tons of contaminated material from the BGRR bioshield.  Biological shield removal could result in the potential spread of contamination to areas outside of the bioshield.  This could potentially result in work stoppage and disruptions to the project schedule, and costly actions to decontaminate the affected areas of the BGRR.

Mitigation Actions

BSA has designed a rigorous contamination control strategy into its biological shield removal plan.  This strategy includes engineered controls, special tooling, design requirements, subcontract performance warranties and extensive field monitoring plans.  These actions should serve to reduce the risk of serious contamination control events that could result in significant project impacts.

Risk 322-5:  Biological Shield Removal Impact Due to Waste Disposal Pathway Disruption

Biological shield removal will result in the generation of more than 200 containers of waste.  Disruptions to the waste disposal pathway could result in cost and schedule impacts to biological shield removal, particularly if the disruptions cause accumulation of project waste beyond the interim storage capacity that exists at BNL. Such disruptions are potentially the result of unforeseeable transportation issues and events, or similar issues and events at the planned disposal sites.

Mitigation Actions

Rigorous planning, controls and disciplined project execution are key to reducing the risks of unforeseeable disruptions to the planned waste disposal pathways.  BSA will include resources for extensive and intrusive oversight of waste packaging, transportation and disposal operations. Lessons learned from across the DOE complex will be continuously evaluated for application at BNL. Effective community outreach and involvement is vital to reducing risks of many disruptions potentially initiated by external parties, and BSA will work with the DOE in developing and implementing the appropriate plans, accordingly.  As a planning step, BSA will carefully evaluate capacity of interim storage at BNL with the objective of mitigating the potential impacts of a large spectrum of waste disposal pathway disruptions.  BSA’s waste management plans, to the extent practical, will provide for alternative pathways and work-arounds under a defense-in-depth strategy.  These actions should serve to reduce many of the risks and associated consequences of disruptions to the waste disposal pathway that could impact biological shield removal.

# Risk 322-6:  Unforeseeable Radiation Dose Rates

By design, BSA is planning for biological shield removal using remotely operated tools and equipment.  BSA is approaching the project with the objective of minimizing hands-on manual work.  However, some level of hands-on activity will be required.  Radiation dose rates significantly in excess of those considered during project planning could potentially impact biological shield removal cost and schedule.

Mitigation Actions

BSA and its subcontractors will include conservative levels of margin in developing project plans.  Opportunities to reduce the extent of required hands-on work will be taken throughout all stages of project development and execution.  Subsequent to graphite pile removal, BSA will acquire actual dose rates on the radiologically affected areas. A detailed ALARA plan that will challenge all work activities to minimize personnel radiation exposure will be developed.

REFERENCES:

Project References

Inter-Agency Agreement DOE Order 413.3 Burns and Roe Engineering Studies – February 2003 Final Record of Decision (ROD) for Area of Concern 9, Brookhaven Graphite Research Reactor (BGRR) – January 2005

ATTACHMENTS:

- Cost Plan

- Schedule

- Supporting Documentation