## INSTRUCTIONS
Benchmarking the Cost-effectiveness of Commercial Buildings Commissioning & Retro-commissioning
Lawrence Berkeley National Laboratory
Version: February 2, 2009
For defintiions of commisisoning and retro-commissioning, plus useful resources, see: http://www.cacx.org/
This workbook provides a data-collection and analysis instrument used in the ongoing LBNL compilation of real-world documentation of the costs and cost-effectiveness of commercial buildings commissioning. Contributors receive a personalized analysis of their projects in comparison to the experience of other buildings in our database.
Address comments/questions to Evan Mills, 510-486-6784 or emills@lbl.gov
Before proceeding, download latest version of spreadsheet from: http://eetd.lbl.gov/ea/mills/Cx/LBNL-Cx-CostBenefit.xls
It is not expected that all data will be available for all projects. Enter data only in color-shaded cells (other cells will be calculated or should not otherwise be altered). Required rows are indicated by bold red font. There is no required data on the Measures tab.
1. THIS WORKBOOK
This workbook has seven tabs (aside from this one), as described below. There are only two tabs in which to enter data, and the rest are informational: 1. The "Main Data Sheet" (the primary data base) and "Measures" (details on measures, if available). The other tabs provide definitions and background information. As your worksheet will ultimately be merged into LBNL's master, do not alter the structure (except as noted below), I.e. do not insert/delete rows or columns or change labels. PLEASE enter information in the exact units shown; adding extraneous information will hamper our efforts to tabulate and otherwise analyze the results. Use Excel's "Comments" feature or the final row to attach clarifying information, notes, or questions.
"MAIN DATA SHEET" Tab
The design is intended to collect the results in a single column ("record") per project. Do not insert or delete rows; do not modify row labels. Where data are available at a finer level of detail (by measure), complete a table on the "Measures" tab, with one row per measure (including associated energy savings, where available).
"Measures" Tab
This template is to be completed to achieve a mapping of problems ("deficiencies") and the recommended solutions ("measures"). Where measure-level cost and energy savings data are available, it should be included. Problems and measures should be listed, irrespective of whether the measures are known to have been implemented. However, include energy savings and implementation cost estimates only for recommended measures known to have been implemented. If the effort required to provide a complete listing of findings is prohibitive, give priority to those with significant energy implications and good cost-effectiveness. Alternatively, all measures may be aggregated into one row. if measure-specific information is not known. Rejected measures may be tabulated on the indicated row.
"Measures Key" Tab
This tab contains definitions of the terms and categories appearing in the Measures Tab.
"Building Type Key" Tab
This tab contains definitions of the building type choices appearing in the Main Data Sheet Tab.
"M&V Key" Tab
This tab includes screen-captures of the IPMVP criteria A-D, used to answer one of the questions in the Main Data Sheet. If savings are determined strictly with engineering calculations, denote method as "E".
"Cost Rules" Tab
Guidelines for inclusion of costs associated with commissioning.
"Non-Energy Impacts" Tab
Examples of the types of non-energy impacts (positive and negative) to consider and attempt to quantify
2. CONFIDENTIALITY
Please include the building name in the data tables. Two rows are provided: one if the building name can be associated with the published data, the other if the building name should not be associated with the published data. It will be the data provider's responsibility to flag any other info that must be kept confidential, but our expectation is that only the building name will be sensitive.
3. ENERGY DATA
It is critical that the pre-/post-commissioning data be free from any influence of non-commissioning retrofits or building modifications. Acceptable data can be in the form of engineering estimates or measured and weather-normalized values, at a whole-building level (not just for the end-use being commissioned). If measured, data are to be characterized according to level of quality per IPMVP (Method A-D). The method underlying energy data reported on the Main Data Sheet should correspond to the M&V method indicated. Use "E" if savings are purely based on engineering estimates. As savings often do not manifest fully in the first year, use year-2 or -3 data if available. Include savings only for measures known to have been implemented. Preferably, enter separate energy use values for electricity, fuel, metered thermal, etc.
4. COST DATA: Definitions [see "Cost Rules" tab for more information]
Include all fixed costs incurred as a part of the commissioning process, no matter what issues were found during commissioning. Some examples of fixed costs include design review, writing and performing verification checks, and writing and performing functional tests.
Capital costs associated with correcting deficiencies identified in new-construction commissioning should be paid for under warranty (not by the commissioning agent) and thus not tabulated here, whereas those identified in existing buildings are generally attributable to the commissioning process. Major energy-efficiency upgrades which go beyond the correction of a deficiency should be considered "retrofit" costs rather than commissioning costs, and not tabulated here.
Include any and all utility rebates or other financial incentives paid by third parties. The Main Data Sheet lets you enter the rebate amount on a separate line, but allocate the amount to the itemized costs as well on a proportionate basis in the Itemized Measures List
Commissioning Study Costs. This is part of the total cost (in addition to implementation). Wherever total costs are shown, these costs must be included. Wherever implementation costs are itemized, these costs do not need to be included (given the difficulties in allocating these costs to specific recommendations).
Do not include Testing and Balancing (TAB) costs. This is not part of what we define as commissioning or retro-commissioning.

## MAIN DATA SHEET
ov
Version: February 2, 2009 | NAVIGATION
Download current version of this workbook before starting: http://eetd.lbl.gov/ea/mills/Cx/LBNL-Cx-CostBenefit.xls Return to Evan Mills, Lawrence Berkeley National Lab, emills@lbl.gov | Project Description | Reasons for Commissioning | Deficiencies & Measures | Cost Data | Baseline Energy Use & Savings | Non-Energy Impacts
INSTRUCTIONS:
1. Download latest version of spreadsheet from: http://eetd.lbl.gov/ea/mills/Cx/LBNL-Cx-CostBenefit.xls
2. Complete yellow-shaded cells - one column per project, starting in Column D. Skip hidden rows.
3. At a minimum, answer the required questions (name and cell outline in red).
4. Important: If a value is zero enter "0" rather than leaving the cell blank. If unknown, write "unknown". If not applicable, write "not applicable"
Note: we use the short-hand term "(retro-)commissioning" to denote either retro-commissioning of existing buildings or commissioning of new buildings.
Questions? Contact Evan Mills at emills@lbl.gov or 510-486-6784
| Format or Units | Notes | Project 1 | Project 2 | Project 3 | etc....
PROJECT DESCRIPTION | [back to top]
Name of person completing this entry | Text
Contact information for person completing this entry: Phone | Text
Contact information for person completing this entry: E-mail | Text
Project Type: Existing building (RCx) or New construction (Cx) | Cx; RCx
Case identifier | PECI-#, TAMU-#, LBNL-#, etc. | For internal tracking
(Retro-)commissioning provider | Name
Person leading the (retro-)commissioning process | Text | Name
(Retro-)commissioning project leader's level of experience | Number of projects previously completed (number only; no text) | Applies to project leader, not firm. Do not include general "energy efficiency experience"
Was the building previously (retro-)commissioned? | Y(es); N(o); U(nknown)
Was this building known to have problems before it was (retro-)commissioned? | Y(es); N(o); U(nknown)
Awards/certifications received after (retro-)commissioning | LEED, Energy Star, CASBEE, EPBD, Green Globes, Other (specify)
Building name and street address (if PUBLIC INFORMATION) | Text | Name will be included in final report, i.e. associated with data in the final report
Building name and street address (if CONFIDENTIAL) | Text | Name will be kept confidential, i.e. not associated with data in the final report
Location - City | Text
Project Location - State | Postal Abbreviation
Project Location - Country | Text
If country other than the US, indicate currency type | Text [3-letter code] | Use same currency throughout this form
Building ownership | Public; Private
Level of (retro-)commissioning | Comprehensive, Specific Systems | E.g. if only the energy-efficiency measures were commissioned, answer would be "SE"
Number of buildings (retro-)commissioned | Number | When unknown, enter "1"
Year original construction completed | Year (NNNN) | Use four-digit format
Total building construction cost (only needed if new building) [$, or other currency] | amount in year built
Year (retro-)commissioning project completed | NNNN | Use four-digit format
Year that (retro-)commissioning costs reported below were incurred [NNNN] | NNNN | If multi-year project, list mid-point
Floor Area:
Entire building | square feet
Floor area served by (retro-)commissioned systems | square feet
If other floor area units, indicate here: | list unit used
Net or Gross; Parking areas | N(p); G(p) | Include "(p)" in code if data include parking/garage spaces. Preferably, exclude parking areas.
Main building type (if more than one, list dominant use in terms of contribution to total energy consumption). See "Building Type Key" for definitions. Apportion total floor area to the appropriate categories below. Sum must add to total. | Bldg type(s): O=office HO=hlthcr-outpatient HI=hlthcr-inpatient HE=higher edu K12=edu K-12 W=warehouse POS=public order and safety L=laboratory | LOD=lodging R=retail PA=public assembly FS=food service FSA=food sales RW=religious worship DC=datacenter CR=cleanroom OTH=other
Notes and/or uses if mixed use
Education
K-12 | " | "
Higher education | " | "
Food Sales | " | "
Food Service | " | "
Health Care
Inpatient | " | "
Outpatient | " | "
High-tech Facilities
Cleanrooms
Data Center
Laboratory | " | "
Lodging | " | "
Mercantile
Retail | " | "
Service | " | "
Office | " | "
Public Assembly | " | "
Public Order and Safety | " | "
Religious Worship | " | "
Warehouse and Storage | " | "
Other | " | "
Vacant | " | "
Laboratory Characteristics (if applicable)
% of floor area in labs
Number of fume hoods | Number
% outside air | floor area served by outside air
REASONS FOR (RETRO-)COMMISSIONING | [back to top] | Place an "x" by the appropriate answer(s)
Ensure system performance (energy and non-energy-related systems) |  | "
Obtain energy savings |  | "
Ensure or improve thermal comfort |  | "
Extended equipment life |  | "
Train and increase awareness of building operators or occupants |  | "
Smoother process and turnover (new construction) |  | "
Increase occupant productivity |  | "
Ensure adequate indoor air quality |  | "
Comply with LEED or other sustainability rating system |  | "
Reduce liability |  | "
Qualify for rebate, financing, or other services |  | "
Research/demonstration/pilot |  | "
Participation in utility program |  | "
Other |  | "
DEFICIENCIES & MEASURES | [back to top] | If information is available, complete separate "Measures" worksheet first. Definitions available on "Measures" Tab.
Number of Problems (deficiencies) Identified, by Component: | Count should agree with that in the "Measures" worksheet for the items that apply.
HVAC (combined heating and cooling) | Number | "
Cooling plant | Number | "
Heating plant | Number | "
Air handling & distribution | Number | "
Terminal units | Number | "
Lighting | Number | "
Envelope | Number | "
Plug loads | Number | "
Facility-wide (e.g. controls, EMCS, or utility related) | Number | "
Other | Number | "
Unknown | Number | "
Number of Measures Recommended To Resolve Problems: |  | Includes accepted as well as rejected measures.
DESIGN, INSTALLATION, RETROFIT, REPLACEMENT
Design change | Number | "
Installation modifications | Number | "
Retrofit/equipment replacement | Number | "
Other | Number | "
OPERATIONS & CONTROL
Implement advanced reset | Number | "
Start/Stop (environmentally determined) | Number | "
Scheduling (occupancy determined) | Number | "
Modify setpoint | Number | "
Equipment staging | Number | "
Modify sequence of operations | Number | "
Loop tuning | Number | "
Behavior modification/manual changes to operations | Number | "
Other | Number | "
MAINTENANCE
Calibration | Number | "
Mechanical fix | Number | "
Heat transfer maintenance | Number | "
Filtration maintenance | Number | "
Other | Number | "
UNKNOWN | Number | "
Diagnostics and Automation Techniques | Text | List tools/methods used, e.g. WBD, ACRX, PacRat, Enforma
Verification of Measure Installation | Yes-all; Yes-some; No; Unknown | Subsequent cost and savings data entered should exclude that for recommended measures known to have been rejected.
(RETRO-)COMMISSIONING COST DATA - [See "Cost Rules" tab for costs to include/exclude] | [back to top] | Give costs in year of original data; do not correct for inflation
Total (retro-)commissioning cost [$, or other currency in year incurred] | $, or other currency (in currency of year reported above as year commissioning was completed) | Should include study costs. Should not include TAB.
Of which, External Commissioning Provider Fee | costs in year incurred
Of which, monitoring/measurement-related costs | costs in year incurred
What % of total is represented by non-energy-related measures (e.g. security system cx), if cost and/or savings data are included below? | %
Cost Paid By:
Building owner | % (enter as decimal value) | Enter "0" if not applicable
Utility (e.g. as rebate) | % (enter as decimal value) | Enter "0" if not applicable
Other (e.g. research grant) | % (enter as decimal value) | Enter "0" if not applicable
Cost Breakdown, by Phase:
New Construction (Cx)
Design Review | % of total cost
Construction Observation | % of total cost
Acceptance Testing | % of total cost
Warranty | % of total cost
Existing Buildings (RCx)
Investigation and Planning | % of total cost
Implementation | % of total cost
Verification & Persistance Tracking | % of total cost
Reporting | % of total cost
Labor | costs in year incurred
Unpaid/unbilled labor | hours
Supplies and equipment costs | costs in year incurred
Utility rebate | costs in year incurred
Travel | costs in year incurred
Scope of (Retro-)commissioning: Items Included in Reported Costs
Commissioning (new buildings)
Stage Commissioning Begun (new construction only) | Design, Construction, Acceptance, Startup | Enter: "D", "C", "A", or "S"
Number of Steps
Commissioning provider development of design intent documents | Y(es); N(o); U(nknown) | Complete only if new building
Write specifications | Y(es); N(o); U(nknown) | Complete only if new building
Develop commissioning plan | Y(es); N(o); U(nknown) | Complete only if new building
Design review (indicate # of review cycles) | Y(es); N(o); U(nknown) | Complete only if new building
Develop sequences of operation (if not well-developed by mechanical or controls contractor) | Y(es); N(o); U(nknown) | Complete only if new building
Review submittals | Y(es); N(o); U(nknown) | Complete only if new building
Construction observation | Y(es); N(o); U(nknown) | Complete only if new building
Verification checks/prefunctional testing | Y(es); N(o); U(nknown) | Complete only if new building
Functional testing; use of diagnostic tools | Y(es); N(o); U(nknown) | Complete only if new building
Commissioning provider significantly involved in issue resolution | Y(es); N(o); U(nknown) | Complete only if new building
Oversee training | Y(es); N(o); U(nknown) | Complete only if new building
Review O&M manuals | Y(es); N(o); U(nknown) | Complete only if new building
Develop systems manual/recommissioning manual | Y(es); N(o); U(nknown) | Complete only if new building
Perform trend analysis, modeling, or benchmarking | Y(es); N(o); U(nknown) | Complete only if new building
Evaluate energy cost savings | Y(es); N(o); U(nknown) | Complete only if new building
Final report | Y(es); N(o); U(nknown) | Complete only if new building
Other (explain) | Text | Complete only if new building
Retro-commissioning (existing buildings)
Number of Steps
Document design intent or update current documentation | Y(es); N(o); U(nknown) | Complete only if existing building
Develop commissioning plan | Y(es); N(o); U(nknown) | Complete only if existing building
Perform utility bill analysis, benchmarking, and/or diagnostics | Y(es); N(o); U(nknown) | Complete only if existing building
Perform trend analysis | Y(es); N(o); U(nknown) | Complete only if existing building
Model building energy use | Y(es); N(o); U(nknown) | Complete only if existing building
Document master list of findings | Y(es); N(o); U(nknown) | Complete only if existing building
Estimate energy cost savings for findings | Y(es); N(o); U(nknown) | Complete only if existing building
Present a findings and recommendations report | Y(es); N(o); U(nknown) | Complete only if existing building
Update system documentation (control sequences) | Y(es); N(o); U(nknown) | Complete only if existing building
Implement O&M improvements | Y(es); N(o); U(nknown) | Complete only if existing building
Implement capital improvements | Y(es); N(o); U(nknown) | Complete only if existing building
Monitor fixes | Y(es); N(o); U(nknown) | Complete only if existing building
Measure energy savings | Y(es); N(o); U(nknown) | Complete only if existing building
Develop systems manual/recommissioning manual | Y(es); N(o); U(nknown) | Complete only if existing building
Final report | Y(es); N(o); U(nknown) | Complete only if existing building
Other (explain) | Text | Complete only if existing building
BASELINE ENERGY USE AND SAVINGS | [back to top] |  | IMPORTANT: Include energy used in central plant serving the building/project being described, if applicable
Whole-buildings energy use data (including fuels and end-uses to which (retro-)commissioning may not have been applied) is strongly preferred. Indicate the end uses included in following energy-use data [Whole Building, or finite set of end uses based on "Components" defined above]. If Components, please indicate which ones. | WB or C | Include savings only for measures known to have been implemented
Are the energy data weather-normalized? | Y(es); N(o); U(nknown) | Include pre-/post-commissioning data net of any influence of non-commissioning retrofits or building modifications. Also answer "Y" if values are engineering estimates.
If yes, using what method? | Describe method
Year of Energy Savings Data | Year (NNNN) | If possible, do not use first post-commissioning year's data (savings often manifest slowly). Use year-2 or -3.
Is the facility part of a campus with central heating and/or cooling? | Y(es); N(o); U(nknown)
If yes, did the (retro)commissioning address the plant? | Y(es); N(o); U(nknown)
Total (Whole-Building) Electricity usage: |  | Excludes electricity use for central plant CW (counted below instead)
Before (retro-)commissioning | kWh/year | enter zero if none, or "unknown" if information is not available
After (retro-)commissioning (or as-commissioned, if new building) | kWh/year | enter zero if none, or "unknown" if information is not available
Savings | kWh/year | enter zero if none, or "unknown" if information is not available
Total (Whole-Building) Electric Peak Demand |  | Excludes electricity use for central plant CW (counted below instead)
Before (retro0)commissioning | peak kW | enter zero if none, or "unknown" if information is not available
After (retro-)commissioning (or as-commissioned, if new building) | peak kW | enter zero if none, or "unknown" if information is not available
Savings | peak kW | enter zero if none, or "unknown" if information is not available
Total (Whole-Building) Fuel usage: |  | Excludes fuel use for central plant HW or steam (counted below instead)
Before (retro-)ommissioning | Millon BTU/year | enter zero if none, or "unknown" if information is not available
After (retro-)commissioning (or as-commissioned, if new building) | Million BTU/year | enter zero if none, or "unknown" if information is not available
Savings | Million BTU/year | enter zero if none, or "unknown" if information is not available
Thermal (Total--Whole-Building--chilled water, hot water, and steam) |  | Enter information here ONLY if it is not available separately for HW, CW, and Steam (in which case, add separately in the following three sub-sections)
Before (retro-)commissioning | Million BTU/year | enter zero if none, or "unknown" if information is not available
After (retro-)commissioning (or as-commissioned, if new building) | Million BTU/year | enter zero if none, or "unknown" if information is not available
Savings | Million BTU/year | enter zero if none, or "unknown" if information is not available
Total (Whole-Building) Hot water
Before (retro-)commissioning | Million BTU/year | enter zero if none, or "unknown" if information is not available
After (retro-)commissioning (or as-commissioned, if new building) | Million BTU/year | enter zero if none, or "unknown" if information is not available
Savings | Million BTU/year | enter zero if none, or "unknown" if information is not available
Total (Whole-Building) Steam
Before (retro-)commissioning | Million BTU/year | enter zero if none, or "unknown" if information is not available
After (retro-)commissioning (or as-commissioned, if new building) | Million BTU/year | enter zero if none, or "unknown" if information is not available
Savings | Million BTU/year | enter zero if none, or "unknown" if information is not available
Total (Whole-Building) Chilled water
Before (retro-)commissioning | Million BTU/year | enter zero if none, or "unknown" if information is not available
After (retro-)commissioning (or as-commissioned, if new building) | Million BTU/year | enter zero if none, or "unknown" if information is not available
Savings | Million BTU/year | enter zero if none, or "unknown" if information is not available
GRAND Total (Whole-Building) energy use (electric, fuel, thermal) | ENTER ONLY IF NOT PROVIDED FOR ELECTRICITY AND INDIVIDUAL FUELS ABOVE
Before (retro-)commissioning | Million BTU/year [count electricity at 10,000 BTU/kWh] | enter zero if none, or "unknown" if information is not available
After (retro-)commissioning (or as-commissioned, if new building) | Million BTU/year [count electricity at 10,000 BTU/kWh] | enter zero if none, or "unknown" if information is not available
GRAND Total (whole-building) energy cost (electric, peak, fuel): | $/year | No inflation correction
Before (retro-)commissioning | $/year | No inflation correction
After (retro-)commissioning (or as-commissioned, if new building) | $/year | No inflation correction
Nominal Energy Savings (all forms combined, cost in year of savings, no inflation-correction) | $/year-project | No inflation correction (use same unit energy costs in pre/post years)
Energy prices associated with cost estimates |  | Use values corresponding to cost data provided above
electricity | $/kWh | indicate if units other than dollars
peak electricity demand | $/kW-Month | "
fuel | $/million BTU | "
purchased thermal energy (hot/cold water and/or steam) | $/million BTU | "
hot water | $/million BTU | "
chilled water | $/million BTU | "
steam | $/million BTU | "
Energy Savings Determination [select answers that correspond to the energy data given in prior rows] -- DOMINANT METHOD SHOULD BE LISTED IN THIS ROW | A; B; C; D; or E | If multiple methods are used, choose ONE of the following to reflect the most prevalent form of determination.
Engineering Estimates/Simulations (no measurements) = "E" | Y(es); N(o); U(nknown)
Measured Savings - IPMVP Option A. Partially measured retrofit isolation | Y(es); N(o); U(nknown) | IPMVP Category: See "M&V Options Tab for definitions"
Measured Savings - IPMVP Option B. Retrofit isolation | Y(es); N(o); U(nknown) | IPMVP Category: See "M&V Options Tab for definitions"
Measured Savings - IPMVP Option C. Whole facility | Y(es); N(o); U(nknown) | IPMVP Category: See "M&V Options Tab for definitions"
Measured Savings - IPMVP Option D. Calibrated simulation | Y(es); N(o); U(nknown) | IPMVP Category: See "M&V Options Tab for definitions"
Do the preceeding savings data reflect all (retro-)commissioning activities described and costed above? | Y(es); N(o); U(nknown)
If "no", list % increase in reported savings anticipated (for measures known to be slated for implementation) | % | will be used to modify raw savings data (if applicable)
Persistence of Energy Savings (existing buildings) or Performance (new construction) | Persistence of Energy Savings or Performance (EUI in given post-Cx year / EUI in pre-Cx year [note which energy type it applies to, e.g. "total", "elect", "fuel", etc.] | If available, also provide notation on the persistence of individual measures, via the column provided in the "Measures" tab.
Year 0 (pre-commissioning) | ratio (Electricity; Fuel; CHW; HW; Steam) | 1.00; 1.00; 1.00; 1.00; 1.00
Year 1 | ratio (Electricity; Fuel) | <1.00 if savings; >1.00 if EUI increases
Year 2 | ratio (Electricity; Fuel) | <1.00 if savings; >1.00 if EUI increases
Year 3 | ratio (Electricity; Fuel) | <1.00 if savings; >1.00 if EUI increases
Year 4 | ratio (Electricity; Fuel) | <1.00 if savings; >1.00 if EUI increases
Year 5 | ratio (Electricity; Fuel) | <1.00 if savings; >1.00 if EUI increases
Year 6 | ratio (Electricity; Fuel) | <1.00 if savings; >1.00 if EUI increases
If one or more periods include changes in occupancy, schedules, equipment, energy prices, or occupied floor area, are these adjusted for in the preceding estimates? | Y(es); N(o); U(nknown)
NON-ENERGY IMPACTS - [See "Non-Energy Impacts" tab for the types of impacts to consider] | [back to top]
First-Cost Savings
For new construction, was building occupied on schedule? | Y(es); N(o); U(nknown)
Change orders and warranty claims | Y(es); N(o); U(nknown)
| $ (or other currency) | Show reductions as a negative value; increases as a positive value
Other first-cost | $ (or other currency) | "
Improved construction team coordination, reduction of disagreements among contractors | Y(es); N(o); U(nknown)
| $ (or other currency) | "
Building start-up and turnover - building occupied more quickly, call-backs reduced, TAB costs reduced | Y(es); N(o); U(nknown)
| $ (or other currency) | "
Project proceeded on schedule, problems detected and corrected earlier than would have been without commissioning | Y(es); N(o); U(nknown)
| $ (or other currency) | "
Benefits to project design - improvements to system design, equipment sized correctly | Y(es); N(o); U(nknown)
| $ (or other currency) | "
Ongoing (recurring) Cost Savings
Improvements to O&M - system documentation available, staff provided with training, staff satisifed with ability to operate building, equipment life extended, ongoing O&M costs reduced. | Y(es); N(o); U(nknown)
Ongoing Labor Cost | O&M; C, P, D, CO; IR, O | Reduction/increase (O&M, Complaints, Productivity, Downtime, Information Requests, Other):
Labor | person-hours/year | Show reductions as a negative value; increases as a positive value
Cost | $/year | "
Other
Thermal Comfort | Y(es); N(o); U(nknown)
| $/year | "
Indoor Air Quality | Y(es); N(o); U(nknown)
| $/year | "
Productivity/Safety | Y(es); N(o); U(nknown)
| $/year | "
Tenant retention; turnover | Y(es); N(o); U(nknown)
| $/year | "
Liability | Y(es); N(o); U(nknown)
| $/year | "
Equipment Life | Y(es); N(o); U(nknown)
| $/year | "
Maintenance | Y(es); N(o); U(nknown)
| $/year | "
Training & education of operations staff or occupants | Y(es); N(o); U(nknown)
| $/year | "
Other (or combination of above) | Y(es); N(o); U(nknown)
| $/year | "
OTHER
Data Source(s) | Text | If from a published paper or report, please provide full citation and a .pdf if available
Comments (summarize concisely here; attach Tabs if desired) | Text
Note on A1: Evan Mills: "25-30k for all in this set"
Note on A1: J. Warner: "New" as of 1994 report
Note on A1: J. Warner: "New" as of 1994 report
Note on A1: Evan Mills: Need count of total projects responding
Note on A1: Evan Mills: Doesn't jive with price-calc'd answers
Note on A1: Evan Mills: Doesn't jive with price-calc'd answers
Note on A1: Evan Mills: Doesn't jive with reported quantities and prices
Note on A1: Evan Mills: Where net cx cost is negative, we post zero here
Note on A1: Evan Mills: Only Cx agent fee given in source doc
Note on A1: Evan Mills: Only Cx agent fee given in source doc
Note on A1: Evan Mills: Only Cx agent fee given in source doc
Note on A1: Evan Mills: Only Cx agent fee given in source doc
Note on A1: Evan Mills: Only Cx agent fee given in source doc
Note on A1: Evan Mills: Only Cx agent fee given in source doc
Note on A1: Evan Mills: Only Cx agent fee given in source doc
Note on A1: Evan Mills: Only Cx agent fee given in source doc
Note on A1: Evan Mills: Only Cx agent fee given in source doc
Note on A1: Evan Mills: Only Cx agent fee given in source doc
Note on A1: Evan Mills: Only Cx agent fee given in source doc
Note on A1: Evan Mills: Added 898 ones not individually allocated to the SBW/Skumatz buildings
Note on A1: Evan Mills: Includes 632 not allocated to individual SBW buildings
Note on A1: Evan Mills: Per MAP
Note on A1: Evan Mills: demonstration project for RCx of Long term care facilities
Note on A1: Evan Mills: conduct a pilot demonstration for replication (utility-funded)
Note on A1: Evan Mills: demonstration project for RCx of Long term care facilities
Note on A1: Hannah: cx demonstration project (could categorize this is research, I suppose)
Note on A1: Hannah: State of Tennessee cx learning experience
Note on A1: Evan Mills: Numbers in parentheses are the UC/CSU project ID's
Note on A1: Evan Mills: From 04-05 MBCx Project List, Col AT
Note on A1: Evan Mills: 100 in place; 40 operated
Note on A1: Evan Mills: Worksheet says "TBD"
Note on A1: Evan Mills: Per Karl Brown
$0.04/ft2-y

## MEASURES
Use this matrix to enter measures for which itemized costs and energy savings estimates are available. | [31 empty] | Version: February 2, 2009
Note: DETAILED DEFINITIONS GIVEN ON "Measures Key" TAB.
INSTRUCTIONS: Provide counts in (only) one Components box and one Strategies box per row, i.e. 2 values per row only. You may insert additional rows, but only above the "Other" row. The "Other" row should include the sum total of any residual values not itemized in the preceding rows. Priority for itemized measures should be given to items that combine high energy savings and attractive payback times. See "Measures Key" tab for definitions, and "M&V Options Tab for key to M&V Code.
This template is to be completed to achieve a mapping of problems ("deficiencies") and the recommended solutions ("measures"). Where measure-level cost and energy savings data are available, it should be included. Problems and measures should be listed, irrespective of whether the measures are known to have been implemented. However, include energy savings and implementation cost estimates only for recommended measures known to have been implemented. If the effort required to provide a complete listing of findings is prohibitive, give priority to those with significant energy implications and good cost-effectiveness. Alternatively, all measures may be aggregated into one row. if measure-specific information is not known. Rejected measures may be tabulated on the indicated row.
Note: Unshaded columns (e.g. "Measure Code") and rows (e.g. totals) will automatically calculate; do not alter formulas
SAMPLE
Project ID Number: (e.g. XYZ-4) | [34 empty] | Energy Savings (use year-2 or -3 data if available)
| Components (locus of fault) | [9 empty] | Measures | [17 empty] | Measure Code | Implemented [Y; Unknown; Rejected] | Savings Estimation Approach (IPMVP A;B;C;D or Estimated) | M&V Code | Physically Persisted [Y/N]? As of _ Years | Detail problems and remediation measures | Electricity Savings (kWh/y) | Peak Electrical Demand Savings [kW/y] | Fuel Savings [Million BTU/y] | Chilled and/or Hot Water Savings | Nominal RCx Implementation Cost [$] | Nominal Energy Cost Savings [$/y] | Nominal Simple Payback [years] | Normalized RCx Implementation Cost [$] 2003 values | Normalized Energy Cost Savings [$/y] 2003 values | Deflator
| HVAC (combined heating and cooling) | Cooling plant | Heating plant | Air handling & distribution | Terminal units | Lighting | Envelope | Plug loads | Facility-wide (e.g. controls, EMCS, or utility related) | Other | Design, Installation, Retrofit, Replacement |  |  |  | Operations & Control | [8 empty] | Maintenance | [19 empty] | #REF!
[11 empty] | Design change (design detail, improper equipment, improper system, etc.) | Installation modifications (construction out of spec, equipment out of spec, O&M access, etc.) | Retrofit/equipment replacement (faulty sensors, etc.) | Other | Implement advanced reset (air, water, lighting) | Start/Stop (environmentally determined) | Scheduling (occupancy determined) - equipment or lighting | Modify setpoint (high VAV setpoint minimum, setpoint suboptimal) | Equipment staging | Modify sequence of operations | Loop tuning | Behavior modification/manual changes to operations | Other | Calibration | Mechanical fix (flow obstructions, leaky valves, leaky ductwork, etc.) | Heat transfer maintenance (dirty heat transfer component, improper refrigerant charge, etc.) | Filtration maintenance | Other | [15 empty] | Normalized Simple Payback [years] 2003 values
| V | C | H | A | T | L | E | P | F | O | D1 | D2 | D3 | D4 | OC1 | OC2 | OC3 | OC4 | OC5 | OC6 | OC7 | OC8 | OC9 | M1 | M2 | M3 | M4 | M5
[8 empty] | 1 | [7 empty] | 1 | [12 empty] | 2 | Y | B | Y-B | Y-3 | AHU-3's running time could be reduced | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
|  |  |  | 2 | [13 empty] | 2 | [10 empty] | 4 | U | E | U-E | Y-2 | Operating room cold and OA requirements govern all of AHUs 7; 8 | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
|  |  |  | 2 | [11 empty] | 2 | [12 empty] | 4 | Y | C | Y-C | N-1 | Prefilters and final filters used in AHU-7 and 8 | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
|  |  |  | 1 | [12 empty] | 1 | [11 empty] | 2 | Y | D | Y-D | Y-4 | AHU-1 (15 hp) serving the 1st floor auditorium is on 7:00-4:30, 5 days a week, but used much less | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
|  |  |  | 1 | [12 empty] | 1 | [11 empty] | 2 | etc. | etc. | etc. | etc. | AHU-10 (7.5 hp) serves the conference/board room & is on 7:00-4:30, 5 days a week but rarely used. | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
|  | 1 | [15 empty] | 1 | [10 empty] | 2 |  |  | - |  | Chilled water supply temperature setpoint is fixed at 44 F | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
|  | 1 | [15 empty] | 1 | [10 empty] | 2 |  |  | - |  | Chiller secondary chilled water pressure differential is based in a fixed setpoint | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
|  | 1 | [15 empty] | 1 | [10 empty] | 2 |  |  | - |  | Chiller has fixed entering condenser water temperature (ECDWT) of 78F that can be optimized | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
[6 empty] | 8 | [18 empty] | 8 |  |  |  | 16 |  |  | - |  | More light fixtures were on than is necessary in room 537 | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
[6 empty] | 4 | [18 empty] | 4 |  |  |  | 8 |  |  | - |  | Operating rooms had lights on late at night | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
[6 empty] | 1 | [18 empty] | 1 |  |  |  | 2 |  |  | - |  | Exterior lights are controlled by a broken timeclock, so lights are on all night. | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
[8 empty] | 1 | [8 empty] | 1 | [7 empty] | 1 |  |  |  | 3 |  |  | - |  | The plate warmer in the kitchen is left on all night. | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
|  | 3 | [20 empty] | 3 | [5 empty] | 6 |  |  | - |  | Primary chilled water pumps P-1, 2; 3 (30 hp) have balancing valves restricted to 40%. | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
|  | 3 | [20 empty] | 3 | [5 empty] | 6 |  |  | - |  | Balancing valves on 75 hp condenser pumps P-7, 8; 9 set at only 20% open | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
|  | 6 | [8 empty] | 6 | [17 empty] | 12 |  |  | - |  | Condenser pumps need isolation valves for cooling tower | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
[6 empty] | 1 | [10 empty] | 1 | [11 empty] | 2 |  |  | - |  | Board room lighting is on 7:00-4:30, 5 days a week, but rarely needed. | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
[6 empty] | 1 | [9 empty] | 1 | [12 empty] | 2 |  |  | - |  | First floor auditorium has no automatic lighting control | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
[6 empty] | 25 | [5 empty] | 25 | [16 empty] | 50 |  |  | - |  | Lighting occupancy sensors could be used in many rooms | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
[6 empty] | 15 | [16 empty] | 15 | [5 empty] | 30 |  |  | - |  | The atrium areas on floor 1 and 2 have recess can lights on when natural daylight is adequate | [6 empty] | #DIV/0! | #REF! | #REF! | #REF!
Other (#) | 1 | 2 |  | 1 | 1 |  |  |  | 6 |  | 2 | 5 | [10 empty] | 4 | [5 empty] | 22 | [11 empty] | #DIV/0! | #REF! | #REF! | #REF!
Rejected (#) |  | 3 |  |  | 8 |  | 2 | 4 |  | 8 |  |  | 3 |  |  | 8 |  |  |  | 4 | [7 empty] | 8 | 48 | R | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Count or total: | 1 | 17 | 0 | 7 | 1 | 55 | 0 | 2 | 6 | 0 | 8 | 30 | 0 | 0 | 0 | 4 | 4 | 5 | 0 | 0 | 0 | 0 | 25 | 0 | 14 | 0 | 0 | 0 | Totals | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #REF! | #REF! | #REF!
Grand Totals: | 89 | [9 empty] | 90
TEMPLATE (Copy and replicate the following master matrix for each project)
Project ID Number: (Should match that used on tthe MAIN DATA SHEET) | [37 empty] | Energy Savings (use year-2 or -3 data if available)
| Components (locus of fault) | [9 empty] | Measures | [17 empty] | Measure Code | Implemented [Y; Unknown; Rejected] | Savings Estimation Approach (IPMVP A;B;C;D or Estimated) | M&V Code | Physically Persisted [Y/N]? As of _ Years | Detail problems and remediation measures | Electricity Savings (kWh/y) | Peak Electrical Demand Savings [kW/y] | Fuel Savings [Million BTU/y] | Chilled and/or Hot Water Savings | Nominal RCx Implementation Cost [$] | Nominal Energy Cost Savings [$/y] | Nominal Simple Payback [years] | Normalized RCx Implementation Cost [$] 2003 values | Normalized Energy Cost Savings [$/y] 2003 values | Deflator
| HVAC (combined heating and cooling) | Cooling plant | Heating plant | Air handling & distribution | Terminal units | Lighting | Envelope | Plug loads | Facility-wide (e.g. controls, EMCS, or utility related) | Other | Design, Installation, Retrofit, Replacement |  |  |  | Operations & Control | [8 empty] | Maintenance | [19 empty] | #REF!
[11 empty] | Design change (design detail, improper equipment, improper system, etc.) | Installation modifications (construction out of spec, equipment out of spec, O&M access, etc.) | Retrofit/equipment replacement (faulty sensors, etc.) | Other | Implement advanced reset (air, water, lighting) | Start/Stop (environmentally determined) | Scheduling (occupancy determined) - equipment or lighting | Modify setpoint (high VAV setpoint minimum, setpoint suboptimal) | Equipment staging | Modify sequence of operations | Loop tuning | Behavior modification/manual changes to operations | Other | Calibration | Mechanical fix (flow obstructions, leaky valves, leaky ductwork, etc.) | Heat transfer maintenance (dirty heat transfer component, improper refrigerant charge, etc.) | Filtration maintenance | Other | [15 empty] | Normalized Simple Payback [years] 2003 values
| V | C | H | A | T | L | E | P | F | O | D1 | D2 | D3 | D4 | OC1 | OC2 | OC3 | OC4 | OC5 | OC6 | OC7 | OC8 | OC9 | M1 | M2 | M3 | M4 | M5
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
[29 empty] | #N/A |  |  | - | [8 empty] | #DIV/0! | #REF! | #REF! | #REF!
Other (#) | [40 empty] | #DIV/0! | #REF! | #REF! | #REF!
Rejected (#) | [29 empty] | R | N/A | N/A | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Count or total: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Totals | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #REF! | #REF! | #REF!
Grand Totals: | 0 | [9 empty] | 0
Sample

## Measures Key
KEY TO MEASURE DEFINITIONS
Design, Installation, Retrofit, Replacement
Code
Design change (design detail, improper equipment, improper system, etc.) | D1
Design problems found and corrected during design review of a new building (Cx), a design problem physically corrected or circumvented (during Cx or RCx). [Problems with the design of control sequences are accounted for under "Operations & Control".]
Installation modifications (construction out of spec, equipment out of spec, O&M access, etc.) | D2
To address out-of-spec or improper installation of equipment, sensors, distribution systems, etc. Could also include corrections to ensure future access for O&M.
Retrofit/equipment replacement (faulty sensors, etc.) | D3
RCx strategies to improve the performance of a system, as distinct from a change in design [treated above]. Major capitol retrofits are not considered part of commissioning and should not be included in this analysis.
Other | D4
Other design, installation, retrofit, or replacement measures.
Operations & Control
Implement advanced reset (air, water, lighting) | OC1
Recommended modifications to reset schedules of HVAC processes. E.g., Supply Air Temperature reset based on Outside Air Temperature; corrections to fan/pump speeds or lighting levels.
Start/Stop (environmentally determined) | OC2
Recommendations that affect environmentally determined equipment control settings (e.g., chiller or boiler lockouts that based on out side air dry bulb temperature or seasonally determined equipment operation).
Scheduling (occupancy determined) - equipment or lighting | OC3
Recommendations affecting the control of equipment availability as a function of building occupancy (e.g. lighting sweeps; temperature setbacks; morning warm-up).
Modify setpoint (high VAV setpoint minimum, setpoint suboptimal) | OC4
Recommendations that modify the setpoint of a control loop. E.g., Supply air temperature setpoint, thermostat setpoint, or static pressure setpoint.
Equipment staging | OC5
Recommendations that affect control settings for the availability or staging of duplicate equipment, e.g., Chiller staging and loading sequence or lead-and-lag pumping sequences.
Modify sequence of operations | OC6
Recommendations that propose changes significant enough to be considered a major modification to the building’s existing sequence of operations.
Loop tuning | OC7
Modify control loop parameters to improve control (reduce cycling, hunting, oscillations).
Behavior modification/manual changes to operations | OC8
Recommendations that seek to modify the behavior of the building staff or occupants or instruct building staff or occupants on the proper use of equipment (e.g. turning off lights upon leaving a room, correctly manipulating the system in response to complaint calls).
Other | OC9
Other operations & control measures.
Maintenance
Calibration | M1
Recommendations that address calibration problems with equipment or systems.
Mechanical fix (flow obstructions, leaky valves, leaky ductwork, etc.) | M2
Replacing belts, broken linkages, motor maintenance, etc.
Heat transfer maintenance (dirty heat transfer component, improper refrigerant charge, etc.) | M3
Coil cleaning, cooling tower water treatment, correcting refrigerant charge
Filtration maintenance | M4
Changing filters, modifying filter racks, changing filter type, etc.
Other | M5
Other maintenance measures.

## Building Type Key
Detailed Building Type Definitions
Description of Building Types Used in the MSE Energy Calculator
In the Commercial Buildings Energy Consumption Survey (CBECS), upon which our calculator is based, buildings were classified according to principal activity, which was the primary business, commerce, or function carried on within each building. Buildings that were used for more than one of the activities described below were assigned to the activity occupying the most floorspace at the time of the interview. Thus, a building assigned to a particular principal activity category may have been used for other activities in a portion of its space or at some time during the year.
Each of the principal activity categories is listed alphabetically and described below. Lists of specific types of buildings included in each category are presented for clarification but are not intended to be exhaustive.
1.Agricultural: See Other.
2.Education: refers to buildings used for academic or technical classroom instruction. This category includes the following:
Schools:
Preschool
Elementary
Junior high
Senior high
College or university classroom/Laboratories
Vocational school.
Other activities that occur on school campuses are reported separately:
Administration (see Office)
Auditorium (see Public Assembly)
Dormitory (see Lodging)
Gymnasium (see Public Assembly)
Infirmary (see Health Care)
Library (see Public Assembly)
Museum (see Public Assembly)
School for the Mentally Retarded (see Health Care)
Stadium (see Public Assembly)
Student Union (see Public Assembly).
3.Enclosed Shopping Center/Mall: See Mercantile and Service.
4.Food Sales: refer to buildings used for retail or wholesale sale of food. This category includes the following:
Convenience store or market
Farmer's market, Fruit/Vegetable market
Grocery store/Supermarket
Meat/Seafood store
Retail bakery
Specialty food store.
5.Food Service: refers to buildings used for preparation and sale of food and beverages for consumption. This category includes the following:
Prepared-Meal Service:
Cafeteria
Carry-out Service:
Caterer
Fast-food establishment
Pizza parlor
Sandwich shop
Full-Service Restaurant:
Bar
Bar and grill
Coffee shop
Diner
Full-menu-service establishment.
6.Health Care: refers to buildings used as diagnostic and treatment facilities for both inpatient and outpatient care. In the tables of this report, inpatient and
outpatient buildings are combined in the "Health Care" Principal Building Activity category. Excluded from this group are skilled nursing or other residential
care facilities (nursing homes).
Inpatient facilities treat the mentally or physically ill. Buildings for overnight care are in this grouping. This category includes the following:
Medical Care Hospital:
Chronic disease
Ear, eye, nose, and throat
General medical and surgical
Maternity
Medical infirmary (connected with an institution)
Orthopedic
Tuberculosis/other respiratory disease
Mental Facility:
Mental retardation/schools for the mentally retarded
Psychiatric
Rehabilitation Facility:
Alcoholism
Substance abuse/narcotics/drug addiction
Physical therapy.
Outpatient facilities may be medical, dental, or psychiatric and involves diagnosis and treatment in which services are not required overnight. Buildings used
for veterinary practices also fall into this category. This category includes the following:
Dental Clinic
Medical Clinic:
Abortion/birth control
Ear, eye, nose, and throat
Emergency walk-in
General
Mental health/psychiatric clinic
Veterinary Facilities.
7.Hospital/Inpatient Health Services: See Health Care.
8.Hotel/Motel/Dorm: See Lodging.
9.Industrial/Manufacturing: See Other.
10.Laboratory:
11.Lodging: refers to buildings used to offer multiple accommodations for short-term or long-term residents, including nursing homes. In the table of this
report, skilled nursing and other residential care facilities are included in the "Lodging" Principal Building Activity category.
Hotel/Motel/Dorm are included in the following short-term and long-term residences:
Short-Term Residence:
Convention hotel
Hotel
Inn
Motel
Shelter home
Tourist home
Long-Term Residence:
Boarding house
Convent/monastery
Extended Stay Hotels
Dormitory/sorority/fraternity
Orphanage
Assisted-living elder care facilities (limited medical facilities)
Skilled Nursing/Other Residential Care refers to buildings used as facilities which offer 24-hour nursing/medical care. This category includes the following:
Homes for the aged
Nursing homes.
12.Mercantile and Service: refers to buildings used for sales and displays of goods or services (excluding food). This category includes shopping malls and
strip centers, as well as retail and service as outlined below.
Retail (other than shopping mall or strip center):
Automobile dealers
Building materials, Garden supply, and Hardware stores
Department stores
Drugstores
Furniture, Home equipment stores and Home furnishings
Liquor stores
Wholesale goods (except food)
Service (other than food service):
Dry cleaner/Car wash/Laundry
Gasoline stations
Motor vehicle repair/service/maintenance
Multiservice establishments
Personal service
Post office.
13.Nonrefrigerated Warehouse or Storage: See Warehouse and Storage.
14.Office: refers to buildings used for general office space, professional offices, and administrative offices. This category includes the following:
Financial Office Building:
Bank
Brokerage firm
Insurance
Real estate
Securities
Professional Office Building:
Administration of an institution
Consulting
Corporate
Engineering
Law
Management
Medical
Mixed professional.
15.Other: refers to buildings used for activities that do not fit into any of the specifically named categories. In the tables of this report, this category includes
laboratories and buildings identified as having several commercial activities that together represent 50 percent or more of the floorspace, but whose largest
single activity is agricultural, industrial/manufacturing, or residential.
Other:
Crematorium
Hangar
Public restrooms/Showers
Telephone exchange
Greenhouse with retail sales of plants
Manufacturing with retail sales of products
Printing plant with retail sales.
Laboratory refers to buildings used for activities which utilize equipment for experimental testing or for analysis. This category includes the following:
Mechanical/Electrical Laboratory
Medical/Dental Laboratory
Agricultural Laboratory.
16.Outpatient Health Services/Clinic: See Health Care.
17.Public Assembly: refers to buildings in which people gather for social or recreational activities whether in private or nonprivate meeting halls. This
category includes the following:
Entertainment Building:
Archive/art gallery/exhibit hall/library/museum
Coliseum/arena (enclosed)
Concert hall
Observatory/planetarium
Night Club
Radio/TV station or studio
Theater/movie house/cinema
Recreational Facility:
Amusement arcade
Bowling alley
Community Centers
Gymnasium/YMCA or YWCA/indoor racket sports, recreation center/athletic facility
Indoor pool
Poolroom
Skating rink
Social/Public/Civic Assembly:
Assembly hall
Auditorium
Convention hall
Funeral home
Lecture hall
Lodge hall
Meeting hall
Student union
Town hall
Other Enclosed Assembly Building:
Armory
Passenger terminal
Stadium.
18.Public Order and Safety: refers to buildings used for the preservation of law and order or public safety. This category includes the following:
Courthouse
Fire station
Jail
Penitentiary/Prison
Reformatory
Sheriff's office.
19.Refrigerated Warehouse or Storage: See Warehouse and Storage.
20.Religious Worship: refers to buildings in which people gather for religious activities. This category includes the following:
Chapel
Church
Mosque
Synagogue
Temple.
21.Residential: See Other.
22.Retail (other than shopping mall or strip center): See Mercantile and Service.
23.Service (other than food service): See Mercantile and Service.
24.Skilled Nursing/Other Residential Care: See Lodging.
25.Strip Shopping Center: See Mercantile and Service.
26.Warehouse and Storage: refers to buildings used to store goods, manufacturing products, merchandise, or raw materials. In the tables of this report, both
refrigerated and non-refrigerated warehouse and storage are included in the "Warehouse" Principal Building Activity category.
Refrigerated Storage refers to buildings specifically designed to store perishable goods or merchandise under refrigeration. Includes "cold storage" facilities,
which store products at temperatures between 0 degrees Fahrenheit and 50 degrees Fahrenheit and "freezer" facilities, which store products at temperatures
between 0 degrees Fahrenheit and 20 degrees Fahrenheit.
This category includes the following:
Cheese warehouse
Cold storage
Fur storage.
Nonrefrigerated Warehouse refers to buildings specifically designed to store perishable goods or merchandise without refrigeration.
27.Vacant: refers to commercial buildings in which more floorspace was vacant than was used for any single commercial activity (as defined above) at the time
of interview. Thus a vacant building may have some occupied floorspace. Vacant space does not include space being maintained and ready for use.

## M&V Key
E . Estimated. Based on engineering calculations, only
Source: http://www.ipmvp.org
E . Estimated. Based on engineering calculations, only

## Cost Rules
Use these rules to determine whether or not to include specific costs in building description.