## Instructions
ENERGY STAR Data Center Infrastructure Rating Development
Data Collection Form
Data Collection Guidelines
§ The data collection effort will focus on stand-alone data centers and data centers in larger buildings (e.g. office buildings) that have submetering capability to isolate data center operations.
§ Report values that were valid for at least 12 consecutive months within a period from March 20, 2008 to June 1, 2009.
§ The facility must have been in normal operation for at least 12 months.
§ If data elements change over time (e.g. the number of racks, UPS utilization), provide the average of that element over the 12 month data collection period.
§ If you have any specific questions about the items listed below, or difficulty assessing data during this data collection period, please send an email to ENERGYSTARdatacenters@icfi.com.
Data Elements List
The following table outlines the data elements of interest; each section of the table corresponds to a tab in this MS Excel Data Template. This data template was created for your convenience, but we will accept the data in any form, provided all of the listed information is included.
Data Element Name | Description/Question | Comments
Tab 1 – Building Information |  | Add data elements for the number of racks and power (megawatts)
Data Center Name or ID | Please provide a unique name (or number) for each data center in your sample.
Zip Code | Please provide the five-digit zip code for each data center's location.
Type of Data Center | Please select among the following: 1 = Traditional Enterprise; 2 = On-Demand Enterprise; 3 = Telecom; 4 = High Performance Computing Center (Scientific); 5 = Hosting; 6 = Internet; 7 = Hybrid | Please select among the following: 1 = Traditional Enterprise; 2 = On-Demand Enterprise; 3 = Telecom; 4 = HPCC; 5 = Hosting; 6 = Internet; 7 = Hybrid
Type of Building | Please select between the following: 1 = Stand-alone, 2 = Enclosed in a larger building (i.e. office building or other space type). NOTE: If the data center is enclosed within another building space, it must be completely submetered in order to proceed with this data collection.
Building Square Footage | Provide the gross or total square footage of the building.
Data Center Square Footage | Provide the square footage of the data center space that includes the rack equipment, service clearance and circulation, control console area, power distribution, and local air conditioning that is encapsulated by the proper protective walls. Exclude administrative offices, storage, loading docks, and other non-essential space that does not directly support the operation of the data center. | Change element to "Data Center Square Footage" and provide definition
Building Earned the ENERGY STAR? | Has the building earned the ENERGY STAR? (Yes or No)
Building LEED Certified? | Has the building received the US Green Building Council LEED certification? (Yes or No) | Change element to "Building LEED Certified?" and the description to "Has the building received the US Green Buildings Council LEED certification? (Yes or No)"
Tab 2 – Data Center Operations
For any element that may change over the course of the data collection period (e.g. number of racks, UPS utilization), please provide an average figure for the 12 months of data.
Reliability (Tier Level) | Using the Uptime Institute's classification of four tiers of reliability (Tier I, II, III, IV), please provide the level of the data center's reliability that describes the amount of required, active, redundant infrastructure. When multiple tier levels exist, the reliability tier level should represent the majority, or the highest percentage, of the data center's total load. When estimating tier levels, the fractional estimates (i.e. 3+ or 3.5) should be rounded DOWN to the whole number for purposes of the data input. (See Uptime's Web site for more information on the tier classifications: http://www.upsite.com/TUIpages/whitepapers/tuitiers.html) | When multiple tier levels exist, the reliability tier level should represent the majority, or the highest percentage, of the data center's total load
Number of Racks | Please provide the number of racks in the data center that are typically in operation.
UPS Utilization | Based on your data center's tier level and corresponding UPS configuration, please enter the percent utilization of your UPS, which is the amount of critical load compared with the redundant capacity of the system. Please use the examples in the FAQs to see the calculations associated with each tier level and UPS configuration. If you have multiple systems and multiple configurations, please use the pro-rated average of all systems weighted by load and their individual system utilizations.
Total Capacity for Cooling | To help determine the Chiller Utilization, provide the data center's total capacity for cooling in tons. | Change element to "Chiller Utilization" and provide definition
Annual Chiller Runtime | To help determine the Chiller Utilization, please provide the annual runtime for the chillers in hours.
Average Chiller Demand | To help determine the Chiller Utilization, enter the average demand for the chillers in KW.
Tab 3 – IT Measurement
Total IT Plug Energy from UPS Meter in KWh | Please enter the annual total IT plug energy, as measured in KWh, from the output of a UPS meter, for energy going into the computer room (not crac units, etc.). This can be entered as one value for the year or as a series of meter/energy readings (i.e. monthly or periodic) that cover the entire calendar year. It is preferable that these measurements are read at approximately the same period and frequency as the utility meter for the building. | Collect BOTH the output value from the UPS meter and the input value from the PDU meter
Start Date | For each energy use value, enter a start and end date. You can provide an entry for each meter/energy reading or one entry for the entire year. | Provide unit of time associated with power measurement (i.e. one month)
End Date
Total IT Plug Energy from PDU Meter in KWh (If Available) | Please enter the annual total IT plug energy, as measured in KWh, from the input of a PDU meter, for energy going into the computer room (not crac units, etc.). This can be entered as one value for the year or as a series of meter/energy readings (i.e. monthly or periodic) that cover the entire calendar year. It is preferrable that these measurements are read at approximately the same period and frequency as the utility meter for the building. If both the UPS and PDU meters are provided, an estimate of the difference between the total UPS and the sum of the PDU's will be estimated as the non-critical UPS load that might be serving the office, mechanical and non-data center loads. | Collect BOTH the output value from the UPS meter and the input value from the PDU meter
Start Date | For each energy use value, enter a start and end date. You can provide an entry for each meter/energy reading or one entry for the entire year. | Provide unit of time associated with power measurement (i.e. one month)
End Date
Tab 4 – Electricity Data
Provide the annual electricity consumption for the building (if a stand-alone data center) or the submetered data center. You can provide this as one value for the year or as a series of meter/energy bill entries that cover the entire year.
Meter ID | Enter a distinguishing name or number for each meter.
Start Date | For each energy use value, enter a start and end date. You can provide an entry for each bill or one entry for the entire year.
End Date
Electricity Consumption in KWh | Enter the electricity consumption in KWh corresponding to the start and end date.
Tab 5 – Natural Gas Data
Provide the annual natural gas consumption for the building (if a stand-alone data center) or the submetered data center. You can provide this as one value for the year or as a series of meter/energy bill entries that cover the entire year.
Meter ID | Enter a distinguishing name or number for each meter.
Start Date | For each energy use value, enter a start and end date. You can provide an entry for each bill or one entry for the entire year.
End Date
Natural Gas Consumption | Enter the natural gas consumption corresponding to the start and end date.
Energy Units | Please enter the corresponding units for the natural gas consumption figure (i.e. therms, ccf, Mcf).
Tab 6 – Other Energy Sources
For each fuel type and other sources of energy (i.e. diesel fuel, steam, chilled water, solar) provide the annual energy consumption for the building (if a stand-alone data center) or the submetered data center. You can provide this as one value for the year or as a series of meter/energy bill entries that cover the entire year. NOTE: Stand-by generator diesel fuel used less than 200 hours per year should not be included.
Fuel Type/Other Energy Source | Please enter the type of energy that the following data represents.
Meter ID | Enter a distinguishing name or number for each meter.
Start Date | For each energy use value, enter a start and end date. You can provide an entry for each bill or one entry for the entire year.
End Date
Energy Consumption | Enter the energy consumption corresponding to the start and end date.
Energy Units | Please enter the corresponding units for the energy consumption figure (i.e. gallons, therms, Kbtu, Mbtu, lbs, ton hours).
Tab 7 – Optional Elements (To be used for future study purposes) |  | Include a separate tab for optional information i.e. supplemental information for future research
Year Constructed | Enter the 4 digit year the building was built.
HVAC "Economizer Cycle" Control Strategy | Does the building utilize an HVAC "economizer cycle" control strategy? Yes or no?
Water-side or Air-side Economizer Cycle? | If yes on "economizer cycle" is this on the water-side or air-side? Please select between the following: 1 = water-side, 2 = air-side
Does the building incorporate peak shaving, demand response, thermal storage or co-generation in its operations? | Does the building incorporate peak shaving, demand response, thermal storage or co-generation in its operations? Please select all operations/strategies that apply.
Percentage of Average IT Utilization | What is the current "average" IT processing load as a percentage of the total server processor capacity? Enter this percentage as one average calculation for the entire year.
Percentage of Peak IT Utilization | What is the current "peak" IT processing load as a percentage of the total server processor capacity? Enter this percentage as one average calculation for the entire year.
Mechanical System Type | Please select the type of mechanical system used for cooling the data center: 1 = Direct Expansion; 2 = Chilled Water; 3 = Condenser; 4 = Other
Liquid-Cooled IT Equipment/Racks | Please check the box if the data center employs liquid cooling for IT equipment and/or racks.
Air Management Techniques | Please check off all of the following air management techniques that are in operation at the data center: Blanking Plates in Racks Hot Aisle/Cold Aisle Equipment CFD Modeling High Delta "T" Cooling Air Separation Chambers Racks with Air Management Control Static Pressure Control Static Pressure Boundaries Dynamically Managed Air-Flow
Operating Set Points | Please check off all of the following operational practices employed at the data center: New ASHRAE Humidity Set Points; Dynamic Temperature Change; Automatic Chiller Water Reset
Additional Comments | If you have any additional comments or explanations about a data center included in this form, please enter it here (see box below table).

## FAQs
Frequently Asked Questions (FAQ)
Review the additional information for select questions below. If you need further clarification, email your questions to: ENERGYSTARDatacenters@icfi.com
Tab 1 - Building Information
Type of Data Center
1 - Traditional Enterprise: Processes data requirements for data center owner 2 - On Demand Enterprise: Processes and expands data processing capacity, when needed, for numerous customers (this would include batch processing and manufacturing type data processing facilities) 3 - Telecom: Telecom Switching Center 4 - High Performance Computing: Scientific and high density data processing 5 - Hosting: Sells data processing services to numerous Customers 6 - Internet: Provides high capacity processing for large numbers of web clients 7 - Hybrid: Combination of two or more of the above
Tab 2 – Data Center Operations
UPS Utilization
There are various configurations of UPS support. Some of the redundancy of the UPS system design will be indicated by the Tier Level already collected in the data elements. Efficiency is also affected by the load on the UPS system (a lightly loaded UPS is less efficient than a system operation in the peak efficiency above 90% - depending on the system manufacture). The formal definition of the % of UPS capacity is the amount of critical load compared with the redundant capacity of the system. For illustrative purposes, examples of the utilization calculation could be any of the following:
Example # 1 Tier One Stand-Alone UPS (No redundancy): The percent of utilization would be calculated by noting a fully loaded UPS should not exceed 85% of the rated capacity - for transients harmonic and temporary loads with equipment swap. Therefore the percent utilization calculation in this example is a 500 kVA unit has 425 kVA of capacity (85%) and a 150 kVA IT load on this unit would represent a 35.3% loaded unit. (150 / 500 x 0.85 = 35.3%)
Example # 2 Tier Two N+1 Redundant UPS: The percent of utilization in this example would be noted as a three module 500 kVA UPS system (three modules of 500 + 500 + 500 = 1000 kVA (plus a redundant module)) since all modules share load and 1500 kVA will be on line a full 850 kVA of capacity of redundant system. A 150 kVA IT load in this system would NOT be 10% of 1500 kVA installed but 17.6% of system utilization (150 / (1500 - 500 (redundant module) X 0.85 = 17.6%). The "normal-mode" UPS loading of each module is 150 / 1500 = 10%, but the system is utilized to 17.6%.
Example # 3 Tier Three N+N UPS modules: The percent utilization would be calculated be noting the redundant UPS (N) system will not need a de-ration factor of 85% since the system will share load between the "A & B" side UPS systems. In this example the systems would be configured in two 500 kVA modulate (1000 kVA - "A") + two additional 500 kVA modules ( 1000 kVA - "B") for a total installed 2000 kVA of UPS modules. This configuration can support 850 kVA redundant load while being fully maintained on the "A" side, while the "B" side is supporting the load (concurrent maintainability). The load calculation for 150 kVA of IT load is ( 150 / (2000 - 1000 (redundant N system)) x .85 = 17.6%). The "normal-mode" UPS load shared across all modules would be 7.5% each but the system utilization in the redundant configuration would still be 17.6% loaded.
Example # 4 Tier Four N+1 + N+1 UPS System: The difference between Tier Three and Tier Four configurations is the redundant module to offer redundancy when the system is in the maintenance mode. If the total load was being supported by the "A" side while the "B" side is being maintained, the "A-side +1" module will still be in reserve for a module failure. In this example the modules installed would be three 500 kVA modules (N+1) for the "A" side and three 500 Kva modules for the "B" side UPS and a system redundant capacity of 1000 kVA. Since each system has reserve when supporting the total load, the 85% de-rating factor is not necessary. Therefore the utilization load for this configuration is [ 150 / (3000 - (1500 (redundant system) + 500 (redundant second system module))] = (150 / 1000 ) = 15.0%
Chiller Utilization
These three elements (total capacity for cooling, annual chiller runtime, and average chiller demand) will be factored into an equation to determine the total IT load being cooled compared to the chiller capacity.
Tab 3 – IT Measurement
Total IT Plug Energy
In general the calculation is attempting to capture the energy used by the IT equipment (this will include the IT equipment fan systems and all other devices: KVM, cabinet monitoring and cabinet circulation fans) that are connected into the plug strip serving the computer room. If the UPS system is only providing load to the computer equipment in the data center, and NOT providing Computer room fans, pumps, telecommunication closets and desktop services outside the data center, then the UPS readings – over time can be recorded. The best case in this circumstance is to read a KWH meter at approximately the same period and frequency as the utility meter for the building. If a KWH meter is not available on the UPS then the instantaneous meter reading can be measured on a periodic basis to predict how load on the UPS changes with the data center processing load. A comparison with the known processing peak and the lowest utilization would be good times to record instantaneous meter readings to capture the range of UPS output. If it is greater than 5%, a more detailed (greater frequency) of recording would be used to estimate the total KWH provided by the UPS over time.
Tab 6 – Other Energy Sources
Generally these systems provide maintenance start-up testing and battery re-fresh run-time exercise cycles that do not sustain actual data center operations for extended periods (defined as less than 200 hours per year). Since the on-line status is not significant you can ignore the make-up diesel fuel as a captured energy source.
Tab 7 - Optional Elements
Does the building utilize an HVAC "economizer cycle" control strategy?
“Economizer Cycle” is a mechanical device that uses any type of system that eliminates the mechanical refrigeration cycle by using outside atmosphere to cool the interior spaces that are normally cooled by an energy intensive refrigerant system. These would include free cooling with economy coils using cooled water from the cooling tower or dry coolers, replacement air used directly from the outside (with exhaust air being flushed to the outside), or a heat exchanger process that transfers heat to the atmosphere without the use of a mechanical input to change a refrigerant state.
If yes on "economizer cycle" is this on the water-side or air-side?
A “Water-side” economizer cycle uses water as the key fluid in the transfer of heat to the atmosphere and does not introduce a large quantity of outside air directly into cooled interior spaces. Usually coils and/or heat exchangers are used with these types of systems.
An “Air-side” economizer cycle generally uses the induction of outside air (when conditions of that air can cool) for the direct conditioning of the space. There is a need to monitor humidity and contaminates when this type of cooling is provided with attention to filtering and the moisture content of the air.
Does the building incorporate peak shaving, demand response, thermal storage or co-generation in its operations?
Peak shaving is a technique that stores heating or cooling generated in an alternate (cheaper cost) time of day to be used when the utility system is experiencing a high demand on their system and charges customers for energy use at a higher cost during that period. The shaving provides the utility with higher system utilization and less capacity peaks – they typically provide customers with a reduced rate of cost for this benefit. Systems can include chilled water storage, ice storage, heated material, solar heated storage and other processes. The utility rate reduction may lower total utility cost, but total energy usage is generally displaced but not reduced with these systems.
Demand response (partial) and co-generation (continuous) processes provide removal of utility load from the utility when their system is stressed. For the ability to temporarily remove or self-generate power, the utility will typically provide a reduced utility rate. These processes may or may not save total energy used.
The ENERGY STAR data collection effort is interested in large energy input to the data center. If the peak shaving, demand response and storage processes do not save energy and are primarily used for utility cost reduction, the effect on an energy rating will be minimal on the calculated rating. Co-generation however would by its continuous nature use a large quantity of energy and therefore would need to be included in the “other energy” tab 6&7 collection.
Percentage of Average IT Utilization
Typically the data center monitors the processor, network and storage processes that occur in the data center. There are peaks in production that when reached, tend to determine if additional processing equipment is required to support the data center applications. The active measurement of the IT equipment is usually automated and monitored. What it being asked in this data element is not the peak, but the average estimate over time of the IT equipment’s utilization (compared to the processor being 100% utilized). It is a value that currently will not affect the index but is the first step in data capture that will allow correlation the actual IT processing work with efficiency. Although there is no standard to measure IT work being processed with energy input, this one measurement of the processor activity verses a dormant state will provide an estimation of the potential for energy saving features, if activated, that could achieve even better efficiencies.
Percentage of Peak IT Utilization
If the console operator can run their capacity or processor monitoring programs, the peak utilization is used for alerting management when more IT equipment is necessary to sustain business application processing. Since this is measured in most data centers, the historical capture should be accurate. The reason for this data element is to provide an understanding of the maximum equipment that will be necessary for peak periods and then, depending on the variability of the enterprise processing needs, be dormant during the non-peak times. By understanding the peak and average utilization characteristics of the data center, analysis with the tracking of input energy and the extent of dormant equipment sitting in reserve for the peak. If these processes are tracked for the data center, the use of devices that can slow down processor clock speed and turn off redundant processors can then be estimated. These concepts are the start of understanding IT work efficiency. For where the data is captured, ask your console operator or check the measurement in the IT utility program available in the processor equipment.

## Tab 1 - Building Information
Tab 1 - Building Information
Data Center Name / ID | Zip Code | Type of Data Center | Type of Building | Building Square Footage | Data Center Square Footage | Building Earned the ENERGY STAR? | Building LEED Rated?
Example #1 | 21045 | 1 - Traditional Enterprise | 1 - Stand-Alone | 36000 | 21600 | No | No
Note on A2: Please provide a unique name or number for each data center. Make sure to use the same identifier on each tab!
Note on C2: Please select one of the seven types of data centers.
Note on D2: Please select one of the two building types.
Note on B2: Please provide the five-digit zip code for each data center's location.
Note on H2: Please select whether the building has received USGBC's LEED certification.
Note on F2: Please provide the square footage of the data center space, including all space that directly supports the operation of the data center
Note on G2: Please select whether the building that houses the data center has earned the ENERGY STAR.

## Tab 2 - Data Center Operations
Tab 2 - Data Center Operations
Data Center Name / ID | Reliability (Tier Level) | Number of Racks | UPS Utilization (%) | Total Capacity for Cooling (tons) | Annual Chiller Runtime (hours) | Average Chiller Demand (KW)
Example #1 | Tier II | 420 | 60% | 950 | 8760 | 550
Note on A2: Please provide a unique name or number for each data center. Make sure to use the same identifier on each tab!
Note on B2: Select one of the four tiers of reliability based on Uptime Institute's classificaiton system.
Note on E2: Please provide the data center's total capacity for cooling.
Note on G2: Enter the average chiller demand.
Note on C2: Provide the number of racks that are usually in operation.
Note on D2: Please enter the amount of critical load compared to the redundant capacity of the UPS as a percentage
Note on F2: Provide the annual runtime for the chillers.

## Tab 3 - IT Measurement
Tab 3 - IT Measurement
Data Center Name / ID | Total IT Plug Energy from UPS Meter (KWh) | Start Date (MM/DD/YYYY) | End Date (MM/DD/YYYY) | Total IT Plug Energy from PDU Meter (KWh) If Available | Start Date (MM/DD/YYYY) | End Date (MM/DD/YYYY)
Example #1 | 1824270 | 2008-02-21 | 2008-03-20 | 1806028 | 2008-02-21 | 2008-03-20
Example #1 | 1814000 | 2008-01-21 | 2008-02-20 | 1795860 | 2008-01-21 | 2008-02-20
Example #1 | 1723300 | 2007-12-21 | 2008-01-20 | 1706067 | 2007-12-21 | 2008-01-20
Example #1 | 1723278 | 2007-11-21 | 2007-12-20 | 1706045 | 2007-11-21 | 2007-12-20
Example #1 | 1723222 | 2007-10-21 | 2007-11-20 | 1705990 | 2007-10-21 | 2007-11-20
Example #1 | 1723168 | 2007-09-21 | 2007-10-20 | 1705936 | 2007-09-21 | 2007-10-20
Example #1 | 1723111 | 2007-08-21 | 2007-09-20 | 1705880 | 2007-08-21 | 2007-09-20
Example #1 | 1723056 | 2007-07-21 | 2007-08-20 | 1705825 | 2007-07-21 | 2007-08-20
Example #1 | 1723000 | 2007-06-21 | 2007-07-20 | 1705770 | 2007-06-21 | 2007-07-20
Example #1 | 1722944 | 2007-05-21 | 2007-06-20 | 1705715 | 2007-05-21 | 2007-06-20
Example #1 | 1722889 | 2007-04-21 | 2007-05-20 | 1705660 | 2007-04-21 | 2007-05-20
Example #1 | 1722833 | 2007-03-21 | 2007-04-20 | 1705605 | 2007-03-21 | 2007-04-20
Note on A2: Please provide a unique name or number for each data center. Make sure to use the same identifier on each tab!
Note on B2: Enter the annual total IT plug energy from the output of a UPS meter.
Note on E2: Enter the annual total IT plug energy from the input of the PDU meter, if available.

## Tab 4 - Electricity Data
Tab 4 - Electricity Data
Data Center Name / ID | Meter ID | Start Date (MM/DD/YYYY) | End Date (MM/DD/YYYY) | Electricity Consumption (KWh)
Example #1 | Electric 45389 | 2008-02-21 | 2008-03-20 | 3283686
Example #1 | Electric 45389 | 2008-01-21 | 2008-02-20 | 3265200
Example #1 | Electric 45389 | 2007-12-21 | 2008-01-20 | 3102000
Example #1 | Electric 45389 | 2007-11-21 | 2007-12-20 | 3101900
Example #1 | Electric 45389 | 2007-10-21 | 2007-11-20 | 3101800
Example #1 | Electric 45389 | 2007-09-21 | 2007-10-20 | 3101700
Example #1 | Electric 45389 | 2007-08-21 | 2007-09-20 | 3101600
Example #1 | Electric 45389 | 2007-07-21 | 2007-08-20 | 3101500
Example #1 | Electric 45389 | 2007-06-21 | 2007-07-20 | 3101400
Example #1 | Electric 45389 | 2007-05-21 | 2007-06-20 | 3101300
Example #1 | Electric 45389 | 2007-04-21 | 2007-05-20 | 3101200
Example #1 | Electric 45389 | 2007-03-21 | 2007-04-20 | 3101100
Note on A2: Please provide a unique name or number for each data center. Make sure to use the same identifier on each tab!
Note on E2: Please enter the building's electricity consumption.

## Tab 5 - Natural Gas Data
Tab 5 - Natural Gas Data
Data Center Name / ID | Meter ID | Start Date (MM/DD/YYYY) | End Date (MM/DD/YYYY) | Natural Gas Consumption | Energy Units
Example #1 | Gas 2624 | 2008-02-05 | 2008-03-04 | 7715 | therms
Example #1 | Gas 2624 | 2008-01-05 | 2008-02-04 | 8000 | therms
Example #1 | Gas 2624 | 2007-12-05 | 2008-01-04 | 2700 | therms
Example #1 | Gas 2624 | 2007-11-05 | 2007-12-04 | 2500 | therms
Example #1 | Gas 2624 | 2007-10-05 | 2007-11-04 | 2300 | therms
Example #1 | Gas 2624 | 2007-09-05 | 2007-10-04 | 2200 | therms
Example #1 | Gas 2624 | 2007-08-05 | 2007-09-04 | 1800 | therms
Example #1 | Gas 2624 | 2007-07-05 | 2007-08-04 | 1750 | therms
Example #1 | Gas 2624 | 2007-06-05 | 2007-07-04 | 1900 | therms
Example #1 | Gas 2624 | 2007-05-05 | 2007-06-04 | 2100 | therms
Example #1 | Gas 2624 | 2007-04-05 | 2007-05-04 | 2400 | therms
Example #1 | Gas 2624 | 2007-03-05 | 2007-04-04 | 2600 | therms
Note on A2: Please provide a unique name or number for each data center. Make sure to use the same identifier on each tab!
Note on E2: Please provide the building's annual natural gas consumption
Note on F2: Provide the unit of measurement for the gas consumption (i.e. therms, ccf)

## Tab 6 - Other Energy Sources
Tab 6 - Other Energy Sources
Data Center Name / ID | Fuel Type/ Other Energy Source | Meter ID | Start Date (MM/DD/YYYY) | End Date (MM/DD/YYYY) | Energy Consumption | Energy Units
Example #1 | N/A
Note on A2: Please provide a unique name or number for each data center. Make sure to use the same identifier on each tab!
Note on B2: Please provide the type of metered energy source.
Note on F2: Please provide the building's consumption of this energy source.
Note on G2: Please provide the unit of measurment for this energy source.

## Tab 7 - Optional Elements
Tab 7 - Optional Elements
Data Center Name / ID | Year Constructed | HVAC "Economizer Cycle" Control Strategy? | Water-side or Air-side Economizer Cycle? | Does the building incorporate peak shaving, demand response, thermal storage, or co-generation in its operations? | Percentage of Average IT Utilization | Percentage of Peak IT Utilization | Mechanical System Type |  |  | Air Management Techniques | [8 empty] | Operating Set Points
[8 empty] | Liquid-Cooled IT Equipment/Racks | Blanking Plates in Racks | Hot Aisle/ Cold Aisle Equipment | CFD Modeling | High-Delta "T" Cooling | Air Separation Chambers | Racks with Air Mgmt Control | Static Pressure Control | Static Pressure Boundaries | Dynamically Managed Air-Flow | New ASHRAE Humidity Set Pts. | Dynamic Temp. Change | Automatic Chiler Water Reset
Example #1 | 1998 | No |  |  | 63% | 76% | 2 = Chilled Water
Additional Comments:
Note on A2: Please provide a unique name or number for each data center. Make sure to use the same identifier on each tab!

## Lists (hidden)
1 - Traditional Enterprise | 1 - Stand-Alone | Yes | Yes | Yes | Water-Side | Peak Shaving | Tier I | UPS Meter | January | 1 = Direct Expansion
2 - On-Demand Enterprise | 2 - Enclosed in a Larger Building | No | No | No | Air-Side | Demand Response | Tier II | PDU Meter | February | 2 = Chilled Water
3 - Telecom | [5 empty] | Thermal Storage | Tier III |  | March | 3 = Condenser
4 - HPCC (Scientific) | [5 empty] | Co-generation | Tier IV |  | April | 4 = Other
5 - Hosting | [8 empty] | May
6 - Internet | [8 empty] | June
7 - Hybrid | [8 empty] | July
August
September
October
November
December