### 5.2.11		Cryogenic System

#### 5.2.11.1	Cryogenic System Description

The magnet’s superconducting transmission line is cooled by pressurized supercritical helium at 4.5-6.0 K. The heat load of the magnet system is removed by the sensible heat of the supercritical helium stream.  The fluid operates just outside the critical region expanding the helium stream as it passes through the transmission line producing a large effective heat capacity.  Cryogens are fed from six (6) refrigerator plants spaced at 38 km intervals around the ring.

Figure 1.

For efficiency reasons, refrigeration is provided at two (2) temperature levels.  Refrigeration at a higher temperature (40 K) provides cooling for a heat shield that is used to intercept much of the heat that would otherwise be absorbed by the lower temperature superconductor. Each plant provides refrigeration for upstream and downstream magnet streams.  Each string is sub-divided into two (2) loops, referred to as “near” and “far” loops.

Figure 2.

##### 5.2.11.1.1	Helium Distribution System

The helium distribution system is designed to distribute refrigeration to the magnet system with a minimal temperature variation.  The distribution system consists of cryogenic valve boxes, transfer lines, and warm helium header.

###### (a)	Cryogenic Valve Boxes

Cryogenic valve boxes are used to redistribute the helium between the conductor loops for steady-state operation and perform various transient state operations.  These boxes are located every 9.5 km and house the control valves and instrumentation required for each circuit.  Boxes vary in configuration dependent upon location in the magnet string.  It is believed these boxes are relatively simple devices mainly providing a transition for flow redistribution.

###### (b)	Transfer Lines

Transfer lines are a part of the magnet assembly.  A line contains five (5) circuits:  4.5 K superconductor supply line (near loop only), 6.0 K superconductor return line, 40 K shield supply line, 70 K shield return line, and a vacuum circuit.  Each section of transfer line is equal in length to a magnet (67.5 meters) and is attached to the magnet assembly via a structural anchor at the midpoint of the magnet.

The 70 K return line is a 3 IPS stainless steel pipe connected to an extruded aluminum shield that surrounds all the inner lines.  The shield is wrapped with a double-sided aluminized mylar (dimpled and perforated).  The longitudinal contraction of the line is compensated with guided formed bellows in the inner connect. During this shrinkage, the G10 support structure is allowed to move within the vacuum space.

The 40 K shield supply line is a 2 1/2 IPS stainless steel pipe supported on the G10 spiders from the aluminum shield.  Bellows are used at the end of each 67.5 m module to compensate for thermal contraction and expansion.

The 4.5 K supply – near loop only – and 6.5 K superconductor return line are Invar tubes which are also anchored at the midpoint of the module.  These lines are a concentric design. The 6.5 K helium flows between two (2) concentric Invar tubes.

The 4.5 K supply line is suspended via G10 spiders from a 6.5 K inner line.

##### 5.2.11.1.2	Helium Pressure Relief and Venting System

Relief valves for each of the five (5) circuits are located every 540 meters.  These valves will vent into the warm helium header that is itself protected every 1 km at 3 MPa (30.4 bar) from over pressurizing.  Each relief is conventional in nature and set to the correct pressure setting of its given circuit.   The primary need for these reliefs are for trapped volume and loss of insulating vacuum scenarios.  The warm header is further protected at the refrigerator (above ground) at a set pressure of 0.2 MPa (2 bar), venting to atmosphere.

Figure 3.

Quench protection of the transmission line is discussed in [1,2].  The 100 kA transmission line conductor contains enough copper that it can be safely shut down with a 1 second time constant following a quench.  A number of detailed quench simulations have been performed [3]. The peak temperature is ~250 K.  The worst-case peak pressure comes from a situation in which a mis-steered beam (kicker misfire) causes the beam to oscillate side-to-side in the beam pipe and scrape heavily in a series of locations separated by a half-betatron wavelength.  In this case the peak temperature is unaffected, but a worst-case pressure occurs when the hydrodynamic shock waves from two adjacent quenches collide at the midpoint between quenches.  The peak pressure is below the 4.1 MPa (40 Bar) pressure rating of the transmission line.  Thus no helium needs be vented anywhere, even for a long period following the quench.  The pressure burst from the hydrodynamic shock wave, as registered on pressure sensors along the transmission line, could provide a convenient method of identifying where the quench occurred.

##### 5.2.11.1.3	Heat Shield Cooling System

Pressurized 40 K helium is used to intercept the radiation and conduction heat leak to the transmission line.  Helium is supplied from the refrigerator at 1.72 MPa (17 bar) and returns at  < 70 K and 1.62 MPa (16 bar).  Flow is supplied via a 3.5” O.D. tube and distributed via a pair of 0.25-inch lines every 270 meters carrying 2.0 g/sec.  This scheme provides shield cooling for every two magnets.  Control valves and temperature sensors are included every 270 meters for heat shield flow control based on temperature requirements.

##### 5.2.11.1.4	Transmission Line Heat Load Estimates

Transmission line heat load estimates are divided into two (2) components:  the primary heat load on the 4.5 K system and the heat load to the 40 K shield system.  The calculated heat loads are presented in Table 1.

##### 5.2.11.1.5	Power Lead Cooling

Due to its low inductance (3 H/m) and low stored energy (15 kJ/m), the transmission line magnets require only a single 50 V power supply and a single set of 100 kA current leads for the entire machine.  If these are conventional (gas-cooled metal) leads, the helium consumption will be 5 g/s for each lead. If desired, this power requirement can be reduced by a factor of 4~5 with the use of High Temperature Superconductor (HTS) current leads.

#### 5.2.11.2	Refrigeration System

The refrigeration system is composed of six (6), 4.5 kW @ 4.5 K capacity facilities equally spaced around the ring. Each facility will also provide 80 kW of 40 K refrigeration used in the shielding of the magnet system.  This provides approximately a 50% margin above expected steady state requirements.  This margin is required to ensure continued operation when the heat load increases either due to events such as a magnet quench or vacuum leak, or because refrigeration capacity falls below its intended design value (i.e. decreasing machine efficiency or inefficient heat transfer due to contamination).  With this scheme, all six refrigerators must be operational for the accelerator to function.   No plant redundancy is built into this design.

Figure 4.

The process helium is compressed from suction pressure of 0.111 MPa (1.01 bar) up to an intermediate pressure of 0.41 MPa (4.0 bar) by means of first stage compressor discharging into a second stage, which compress the helium to 1.88 MPa (18.5 bar). Turbo machinery is used for the refrigeration plants while reciprocating machines comprise the compressor system. There are two cold boxes: the upper and lower cold boxes.  A cold box contains five (5) plate-and-fin type heat exchangers and three expanders.  To avoid return helium gas instabilities due to the elevation change from the tunnel to the surface, the lower cold box will be located at the tunnel level.  This requires a dedicated space of 16,000 cubic feet (20' along the beam by 20' transverse by 40' high) located near the accelerator tunnel.

These plants are well within the existing commercial vendor capabilities.  These plants contain no nitrogen pre-cooling. The cold configuration is a horizontal carbon steel shell enclosure housing all heat exchangers, piping, valves, cold end of turbo expanders and vessels operating at cryogenic temperatures. The equipment within the cold box and the inner face of the vacuum jacket are covered by multilayer aluminized Mylar. The cold boxes are designed to withstand the outside atmospheric pressure while they are evacuated and are also protected against overpressure by safety valves. All internal valves, filters, turbo expanders, bayonets and major pipe connections are fixed at the top plate and are accessible from a structural steel platform along the length of the cold box. The turbo expanders are self activated gas bearing, superior in their performance to oil bearing turbines. Each turbo expander is a small single-stage centrifugal turbine braked by a direct-coupled, single stage centrifugal compressor. The turbine housing is vertically mounted to a plate at the cold box top, projecting into its vacuum space. Within the cold box are brazed aluminum heat exchangers, pressure vessels containing and adsorbent to remove impurities and the cold end of gas bearing turbo expanders.  Part of the outer shell cover is flanged and has an O ring seal, and can be moved away on wheels, for complete access to all cold box internal components and piping. Two cold box panels will be mounted on the structural steel platform next to the cold box. One containing all instrument terminations and transmitters, and the other an assembly of purge and defrost valves. Provisions for purification of the process helium will be provided at each plant as will oil removal systems. A commercial control system package will permit the unattended operation of these plants.

##### 5.2.11.2.1	Helium Compressor System

The compression package will consist of three oil flooded rotating screw compressors. One compressor will compress from 0.111 MPa (1.1 bar) to 0.4 MPa (4.0 bar), and the two other will compress in parallel from 0.4 MPa (4.0 bar) to 1.88 MPa (18.5 bar). The first stage compressor is smaller than the two (2) second stage machines. Each compressor skid contains the compressor, main drive motor, oil reservoir/separator vessel, and lubrication system mounted on a common rigid skid base. The base plate provided is suitable for installation on a flat pad without grouting. The helium enters the compressor and is compressed through the rotating screw compressor, also flooded with oil.  The oil seals the rotor and absorbs some heat of compression. The compressed warm helium passes through a water-cooled heat exchanger and then into a bulk oil separator. The oil is also passed through a separate water-cooled heat exchanger. Each compressor is direct driven by an electric induction electric motor. The compressor assemblies are equipped with automatic inlet and outlet block valves and automatic recycle valves.

The high-pressure helium from the compressors passes through a skid mounted oil removal system. The oil removal system consists of three stages of coalescing filter housings followed by a vessel containing activated carbon. All entrained oil is filtered out of the gas stream by the three stages of filters. The small amount of oil in the vapor phase is removed by the activated carbon. The total amount of oil contained in the helium leaving the oil removal assembly is less than 10 ppb (w/w).

##### 5.2.11.2.2	Helium Liquid and Gas Storage and Inventory Management

##### 5.2.11.2.3	Cryogenic Control System

#### 5.2.11.3	Design Operating Conditions

##### 5.2.11.3.1	Steady State

Helium is supplied from a refrigerator at 4.5 K, 0.4 MPa (4 bar) and returned at 5.8 K, 0.19 MPa (1.9 bar). Supercritical supply helium is fed from the helium plant to four parallel loops.  Each loop is comprised of 9.5 km of magnet and transmission line.  There are cryogenic connecting boxes at the beginning and end of each 9.5 km section.  At the exit of the refrigerator the helium process is split into four (4) paths.  There are upstream and downstream magnet strings that are mirror images of each other. The typical flow schematic of a magnet string is shown in Figure ?.    As helium enters the upstream or downstream magnet strings the flow is split into two parts:  half enters the 4.5 K transmission line circuit (for the near loop) and half enters the 4.5 K current return circuit contained in the magnet (for the far loop). There is expected to be an approximately 1 K gradient across each loop. These loop flows are then re-distributed at valve boxes and become the return 6.0 K shield flow.

The cooling scheme relies on a balance between heat leak and pressure drop.  Any scenario causing an upset in the heat load (i.e. vacuum degradation) can be compensated by increasing the helium flow rate and supply pressure for the proper loop.  The refrigerator has been oversized by 50% to compensate for these types of upset conditions.

Figure 5.					Figure 6.

##### 5.2.11.3.2	System-Wide Purification

Purification of this machine will be done in two (2) steps.  First each sector will be pumped and backfilled five (5) times to 25 inches of mercury via pump outs on every helium circuit at each valve box located every 10 km.  This method has been proven to work in the Tevatron.  Levels of contamination less than 100 ppmv are achieved with this first step by using roughing pumps.  The second step is dilution purification.  A purifier with a nitrogen cooled charcoal bed will be located at each refrigeration plant.  The discharge gas of the compressor system will be circulated through this purifier and then will be distributed to the magnet/transmission line system.  Contamination instrumentation, such as arc cells used on the Tevatron, will be used to monitor the ppmv levels in each sector.  The system will be ready for cool down when contamination levels are < 5 ppm.  It is estimated that the purification for a sector in the VLHC will be 72 hours.

##### 5.2.11.3.3	System-Wide Cool down

Cool down of the VLHC will be done in three (3) stages.  The first stage involves the cool down of the helium plants.  The second stage is the cool down of the transmission line to 40 K.  Finally the transmission line will be cooled done to operating temperatures.

In the first stage, cooling is provided by turbines and should not take more than 24 hours per plant.  In the second stage, the plant is setup in the liquefaction mode and 40 K gas at 0.4 MPa (4 bar) is sent via cool down valves located at each valve box back to the compressor suction warm gas header located in the tunnel.  Gas flows from the refrigerator into the warm header through the near loop transmission line, the 6.5 K return, and the current return circuits.  When the temperature at the end of the “near” loop (measured at the valve box) is 70 K the flow is then re-directed to the “far” loop and into the return header.  As the “far” loop temperature reaches 70 K the second cooldown stage can be started.

During the second cool down stage the plant is re-tuned for an outlet temperature of 4.5 K.  The flow pattern for the second stage is the same as the first stage.  As the temperature for each loop is at 7 K the cool down valves can be closed and the flow will be looped back in refrigerator mode.

Total cool down time is expected to be on the order of 10 days.

References

[1] Koepke et al.

[2] DR doc

[3] N. Shatil final report

# Footnotes

current file: Q:\VLHC\TDDoc\DesignStudyReport\05_Stage1_components\Draft2.1\5.2.11_Cryo Update draft 26 Mar_ed010328.doc