## 152 Calculation
Draft ASHRAE standard 152 duct efficiency calculations
2003-01-01 |  | modified by PRC (location index and lookup values) July 2003
INPUT PARAMETERS |  |  | CALCULATED PARAMETERS
| Value used in calculation | Notes
Location Index | 149 | Cleveland, OH
Conditioned floor area, (ft^2) | 1761
Number of Stories | 2
Number of return Registers | 3 |  | Ground Temperature for basements, and slabs | 46
House Volume, (ft^3) | 14440.2 | has a default of 8.2*Floor Area
Supply Duct Surface Area, (ft^2) | 356.6025 | has default equation | Fraction of supply duct outside conditioned space | #VALUE!
Return Duct Surface Area, (ft^2) | 198.1125 | has default equation | Fraction of return duct outside conditioned space | 1
Fraction of supply duct in attic | 1 |  | Design Supply Duct Zone temperature, Heating, (F) | #VALUE! | Design Temp. diff for supply, dTs, heating | #VALUE!
Fraction of supply duct in garage | 0 |  | Seasonal Supply Duct Zone temperature, Heating, (F) | #VALUE! | Seasonal Temp. diff for supply, dTs, heating | #VALUE!
Fraction of supply duct in unvented & uninsulated crawlspace | 0 |  | Design Return Duct Zone temperature, Heating, (F) | #VALUE! | Design Temp. diff for return, dTr, heating | #VALUE!
Fraction of supply duct in unvented crawlspace with insulated building floor and crawlspace walls | 0 |  | Seasonal Return Duct Zone temperature, Heating, (F+D26) | #VALUE! | Seasonal Temp. diff for return, dTr, heating | #VALUE!
Fraction of supply duct in unvented crawlspace with insulated building floor | 0 |  | Design Supply Duct Zone temperature, Cooling, (C) | #VALUE! | Design Temp. diff for supply, dTs, cooling | #VALUE!
Fraction of supply duct in Vented & uninsulated crawlspace | 0 |  | Seasonal Supply Duct Zone temperature, Cooling, (C) | #VALUE! | Seasonal Temp. diff for supply, dTs, cooling | #VALUE!
Fraction of supply duct in Vented crawlspace with insulated building floor and crawlspace walls | 0 |  | Design Return Duct Zone temperature, Cooling, (C) | 108 | Design Temp. diff for return, dTr, cooling | -30 | 108
Fraction of supply duct in Vented crawlspace with insulated building floor | 0 |  | Seasonal Return Duct Zone temperature, Cooling, (C) | #VALUE! | Seasonal Temp. diff for return, dTr, cooling | #VALUE! | #VALUE!
Fraction of supply duct in uninsulated basement | 0 |  | Design Supply Duct Zone Enthalpy, Cooling, (Btu/lbF) | #VALUE!
Fraction of supply duct in basement with insulated walls | 0 |  | Seasonal Supply Duct Zone Enthalpy, Cooling, (Btu/lbF) | #VALUE!
Fraction of supply duct in basement with insulated ceiling | 0 |  | Design Return Duct Zone Enthalpy, Cooling, (Btu/lbF) | 40.6691 |  |  | 40.6691
Fraction of supply duct under slab | 0 |  | Seasonal Return Duct Zone Enthalpy, Cooling, (Btu/lbF) | #VALUE! |  |  | #VALUE!
Fraction of supply duct in exterior walls | 0 |  | Fcycloss | #VALUE!
Fraction of return duct in attic | 1
Fraction of return duct in garage | 0 |  | Infiltration, Fan off, cfm | 84.2345
Fraction of return duct in unvented & uninsulated crawlspace | 0 |  | HIGH SPEED: |  |  | LOW SPEED:
Fraction of return duct in unvented crawlspace with insulated building floor and crawlspace walls | 0 |  | Heating as | 0.9 |  | Heating as | #DIV/0!
Fraction of return duct in unvented crawlspace with insulated building floor | 0 |  | Heating, ar | 0.9 |  | Heating, ar | #DIV/0!
Fraction of return duct in Vented & uninsulated crawlspace | 0 |  | Cooling as | 0.9 |  | Cooling as | #DIV/0!
Fraction of return duct in Vented crawlspace with insulated building floor and crawlspace walls | 0 |  | Cooling ar | 0.9 |  | Cooling ar | #DIV/0!
Fraction of return duct in Vented crawlspace with insulated building floor | 0 |  | Temperature change across heat exchanger, dTe, heating | 61.7284 |  | Temperature change across heat exchanger, dTe, heating, low capacity | #DIV/0!
Fraction of return duct in uninsulated basement | 0 |  | Temperature change across heat exchanger, dTe, cooling | -27.7778 |  | Temperature change across heat exchanger, dTe, cooling, low capacity | #DIV/0!
Fraction of return duct in basement with insulated walls | 0 |  | Heating, Bs | #VALUE! |  | Heating, Bs | #VALUE!
Fraction of return duct in basement with insulated ceiling | 0 |  | Heating, Br | 0.9713 |  | Heating, Br | #DIV/0!
Fraction of return duct under slab | 0 |  | Cooling, Bs | #VALUE! |  | Cooling, Bs | #VALUE!
Fraction of return duct in exterior walls | 0 |  | Cooling, Br | 0.96426 |  | Cooling, Br | #DIV/0!
Supply Duct R value(hft^2F/Btu) | 4.2 |  | Imbalance Flow, Heating, (cfm) | 0 |  | Imbalance Flow, Heating, (cfm) | 0
Return Duct R value(hft^2F/Btu) | 4.2 |  | Imbalance Flow, Cooling, (cfm) | 0 |  | Imbalance Flow, Cooling, (cfm) | 0
Heating Design temperature from Table 6.3a (F) | 6 | lookup value based on location | Net building infiltration, heating, (cfm) | 86.1227 |  | Net building infiltration, heating, (cfm) | 86.1227
Cooling Design temperature from Table 6.3a (F) | 86 | lookup value | Net building infiltration, cooling, (cfm) | 86.1227 |  | Net building infiltration, cooling, (cfm) | 86.1227
Heating Seasonal temperature from Table 6.3a (F) | 34 | lookup value | Load Factor, heating, design | #VALUE! |  | Load Factor, heating, design | #VALUE!
Cooling Seasonal temperature from Table 6.3a (F) | 80 | lookup value | Load Factor, heating, seasonal | #VALUE! |  | Load Factor, heating, seasonal | #VALUE!
Design Humidity ratio | 0.0133 | lookup value | Load Factor, cooling, design | #VALUE! |  | Load Factor, cooling, design | #DIV/0!
Design Indoor Humidity ratio | 0.0093 | lookup value
Seasonal Humidity Ratio | 0.0124 | lookup value | Load Factor, cooling, seasonal | #VALUE! |  | Load Factor, cooling, seasonal | #DIV/0!
Seasonal Indoor Humidity ratio | 0.009 | lookup value | Equipment factor, heating, design | 1
Design Enthalpy | 35 | lookup value | Equipment factor, heating, seasonal | 1
Design Indoor Enthalpy | 29 | lookup value | Equipment Factor, Cooling, design | 1.0004 | Manufacturers rated fan flow | 1198.8
Seasonal Enthalpy | 33 | lookup value | Equipment Factor, cooling, seasonal | 1.0004
Seasonal Indoor Enthalpy | 29 | lookup value
Is there solar gain reduction in the attic? [Y/N] | N
Equipment Heating Capacity, Btu/hour | 100000 | Enter single speed equipment capacity here. For two speed equipment, enter higher capacity here
Equipment Cooling Capacity, Btu/hour (this should be entered as a negative number) | -36000 | Enter single speed equipment capacity here. For two speed equipment, enter higher capacity here
Equipment Heating Capacity, Btu/hour, LOW | 0 | For two speed equipment, enter lower capacity here
Equipment Cooling Capacity, Btu/hour (this should be entered as a negative number), LOW | 0 | For two speed equipment, enter lower capacity here
Heating Fan Flow, (cfm) | 1500 | For two speed equipment, enter higher flow here
Cooling Fan Flow, (cfm) | 1200 | For two speed equipment, enter higher flow here
Heating Supply duct leakage (cfm) | 150 | For two speed equipment, enter higher flow here
Heating Return duct leakage (cfm) | 150 | For two speed equipment, enter higher flow here
Cooling Supply duct leakage (cfm) | 120 | For two speed equipment, enter higher flow here
Cooling Return duct leakage (cfm) | 120 | For two speed equipment, enter higher flow here
Heating Fan Flow, (cfm), ACCA Manual D calculation or measured value, LOW SPEED | 0 | For two speed equipment, enter lower flow here
Cooling Fan Flow, (cfm), ACCA Manual D calculation or measured value, LOW SPEED | 0 | For two speed equipment, enter lower flow here
Heating Supply duct leakage (cfm), LOW SPEED | 0 | For two speed equipment, enter lower flow here
Heating Return duct leakage (cfm), LOW SPEED | 0 | For two speed equipment, enter lower flow here
Cooling Supply duct leakage (cfm), LOW SPEED | 0 | For two speed equipment, enter lower flow here
Cooling Return duct leakage (cfm), LOW SPEED | 0 | For two speed equipment, enter lower flow here
For Duct Thermal Mass Correction, Enter F for flex duct or duct board, M for sheet metal | F
Enter 1 for single speed equipment, 2 for multispeed equipment | 1 |  | Uncorrected DE
For Vented Attic, Enter V for vented, U for unvented | V
For cooling systems, Enter T for TXV control, O for other control | O |  | #VALUE!
Enter H for HEATING with a heat pump, O for anything else | O |  | #VALUE!
Supply Duct Thermal regain | 0.1 |  | #VALUE!
Return Duct Thermal regain | 0.1 |  | #VALUE!
OUTPUT PARAMETERS
Delivery Effectiveness |  |  | Distribution System Efficiency
Heating, design | #VALUE! |  | Heating, design | #VALUE!
Heating, seasonal | #VALUE! |  | Heating, seasonal | #VALUE!
Cooling, design | #VALUE! |  | Cooling, design | #VALUE!
Cooling, seasonal | #VALUE! |  | Cooling, seasonal | #VALUE!

## Enthalpy Calculation
Enthalpy Calculations
Indoor
Tin,DB [F] | 78
Cooling
Design Duct Zone Temperature Calculations
Dcut location | TDB,design | TDB,seasonal | W,design | W,seasonal | hdesign | hseasonal
Attic 3-5 in 12 roof, supplies | 108 | 93 | 0.0133 | 0.0124 | 40.6691 | 35.9884
Garage | 93 | 87 | 0.0133 | 0.0124 | 36.9805 | 34.5154
Unvented & uninsulated crawlspace | 81.2 | #VALUE! | 0.0133 | 0.0124 | 34.0788 | #VALUE!
Unvented crawlspace with insulated building floor and crawlspace walls | 84 | 79.5 | 0.0133 | 0.0124 | 34.7673 | 32.6741
Unvented crawlspace with insulated building floor | 84.6667 | 79.6667 | 0.0133 | 0.0124 | 34.9313 | 32.715
Vented & uninsulated crawlspace | 82 | 79 | 0.0133 | 0.0124 | 34.2755 | 32.5513
Vented crawlspace with insulated building floor and crawlspace walls | 84.6667 | 79.6667 | 0.0133 | 0.0124 | 34.9313 | 32.715
Vented crawlspace with insulated building floor | 85.1111 | 79.7778 | 0.0133 | 0.0124 | 35.0406 | 32.7423
uninsulated basement | 63.6 | 62.4 | 0.0093 | 0.009 | 25.3939 | 24.7744
basement with insulated walls | 53.2 | 52.6 | 0.0093 | 0.009 | 22.855 | 22.3832
basement with insulated ceiling | 56 | 54.5 | 0.0093 | 0.009 | 23.5385 | 22.8468
under slab | 46 | 46 | 0.0093 | 0.009 | 21.0972 | 20.7728
exterior walls | 82 | 79 | 0.0093 | 0.009 | 29.8859 | 28.8247
Conditioned space | 78 | 78 | 0.0093 | 0.009 | 28.9094 | 28.5807

## Zone temperatures
Heating | Design | Seasonal | Cooling | Design | Seasonal
Attic | 16 | 41 | Attic | 108 | 93
Garage | 19 | 45 | Garage | 93 | 87
Unvented & uninsulated crawlspace | 43.2 | 54.4 | Unvented & uninsulated crawlspace | 81.2 | 78.8
Unvented crawlspace with insulated building floor and crawlspace walls | 21.5 | 42.5 | Unvented crawlspace with insulated building floor and crawlspace walls | 84 | 79.5
Unvented crawlspace with insulated building floor | 16.3333 | 39.6667 | Unvented crawlspace with insulated building floor | 84.6667 | 79.6667
Vented & uninsulated crawlspace | 37 | 51 | Vented & uninsulated crawlspace | 82 | 79
Vented crawlspace with insulated building floor and crawlspace walls | 16.3333 | 39.6667 | Vented crawlspace with insulated building floor and crawlspace walls | 84.6667 | 79.6667
Vented crawlspace with insulated building floor | 12.8889 | 37.7778 | Vented crawlspace with insulated building floor | 85.1111 | 79.7778
uninsulated basement | 44.6 | 50.2 | uninsulated basement | 63.6 | 62.4
basement with insulated walls | 57 | 57 | basement with insulated walls | 53.2 | 52.6
basement with insulated ceiling | 36 | 43 | basement with insulated ceiling | 56 | 54.5
under slab | 46 | 46 | under slab | 46 | 46
exterior walls | 37 | 51 | exterior walls | 82 | 79

## Table 6.3b
Table 6.3b
Design and Seasonal Temperature, Humidity and Enthalpy Conditions (IP)
|  |  | Temperature (F) |  |  |  | Humidity Ratio |  |  |  | Enthalpy
Index | Location | State | Heating Design | Heating Seasonal | Cooling Design | Cooling Seasonal | Wdesign | Wseasonal | Windesign | Winseasonal | Design hout | Seasonal hout | Design hin | Seasonal hin
1 | Adak | AK | 23 | 39
2 | Annette | AK | 17 | 40 | 70 | 70 | 0.0084 | 0.0094 | 0.0073 | 0.0078 | 26 | 28 | 27 | 27
3 | Bethel | AK | -24 | 16 | 68 | 68 | 0.0078 | 0.0067 | 0.0071 | 0.0067 | 25 | 25 | 27 | 26
4 | BigDelta | AK | -39 | 8 | 75 | 75 | 0.0062 | 0.0073 | 0.0065 | 0.0069 | 25 | 26 | 26 | 26
5 | Fairbanks | AK | -31 | 2 | 79 | 79 | 0.0076 | 0.0067 | 0.007 | 0.0067 | 27 | 25 | 26 | 26
6 | Gulkana | AK | -39 | 11 | 75 | 75 | 0.0073 | 0.0061 | 0.0069 | 0.0065 | 26 | 25 | 26 | 26
7 | Homer | AK | 4 | 30 | 63 | 63 | 0.0079 | 0.0094 | 0.0072 | 0.0078 | 24 | 27 | 27 | 27
8 | Juneau | AK | 7 | 34 | 70 | 70 | 0.0084 | 0.0078 | 0.0074 | 0.0071 | 26 | 26 | 27 | 27
9 | King Salmon | AK | -19 | 21 | 66 | 66 | 0.0071 | 0.0102 | 0.0068 | 0.0081 | 24 | 29 | 26 | 28
10 | Kodiak | AK | 11 | 36 | 64 | 64 | 0.0074 | 0.0115 | 0.007 | 0.0086 | 24 | 30 | 26 | 28
11 | McGrath | AK | -41 | 6 | 73 | 73 | 0.0066 | 0.007 | 0.0066 | 0.0068 | 25 | 25 | 26 | 26
12 | Nome | AK | -26 | 15 | 64 | 64 | [6 empty] | 19 | 19
13 | Yakutat | AK | 2 | 33 | 63 | 63 | 0.0077 | 0.0063 | 0.0071 | 0.0065 | 23 | 24 | 26 | 26
14 | Birmingham | AL | 21 | 43 | 91 | 82 | 0.0151 | 0.0143 | 0.01 | 0.0097 | 39 | 35 | 30 | 29
15 | Mobile | AL | 30 | 49 | 91 | 82 | 0.0167 | 0.0157 | 0.0107 | 0.0103 | 40 | 37 | 30 | 30
16 | Montgomery | AL | 27 | 45 | 93 | 83 | 0.0147 | 0.015 | 0.0099 | 0.01 | 39 | 36 | 30 | 30
17 | Fort Smith | AR | 19 | 39 | 95 | 85 | 0.0143 | 0.0148 | 0.0097 | 0.0099 | 39 | 37 | 29 | 30
18 | Little Rock | AR | 21 | 40 | 95 | 84 | 0.0159 | 0.0159 | 0.0103 | 0.0103 | 40 | 38 | 30 | 30
19 | Phoenix | AZ | 38 | 49 | 107 | 91 | 0.0085 | 0.0079 | 0.0074 | 0.0071 | 35 | 31 | 27 | 27
20 | Prescott | AZ | 20 | 38 | 91 | 82 | 0.0044 | 0.0071 | 0.0058 | 0.0068 | 27 | 27 | 25 | 26
21 | Tucson | AZ | 34 | 48 | 102 | 87 | 0.0044 | 0.0076 | 0.0057 | 0.007 | 29 | 29 | 25 | 26
22 | Yuma | AZ | 44 | 52 | 109 | 92 | 0.0094 | 0.0091 | 0.0078 | 0.0076 | 37 | 32 | 27 | 27
23 | Bakersfield | CA | 35 | 48 | 102 | 87 | 0.0082 | 0.0076 | 0.0073 | 0.007 | 34 | 29 | 27 | 26
24 | Burbank | CA | 41 | 53 | 95 | 82 | 0.0085 | 0.0089 | 0.0074 | 0.0076 | 32 | 30 | 27 | 27
25 | Dagget | CA | 32 | 47 | 106 | 90 | 0.006 | 0.0065 | 0.0064 | 0.0066 | 32 | 29 | 26 | 26
26 | Fresno | CA | 32 | 47 | 100 | 88 | 0.0086 | 0.008 | 0.0074 | 0.0072 | 34 | 30 | 27 | 27
27 | Long Beach | CA | 42 | 55 | 88 | 79 | 0.0088 | 0.0101 | 0.0075 | 0.008 | 31 | 30 | 27 | 28
28 | Los Angeles | CA | 45 | 56 | 81 | 75 | 0.0092 | 0.0102 | 0.0077 | 0.0081 | 29 | 29 | 27 | 28
29 | Point Mugu | CA | 41 | 54 | 79 | 75 | 0.0096 | 0.0091 | 0.0078 | 0.0077 | 29 | 28 | 27 | 27
30 | Sacramento | CA | 33 | 48 | 97 | 86 | 0.0081 | 0.0086 | 0.0072 | 0.0074 | 32 | 30 | 27 | 27
31 | San Diego | CA | 42 | 57 | 88 | 76 | 0.0101 | 0.0103 | 0.0081 | 0.0081 | 32 | 29 | 28 | 28
32 | SanFrancisc | CA | 39 | 51 | 79 | 77 | 0.0073 | 0.0073 | 0.0069 | 0.0069 | 27 | 27 | 26 | 26
33 | Santa Maria | CA | 35 | 49 | 82 | 77 | 0.0076 | 0.0071 | 0.007 | 0.0069 | 28 | 26 | 26 | 26
34 | Colorado Springs | CO | 4 | 35 | 88 | 81 | 0.003 | 0.0072 | 0.0052 | 0.0069 | 24 | 27 | 24 | 26
35 | Denver | CO | 3 | 33 | 90 | 82 | 0.0037 | 0.0061 | 0.0055 | 0.0064 | 26 | 26 | 25 | 26
36 | Eagle | CO | -7 | 28 | 86 | 80 | 0.0034 | 0.0069 | 0.0054 | 0.0068 | 24 | 27 | 25 | 26
37 | GrandJunction | CO | 7 | 34 | 93 | 84 | 0.004 | 0.0059 | 0.0056 | 0.0064 | 27 | 27 | 25 | 26
38 | Pueblo | CO | 5 | 32 | 95 | 84 | 0.0047 | 0.0069 | 0.0059 | 0.0067 | 28 | 28 | 25 | 26
39 | Hartford | CT | 6 | 33 | 88 | 81 | 0.0129 | 0.0117 | 0.0092 | 0.0087 | 35 | 32 | 29 | 28
40 | Washington | DC | 20 | 37 | 93 | 81 | 0.0147 | 0.0137 | 0.0099 | 0.0095 | 39 | 35 | 30 | 29
41 | Wilmington | DE | 14 | 37 | 90 | 80 | 0.014 | 0.0129 | 0.0096 | 0.0091 | 37 | 33 | 29 | 29
42 | Apalachicola | FL | 35 | 50 | 90 | 82 | 0.0188 | 0.0168 | 0.0115 | 0.0107 | 42 | 38 | 31 | 30
43 | Daytona | FL | 37 | 51 | 90 | 80 | 0.0171 | 0.0159 | 0.0109 | 0.0104 | 40 | 37 | 31 | 30
44 | Jacksonville | FL | 32 | 44 | 93 | 82 | 0.0163 | 0.0155 | 0.0105 | 0.0102 | 40 | 37 | 30 | 30
45 | Miami | FL | 50 | 54 | 90 | 80 | 0.0171 | 0.016 | 0.0109 | 0.0104 | 40 | 37 | 31 | 30
46 | Orlando | FL | 42 | 53 | 93 | 82 | 0.0163 | 0.0154 | 0.0105 | 0.0102 | 40 | 37 | 30 | 30
47 | Tallahassee | FL | 28 | 46 | 93 | 81 | 0.0163 | 0.0154 | 0.0105 | 0.0102 | 40 | 36 | 30 | 30
48 | Tampa | FL | 40 | 52 | 91 | 81 | 0.0167 | 0.0157 | 0.0107 | 0.0103 | 40 | 37 | 30 | 30
49 | West PalmBeach | FL | 47 | 54 | 90 | 80 | 0.0171 | 0.0159 | 0.0109 | 0.0104 | 40 | 37 | 31 | 30
50 | Augusta | GA | 25 | 43 | 93 | 82 | 0.0147 | 0.0146 | 0.0099 | 0.0098 | 39 | 36 | 30 | 29
51 | Atlanta | GA | 23 | 43 | 91 | 80 | 0.0136 | 0.014 | 0.0094 | 0.0096 | 37 | 35 | 29 | 29
52 | Macon | GA | 27 | 44 | 93 | 83 | 0.0147 | 0.0143 | 0.0099 | 0.0097 | 39 | 35 | 30 | 29
53 | Savanah | GA | 29 | 45 | 93 | 81 | 0.0163 | 0.0152 | 0.0105 | 0.0101 | 40 | 36 | 30 | 30
54 | Barberspoint | HI | 61 | 62 | 90 | 78 | 0.014 | 0.0142 | 0.0096 | 0.0097 | 37 | 34 | 29 | 29
55 | Hilo | HI | 63 | 64 | 84 | 77 | 0.0152 | 0.0144 | 0.0101 | 0.0098 | 37 | 34 | 30 | 29
56 | Honolulu | HI | 63 | 64 | 88 | 79 | 0.0144 | 0.0132 | 0.0098 | 0.0093 | 37 | 33 | 29 | 29
57 | Lihue | HI | 62 | 63 | 84 | 77 | 0.0168 | 0.0146 | 0.0107 | 0.0099 | 39 | 35 | 30 | 30
58 | Burlington | IA | 1 | 31 | 91 | 80 | 0.0151 | 0.0142 | 0.01 | 0.0097 | 39 | 35 | 30 | 29
59 | DesMoines | IA | -4 | 29 | 90 | 81 | 0.014 | 0.0129 | 0.0096 | 0.0091 | 37 | 33 | 29 | 29
60 | MasonCity | IA | -10 | 26 | 88 | 80 | 0.0144 | 0.0132 | 0.0098 | 0.0093 | 37 | 34 | 29 | 29
61 | Sioux City | IA | -6 | 27 | 90 | 82 | 0.014 | 0.0145 | 0.0096 | 0.0098 | 37 | 35 | 29 | 29
62 | Boise | ID | 9 | 38 | 93 | 84 | 0.0052 | 0.0062 | 0.0061 | 0.0065 | 28 | 27 | 25 | 26
63 | Lewiston | ID | 15 | 39 | 93 | 84 | 0.0064 | 0.0065 | 0.0065 | 0.0066 | 29 | 27 | 26 | 26
64 | Pocatello | ID | 0 | 32 | 90 | 83 | 0.0048 | 0.0058 | 0.0059 | 0.0063 | 27 | 26 | 25 | 26
65 | Chicago | IL | 3 | 33 | 90 | 81 | 0.014 | 0.0115 | 0.0096 | 0.0086 | 37 | 32 | 29 | 28
66 | Moline | IL | -3 | 31 | 90 | 81 | 0.014 | 0.0133 | 0.0096 | 0.0093 | 37 | 34 | 29 | 29
67 | Springfield | IL | 2 | 33 | 91 | 81 | 0.0151 | 0.0131 | 0.01 | 0.0093 | 39 | 34 | 30 | 29
68 | Evansville | IN | 9 | 37 | 91 | 81 | 0.0151 | 0.0137 | 0.01 | 0.0095 | 39 | 35 | 30 | 29
69 | FortWayne | IN | 2 | 32 | 88 | 79 | 0.0144 | 0.0129 | 0.0098 | 0.0091 | 37 | 33 | 29 | 29
70 | Indianapolis | IN | 3 | 33 | 88 | 80 | 0.0144 | 0.0131 | 0.0098 | 0.0092 | 37 | 34 | 29 | 29
71 | South Bend | IN | 3 | 33 | 88 | 80 | 0.0129 | 0.0123 | 0.0092 | 0.0089 | 35 | 33 | 29 | 28
72 | Dodge City | KS | 6 | 35 | 97 | 85 | 0.0094 | 0.0111 | 0.0078 | 0.0084 | 34 | 33 | 27 | 28
73 | Goodland | KS | 2 | 33 | 93 | 85 | 0.0076 | 0.0095 | 0.007 | 0.0078 | 31 | 31 | 26 | 27
74 | Kansas City | KS | 4 | 34 | 93 | 83 | 0.0147 | 0.0141 | 0.0099 | 0.0096 | 39 | 35 | 30 | 29
75 | Topeka | KS | 4 | 32 | 93 | 82 | 0.0147 | 0.0145 | 0.0099 | 0.0098 | 39 | 36 | 30 | 29
76 | Wichita | KS | 8 | 34 | 97 | 85 | 0.0123 | 0.0133 | 0.0089 | 0.0093 | 37 | 35 | 28 | 29
77 | Lexington | KY | 10 | 36 | 88 | 80 | 0.0144 | 0.0138 | 0.0098 | 0.0095 | 37 | 34 | 29 | 29
78 | Louisville | KY | 11 | 37 | 90 | 82 | 0.0155 | 0.0136 | 0.0102 | 0.0095 | 39 | 35 | 30 | 29
79 | BatonRouge | LA | 30 | 48 | 91 | 82 | 0.0167 | 0.016 | 0.0107 | 0.0104 | 40 | 37 | 30 | 30
80 | Lake Charles | LA | 32 | 48 | 91 | 82 | 0.0167 | 0.0164 | 0.0107 | 0.0105 | 40 | 38 | 30 | 30
81 | Neworleans | LA | 39 | 49 | 91 | 81 | 0.0167 | 0.0162 | 0.0107 | 0.0105 | 40 | 37 | 30 | 30
82 | Shreveport | LA | 26 | 46 | 95 | 83 | 0.0159 | 0.0155 | 0.0103 | 0.0102 | 40 | 37 | 30 | 30
83 | Boston | MA | 12 | 37 | 88 | 80 | 0.0129 | 0.0111 | 0.0092 | 0.0084 | 35 | 31 | 29 | 28
84 | Baltimore | MD | 15 | 37 | 91 | 81 | 0.0136 | 0.0133 | 0.0094 | 0.0093 | 37 | 34 | 29 | 29
85 | Patuxent River | MD | 21 | 41 | 90 | 80 | 0.0155 | 0.0142 | 0.0102 | 0.0097 | 39 | 35 | 30 | 29
86 | Bangor | ME | -2 | 29 | 84 | 78 | 0.011 | 0.0101 | 0.0084 | 0.008 | 32 | 30 | 28 | 28
87 | Caribou | ME | -10 | 25 | 82 | 77 | 0.0101 | 0.0099 | 0.008 | 0.008 | 31 | 29 | 28 | 27
88 | Portland | ME | 2 | 32 | 82 | 77 | 0.0127 | 0.0114 | 0.0091 | 0.0086 | 34 | 31 | 29 | 28
89 | Alpena | MI | -1 | 29 | 84 | 79 | 0.011 | 0.0119 | 0.0084 | 0.0088 | 32 | 32 | 28 | 28
90 | Detroit | MI | 5 | 34 | 88 | 80 | 0.0129 | 0.0215 | 0.0092 | 0.0126 | 35 | 43 | 29 | 33
91 | Flint | MI | 3 | 31 | 86 | 79 | 0.0133 | 0.0116 | 0.0093 | 0.0086 | 35 | 32 | 29 | 28
92 | GrandRapids | MI | 5 | 32 | 86 | 80 | 0.0133 | 0.0121 | 0.0093 | 0.0088 | 35 | 32 | 29 | 28
93 | Sault Saint Marie | MI | -7 | 25 | 81 | 78 | 0.0118 | 0.0118 | 0.0087 | 0.0087 | 32 | 32 | 28 | 28
94 | Traverse City | MI | 2 | 30 | 86 | 80 | 0.0119 | 0.0115 | 0.0088 | 0.0086 | 34 | 32 | 28 | 28
95 | Duluth | MN | -16 | 22 | 81 | 78 | 0.0105 | 0.0111 | 0.0082 | 0.0084 | 31 | 31 | 28 | 28
96 | International Falls | MN | -23 | 17 | 82 | 77 | 0.0101 | 0.0107 | 0.008 | 0.0083 | 31 | 30 | 28 | 28
97 | Minneapolis | MN | -11 | 24 | 88 | 81 | 0.0129 | 0.0125 | 0.0092 | 0.009 | 35 | 33 | 29 | 29
98 | Rochester | MN | -12 | 25 | 86 | 78 | 0.0133 | 0.0126 | 0.0093 | 0.009 | 35 | 33 | 29 | 29
99 | Columbia | MO | 5 | 34 | 91 | 82 | 0.0151 | 0.0135 | 0.01 | 0.0094 | 39 | 34 | 30 | 29
100 | Saint Louis | MO | 8 | 35 | 93 | 82 | 0.0147 | 0.0144 | 0.0099 | 0.0098 | 39 | 35 | 30 | 29
101 | Springfield | MO | 9 | 37 | 91 | 81 | 0.0151 | 0.0147 | 0.01 | 0.0099 | 39 | 36 | 30 | 30
102 | Jackson | MS | 25 | 48 | 93 | 81 | 0.0163 | 0.015 | 0.0105 | 0.01 | 40 | 36 | 30 | 30
103 | Meridian | MS | 25 | 44 | 93 | 83 | 0.0163 | 0.0148 | 0.0105 | 0.0099 | 40 | 36 | 30 | 30
104 | Billings | MT | -7 | 29 | 90 | 82 | 0.006 | 0.0074 | 0.0064 | 0.007 | 28 | 28 | 26 | 26
105 | Cut Bank | MT | -16 | 26 | 84 | 79 | 0.0049 | 0.0067 | 0.006 | 0.0067 | 26 | 26 | 25 | 26
106 | Glasgow | MT | -17 | 22 | 90 | 83 | 0.006 | 0.0079 | 0.0064 | 0.0072 | 28 | 29 | 26 | 27
107 | GreatFalls | MT | -13 | 29 | 88 | 81 | 0.0052 | 0.0064 | 0.0061 | 0.0066 | 27 | 27 | 25 | 26
108 | Helena | MT | -10 | 29 | 88 | 82 | 0.0041 | 0.0058 | 0.0056 | 0.0063 | 26 | 26 | 25 | 26
109 | Lewistown | MT | -12 | 30 | 86 | 81 | 0.0056 | 0.0083 | 0.0062 | 0.0073 | 27 | 29 | 26 | 27
110 | MilesCity | MT | -12 | 24 | 93 | 84 | 0.0064 | 0.0068 | 0.0065 | 0.0067 | 29 | 28 | 26 | 26
111 | Missoula | MT | -1 | 33 | 88 | 82 | 0.0052 | 0.0064 | 0.0061 | 0.0066 | 27 | 27 | 25 | 26
112 | Asheville | NC | 16 | 40 | 86 | 79 | 0.0133 | 0.0142 | 0.0093 | 0.0097 | 35 | 35 | 29 | 29
113 | CapeHatteras | NC | 29 | 46 | 86 | 79 | 0.018 | 0.0165 | 0.0112 | 0.0106 | 40 | 37 | 31 | 30
114 | Charlotte | NC | 23 | 41 | 91 | 81 | 0.0136 | 0.013 | 0.0094 | 0.0092 | 37 | 34 | 29 | 29
115 | CherryPoint | NC | 28 | 45 | 93 | 80 | 0.018 | 0.0153 | 0.0112 | 0.0101 | 42 | 36 | 31 | 30
116 | Greensboro | NC | 19 | 40 | 90 | 81 | 0.014 | 0.0134 | 0.0096 | 0.0094 | 37 | 34 | 29 | 29
117 | Raleigh | NC | 20 | 40 | 90 | 81 | 0.0155 | 0.0145 | 0.0102 | 0.0098 | 39 | 35 | 30 | 29
118 | Bismarck | ND | -16 | 22 | 90 | 82 | 0.0084 | 0.0107 | 0.0074 | 0.0083 | 31 | 31 | 27 | 28
119 | Fargo | ND | -17 | 19 | 88 | 82 | 0.0115 | 0.012 | 0.0086 | 0.0088 | 34 | 33 | 28 | 28
120 | Minot | ND | -16 | 22 | 90 | 81 | 0.0097 | 0.0097 | 0.0079 | 0.0079 | 32 | 30 | 27 | 27
121 | GrandIsland | NE | -2 | 29 | 93 | 83 | 0.0117 | 0.0122 | 0.0087 | 0.0089 | 35 | 33 | 28 | 28
122 | North Platte | NE | -4 | 29 | 91 | 83 | 0.0107 | 0.0109 | 0.0083 | 0.0083 | 34 | 32 | 28 | 28
123 | Omaha | NE | -2 | 31 | 91 | 82 | 0.0151 | 0.0138 | 0.01 | 0.0095 | 39 | 35 | 30 | 29
124 | Scottsbluff | NE | -3 | 30 | 91 | 83 | 0.0068 | 0.0088 | 0.0067 | 0.0075 | 29 | 30 | 26 | 27
125 | Concord | NH | -2 | 29 | 86 | 81 | 0.0119 | 0.0117 | 0.0088 | 0.0087 | 34 | 32 | 28 | 28
126 | Lakehurst | NJ | 13 | 37 | 88 | 81 | 0.0144 | 0.0131 | 0.0098 | 0.0092 | 37 | 34 | 29 | 29
127 | Newark | NJ | 14 | 38 | 90 | 80 | 0.014 | 0.0117 | 0.0096 | 0.0087 | 37 | 32 | 29 | 28
128 | Albuquerque | NM | 18 | 38 | 93 | 83 | 0.004 | 0.007 | 0.0056 | 0.0068 | 27 | 28 | 25 | 26
129 | Clayton | NM | 9 | 36 | 91 | 80 | 0.0056 | 0.0088 | 0.0062 | 0.0075 | 28 | 29 | 26 | 27
130 | Roswell | NM | 20 | 40 | 97 | 86 | 0.0055 | 0.0085 | 0.0062 | 0.0074 | 29 | 30 | 26 | 27
131 | Truthandconsequenses | NM | 26 | 40 | 95 | 83 | 0.0036 | 0.0069 | 0.0054 | 0.0068 | 27 | 28 | 25 | 26
132 | Tucumcari | NM | 15 | 38 | 95 | 85 | 0.0059 | 0.0095 | 0.0064 | 0.0078 | 29 | 31 | 26 | 27
133 | Elko | NV | 1 | 32 | 93 | 84 | 0.0029 | 0.0052 | 0.0052 | 0.0061 | 26 | 26 | 24 | 25
134 | Ely | NV | 0 | 30 | 88 | 80 | 0.002 | 0.0041 | 0.0048 | 0.0056 | 23 | 24 | 24 | 25
135 | Las Vegas | NV | 30 | 46 | 106 | 91 | 0.0048 | 0.0054 | 0.0059 | 0.0062 | 31 | 28 | 25 | 25
136 | Reno | NV | 13 | 36 | 91 | 84 | 0.0033 | 0.0055 | 0.0053 | 0.0062 | 26 | 26 | 25 | 26
137 | Tonopah | NV | 13 | 36 | 91 | 82 | 0.0022 | 0.0049 | 0.0049 | 0.006 | 24 | 25 | 24 | 25
138 | Winnemucca | NV | 7 | 34 | 95 | 86 | 0.0025 | 0.0041 | 0.005 | 0.0056 | 26 | 25 | 24 | 25
139 | Albany | NY | -2 | 31 | 86 | 79 | 0.0119 | 0.0112 | 0.0088 | 0.0085 | 34 | 31 | 28 | 28
140 | Binghamton | NY | 2 | 30 | 82 | 78 | 0.0114 | 0.0125 | 0.0085 | 0.009 | 32 | 32 | 28 | 29
141 | Buffalo | NY | 5 | 32 | 84 | 78 | 0.0123 | 0.012 | 0.0089 | 0.0088 | 34 | 32 | 29 | 28
142 | Massena | NY | -10 | 27 | 84 | 79 | 0.0123 | 0.012 | 0.0089 | 0.0088 | 34 | 32 | 29 | 28
143 | N.Y. Central | NY | 15 | 38 | 88 | 78 | 0.0129 | 0.0128 | 0.0092 | 0.0091 | 35 | 33 | 29 | 29
144 | N.Y. LA Guardia | NY | 17 | 38 | 90 | 80 | 0.014 | 0.0127 | 0.0096 | 0.0091 | 37 | 33 | 29 | 29
145 | Rochester | NY | 5 | 31 | 86 | 80 | 0.0133 | 0.0131 | 0.0093 | 0.0092 | 35 | 34 | 29 | 29
146 | Syracuse | NY | 2 | 31 | 86 | 79 | 0.0133 | 0.0124 | 0.0093 | 0.009 | 35 | 32 | 29 | 29
147 | Akron | OH | 5 | 33 | 86 | 79 | 0.0133 | 0.013 | 0.0093 | 0.0092 | 35 | 33 | 29 | 29
148 | Cincinnatti | OH | 12 | 36 | 90 | 80 | 0.0155 | 0.0122 | 0.0102 | 0.0089 | 39 | 33 | 30 | 28
149 | Cleveland | OH | 6 | 34 | 86 | 80 | 0.0133 | 0.0124 | 0.0093 | 0.009 | 35 | 33 | 29 | 29
150 | Columbus | OH | 6 | 35 | 88 | 80 | 0.0144 | 0.013 | 0.0098 | 0.0092 | 37 | 34 | 29 | 29
151 | Dayton | OH | 5 | 34 | 88 | 79 | 0.0144 | 0.0123 | 0.0098 | 0.0089 | 37 | 32 | 29 | 28
152 | Toledo | OH | 3 | 32 | 88 | 80 | 0.0129 | 0.0138 | 0.0092 | 0.0095 | 35 | 34 | 29 | 29
153 | Youngstown | OH | 4 | 32 | 84 | 79 | 0.0123 | 0.012 | 0.0089 | 0.0088 | 34 | 32 | 29 | 28
154 | Oklahoma | OK | 15 | 38 | 97 | 84 | 0.0138 | 0.0135 | 0.0095 | 0.0094 | 39 | 35 | 29 | 29
155 | Tulsa | OK | 14 | 38 | 97 | 84 | 0.0138 | 0.0145 | 0.0095 | 0.0098 | 39 | 36 | 29 | 29
156 | Astoria | OR | 29 | 46 | 72 | 72 | 0.0101 | 0.0099 | 0.008 | 0.008 | 28 | 30 | 28 | 27
157 | Medford | OR | 24 | 41 | 95 | 84 | 0.0072 | 0.0078 | 0.0069 | 0.0071 | 31 | 29 | 26 | 27
158 | NorthBend | OR | 32 | 48 | 70 | 70 | 0.0093 | 0.0101 | 0.0077 | 0.008 | 27 | 28 | 27 | 28
159 | Pendleton | OR | 11 | 39 | 93 | 84 | 0.0052 | 0.0062 | 0.0061 | 0.0065 | 28 | 27 | 25 | 26
160 | Portland | OR | 27 | 45 | 86 | 80 | 0.0092 | 0.0091 | 0.0077 | 0.0076 | 31 | 29 | 27 | 27
161 | Redmond | OR | 9 | 37 | 90 | 83 | 0.0048 | 0.0061 | 0.0059 | 0.0064 | 27 | 27 | 25 | 26
162 | Salem | OR | 25 | 44 | 88 | 81 | 0.0088 | 0.0082 | 0.0075 | 0.0073 | 31 | 28 | 27 | 27
163 | Allentown | PA | 10 | 34 | 88 | 79 | 0.0129 | 0.0124 | 0.0092 | 0.0089 | 35 | 32 | 29 | 29
164 | Erie | PA | 7 | 33 | 82 | 77 | 0.0127 | 0.0129 | 0.0091 | 0.0091 | 34 | 33 | 29 | 29
165 | Harrisburg | PA | 13 | 36 | 90 | 81 | 0.014 | 0.0124 | 0.0096 | 0.0089 | 37 | 33 | 29 | 29
166 | Philadelphia | PA | 15 | 37 | 90 | 81 | 0.014 | 0.013 | 0.0096 | 0.0092 | 37 | 34 | 29 | 29
167 | Pittsburg | PA | 11 | 33 | 88 | 78 | 0.0115 | 0.0118 | 0.0086 | 0.0087 | 34 | 32 | 28 | 28
168 | Providence | RI | 10 | 35 | 86 | 79 | 0.0133 | 0.0121 | 0.0093 | 0.0088 | 35 | 32 | 29 | 28
169 | Charleston | SC | 28 | 46 | 91 | 81 | 0.0167 | 0.0158 | 0.0107 | 0.0103 | 40 | 37 | 30 | 30
170 | Greenville | SC | 23 | 42 | 91 | 80 | 0.0136 | 0.0137 | 0.0094 | 0.0095 | 37 | 34 | 29 | 29
171 | Columbia | SC | 24 | 43 | 93 | 83 | 0.0147 | 0.0141 | 0.0099 | 0.0097 | 39 | 35 | 30 | 29
172 | Huron | SD | -12 | 22 | 91 | 83 | 0.0121 | 0.0125 | 0.0088 | 0.009 | 35 | 34 | 28 | 29
173 | Pierre | SD | -9 | 26 | 95 | 84 | 0.0098 | 0.0113 | 0.0079 | 0.0085 | 34 | 33 | 27 | 28
174 | Rapid City | SD | -5 | 29 | 91 | 83 | 0.0068 | 0.0091 | 0.0067 | 0.0076 | 29 | 30 | 26 | 27
175 | Sioux Falls | SD | -11 | 26 | 90 | 82 | 0.0125 | 0.013 | 0.009 | 0.0092 | 35 | 34 | 29 | 29
176 | Chattanooga | TN | 20 | 40 | 91 | 82 | 0.0151 | 0.0151 | 0.01 | 0.01 | 39 | 36 | 30 | 30
177 | Knoxville | TN | 19 | 39 | 90 | 81 | 0.014 | 0.0141 | 0.0096 | 0.0096 | 37 | 35 | 29 | 29
178 | Memphis | TN | 21 | 41 | 93 | 82 | 0.0163 | 0.0149 | 0.0105 | 0.01 | 40 | 36 | 30 | 30
179 | Nashville | TN | 16 | 40 | 91 | 81 | 0.0151 | 0.0141 | 0.01 | 0.0096 | 39 | 35 | 30 | 29
180 | Abilene | TX | 22 | 42 | 97 | 85 | 0.0108 | 0.0125 | 0.0083 | 0.009 | 35 | 34 | 28 | 29
181 | Amarillo | TX | 12 | 37 | 93 | 84 | 0.0076 | 0.0105 | 0.007 | 0.0082 | 31 | 32 | 26 | 28
182 | Austin | TX | 30 | 47 | 97 | 85 | 0.0123 | 0.0147 | 0.0089 | 0.0099 | 37 | 36 | 28 | 30
183 | Brownsville | TX | 40 | 51 | 93 | 82 | 0.0163 | 0.0166 | 0.0105 | 0.0106 | 40 | 38 | 30 | 30
184 | Corpus Christie | TX | 36 | 50 | 93 | 83 | 0.0163 | 0.017 | 0.0105 | 0.0108 | 40 | 39 | 30 | 31
185 | DelRio | TX | 32 | 47 | 99 | 84 | 0.0119 | 0.0135 | 0.0088 | 0.0094 | 37 | 35 | 28 | 29
186 | ElPaso | TX | 25 | 44 | 99 | 85 | 0.0051 | 0.0076 | 0.0061 | 0.007 | 29 | 29 | 25 | 26
187 | Fort Worth | TX | 24 | 44 | 97 | 85 | 0.0138 | 0.0137 | 0.0095 | 0.0095 | 39 | 36 | 29 | 29
188 | Houston | TX | 34 | 49 | 93 | 83 | 0.0163 | 0.016 | 0.0105 | 0.0104 | 40 | 37 | 30 | 30
189 | Kingsville | TX | 36 | 50 | 97 | 84 | 0.0155 | 0.0169 | 0.0102 | 0.0108 | 40 | 39 | 30 | 31
190 | Laredo | TX | 36 | 51 | 100 | 87 | 0.0115 | 0.0142 | 0.0086 | 0.0097 | 37 | 36 | 28 | 29
191 | Lubbock | TX | 17 | 39 | 95 | 85 | 0.0085 | 0.0103 | 0.0074 | 0.0081 | 32 | 32 | 27 | 28
192 | Lufkin | TX | 27 | 45 | 95 | 84 | 0.0159 | 0.0161 | 0.0103 | 0.0104 | 40 | 38 | 30 | 30
193 | Midland | TX | 22 | 43 | 97 | 84 | 0.0068 | 0.0105 | 0.0067 | 0.0082 | 31 | 32 | 26 | 28
194 | Port Arthur | TX | 32 | 49 | 93 | 82 | 0.018 | 0.0169 | 0.0112 | 0.0107 | 42 | 38 | 31 | 30
195 | San Angelo | TX | 24 | 43 | 97 | 85 | 0.0094 | 0.0118 | 0.0078 | 0.0087 | 34 | 33 | 27 | 28
196 | San Antonio | TX | 30 | 47 | 95 | 84 | 0.0127 | 0.0146 | 0.0091 | 0.0098 | 37 | 36 | 29 | 29
197 | Waco | TX | 26 | 44 | 99 | 85 | 0.0134 | 0.0145 | 0.0094 | 0.0098 | 39 | 36 | 29 | 29
198 | Wichita Falls | TX | 19 | 40 | 100 | 87 | 0.0115 | 0.014 | 0.0086 | 0.0096 | 37 | 36 | 28 | 29
199 | Cedar City | UT | 8 | 34 | 91 | 82 | 0.0033 | 0.0059 | 0.0053 | 0.0063 | 26 | 26 | 25 | 26
200 | SaltLakeCity | UT | 11 | 35 | 95 | 86 | 0.0025 | 0.0061 | 0.005 | 0.0064 | 26 | 27 | 24 | 26
201 | Norfolk | VA | 24 | 42 | 91 | 81 | 0.0056 | 0.0146 | 0.0062 | 0.0098 | 28 | 36 | 26 | 30
202 | Richmond | VA | 18 | 40 | 91 | 81 | 0.0151 | 0.014 | 0.01 | 0.0096 | 39 | 35 | 30 | 29
203 | Roanoke | VA | 17 | 39 | 90 | 81 | 0.0155 | 0.0128 | 0.0102 | 0.0091 | 39 | 33 | 30 | 29
204 | Burlington | VT | -6 | 28 | 84 | 78 | 0.0137 | 0.0113 | 0.0095 | 0.0085 | 35 | 31 | 29 | 28
205 | Olympia | WA | 23 | 43 | 82 | 79 | 0.0127 | 0.0082 | 0.0091 | 0.0073 | 34 | 28 | 29 | 27
206 | Seattle | WA | 28 | 44 | 81 | 78 | 0.0092 | 0.0084 | 0.0077 | 0.0074 | 29 | 28 | 27 | 27
207 | Spokane | WA | 7 | 36 | 90 | 81 | 0.0048 | 0.0062 | 0.0059 | 0.0065 | 27 | 26 | 25 | 26
208 | Yakima | WA | 11 | 37 | 91 | 83 | 0.0068 | 0.0068 | 0.0067 | 0.0067 | 29 | 27 | 26 | 26
209 | EauClair | WI | -13 | 24 | 88 | 81 | 0.0129 | 0.0134 | 0.0092 | 0.0094 | 35 | 34 | 29 | 29
210 | GreenBay | WI | -7 | 27 | 86 | 79 | 0.0133 | 0.0129 | 0.0093 | 0.0092 | 35 | 33 | 29 | 29
211 | LaCrosse | WI | -8 | 29 | 88 | 81 | 0.0144 | 0.0131 | 0.0098 | 0.0092 | 37 | 34 | 29 | 29
212 | Madison | WI | -6 | 28 | 88 | 79 | 0.0129 | 0.0123 | 0.0092 | 0.0089 | 35 | 33 | 29 | 28
213 | Milwaukee | WI | -2 | 31 | 86 | 79 | 0.0133 | 0.013 | 0.0093 | 0.0092 | 35 | 33 | 29 | 29
214 | Charleston | WV | 11 | 37 | 88 | 81 | 0.0144 | 0.0127 | 0.0098 | 0.0091 | 37 | 33 | 29 | 29
215 | Huntington | WV | 11 | 37 | 88 | 80 | 0.0144 | 0.0134 | 0.0098 | 0.0093 | 37 | 34 | 29 | 29
216 | Casper | WY | -5 | 30 | 90 | 82 | 0.0026 | 0.0054 | 0.0051 | 0.0062 | 24 | 26 | 24 | 25
217 | Cheyenne | WY | 0 | 32 | 84 | 80 | 0.0038 | 0.0069 | 0.0055 | 0.0068 | 24 | 27 | 25 | 26
218 | Rock Springs | WY | -2 | 29 | 84 | 79 | 0.0018 | 0.0043 | 0.0047 | 0.0057 | 22 | 24 | 24 | 25
219 | Sheridan | WY | -7 | 30 | 90 | 82 | 0.0048 | 0.0081 | 0.0059 | 0.0072 | 27 | 28 | 25 | 27
220 | Edmonton | AB | -23 | 21 | 78 | 76 | 0.008 | 0.0082 | 0.0072 | 0.0073 | 27 | 27 | 27 | 27
221 | Montreal | PQ | -8 | 27 | 83 | 77 | 0.0126 | 0.0124 | 0.009 | 0.009 | 34 | 32 | 29 | 29
222 | Vancouver | BC | 23 | 44 | 74 | 73 | 0.0103 | 0.0104 | 0.0081 | 0.0082 | 29 | 29 | 28 | 28
223 | Toronto | ON | 1 | 26 | 84 | 78 | 0.0123 | 0.0126 | 0.0089 | 0.009 | 34 | 33 | 28 | 29
224 | Winnipeg | MN | -24 | 16 | 84 | 79 | 0.0104 | 0.0092 | 0.0082 | 0.0077 | 32 | 29 | 28 | 27