1

Ozone Transport Assessment Group

Control Technologies and

Options Workgroup

FINAL

States' Report on Electric Utility

Nitrogen Oxides Reduction Technology Options

for Application by The

Ozone Transport Assessment Group

Prepared for the

OTAG Control Technologies & Options Workgroup

by Ken Colburn

April 11, 1996

2

STATES' REPORT

on

ELECTRIC UTILITY

NITROGEN OXIDES REDUCTION TECHNOLOGY OPTIONS

FOR APPLICATION BY THE

OZONE TRANSPORT ASSESSMENT GROUP

TABLE OF CONTENTS

Executive Summary	ii

Section 1.Introduction	1

Section 2.NOx Formation in Utility Boilers and Combustion Turbines	5

Section 3.Electric Utility NOx Emission Control Regulatory Framework	8

Section 4.Utility Boilers and Combustion Turbines:  Description of Equipment	12

Section 5.NOx Control Technologies for Utilities	17

Section 6.Increasing Emission Reduction Requirements and Deregulation of the Electric Utility Industry	41

Section 7.Strategy Development and Implementation Issues for Electric

Utility Sources	44

Section 8.Summary Matrix of NOx Control Technology Cost and Performance	46

Appendix A.Cost Evaluation Behind Industry-Estimated Control Cost Range in Summary Matrix	47

Selected References	49

STATES' REPORT

on

ELECTRIC UTILITY

NITROGEN OXIDES REDUCTION TECHNOLOGY OPTIONS

FOR APPLICATION BY THE

OZONE TRANSPORT ASSESSMENT GROUP

EXECUTIVE SUMMARY

This report provides a brief overview of NOx control technologies available for fossil fuel-fired electric utility power generation equipment (boilers, combustors, steam generators, etc.).  While this report evaluates controls that are commercially available today, NOx control technologies are undergoing rapid improvement by both manufacturers and utility users, and the learning curve of their application and use is swiftly maturing.  In addition, other high-performance control technologies, and hybridizations of existing technologies, are in various stages of development by major electric utility equipment manufacturers.  The extent of development of new NOx controls, as well as the improvement of existing NOx controls, is largely influenced by the incentives provided when establishing any regulations.

The Ozone Transport Assessment Group (OTAG) is considering the possibility of establishing a NOx "cap and trade" program to provide market-based incentives to significantly reduce NOx emissions from electric utilities in 37 States.  The OTAG region contains approximately 1,500 fossil fuel-fired boilers capable of generating over 260,000 Megawatts (MW).  These boilers emitted approximately 5,600,000 tons of NOx in 1990 and are of varying size, design, and fuel capacities.  Of the 1,500 boilers, approximately 900 burn coal and accounted for over 85% of NOx emitted in 1990.  As a result, NOx controls for coal-fired boilers are of particular importance.

There are currently two major categories of NOx controls available for utility boilers:  combustion controls (e.g., low NOx burners, overfire air), and post-combustion controls (e.g., selective catalytic reduction or SCR, selective noncatalytic reduction or SNCR, and reburning).  Combustion controls prevent the formation of NOx by delaying the mixing of fuel and air in the main combustion zone.  Post-combustion controls destroy NOx that has been formed in the main combustion zone by injecting ammonia (SCR), urea (SNCR), or additional fuel (reburning).

Currently available combustion controls can, on average, reduce NOx by approximately 50 percent from uncontrolled levels.  Post-combustion controls can either be applied in conjunction with combustion controls or by themselves, and depending upon how such controls are designed and engineered, they can reduce NOx as little as 30% or as much as 95%.  The following bullets provide summary information on the average NOx emission levels achieved by these controls and their associated incremental costs.

oCoal-fired boilers

With combustion controls, coal-fired boilers typically emit at a rate of 0.35 to 0.55 pounds per million British thermal units (lb/mmBtu) of NOx.  The addition of post-combustion controls can further reduce boiler NOx emissions to levels below 0.2 lb/mmBtu.  The cost-effectiveness of these reductions typically ranges from $200 to $600 per ton of NOx removed when applying combustion controls, and from $500 to $2,000 per ton of NOx removed when applying post-combustion controls.

oOil-fired boilers

With combustion controls, oil-fired boilers typically emit 0.3 lb/mmBtu of NOx, and the cost-effectiveness of these reductions typically ranges from $600 to $1,500 per ton of NOx removed.  The addition of post-combustion controls can further reduce boiler NOx emissions to levels below 0.1 lb/mmBtu, with typical costs ranging from $1,200 to $2,200 per ton of NOx removed.

oGas-fired boilers

With combustion controls, gas-fired boilers typically emit 0.25 lb/mmBtu of NOx, and the cost-effectiveness of these reductions typically ranges from $600 to $1,500 per ton of NOx removed.  The addition of post-combustion controls can reduce boiler NOx emissions to levels below 0.1 lb/mmBtu, with typical costs ranging from $900 to $2,000 per ton of NOx removed.

It should be noted that the above figures represent typical performance and costs.  As described in detail throughout the report, some boilers can achieve better performance at lower costs and vice-versa.  Additionally, some controls are not applicable to certain types of boilers.

An important factor in the evaluation of any technology is also gaining an understanding of the underlying financial incentives for improving performance and lowering cost.  In the case of pollution controls, any incentive to go below a certain standard prompts innovation by both the regulated entities and the pollution control manufacturers.  Trading of emission reductions and allowances alone can be expected to reduce overall NOx control costs by over half (56%) of the per-ton costs noted above.

The SOx allowance system authorized by Title IV of the Clean Air Act is a good illustration.  Through the use of market-based programs and incentives, the cost of SOx reduction is far lower today than even the lowest estimate in 1990.  Because of the underlying incentives built into this program, industry responded to the regulation in ways that were not, at the time, anticipated or expected, such as:  (1) negotiating with railroad companies to reduce their coal transportation rates; (2) encouraging greater improvement of mining techniques; (3) blending and burning low sulfur coals at lower cost; and (4) reducing SOx scrubber costs by 40%.

Similarly, in the area of NOx control, such advances are already being driven by upcoming regulatory actions in the Northeastern Ozone Transport Region (OTR), where one commercial boiler has been retrofitted with newer generation combustion controls and achieves a long-term NOx emission rate of 0.23 lb/mmBtu.  Another coal fired boiler in the OTR has been retrofitted with SCR at a cost of approximately $400 per ton--an achievement previously discounted as unrealistically optimistic.  The OTAG process and newly proposed Title IV (Acid Rain) rules for NOx have also spurred control technology markets, so much so that many of the cost estimates for NOx control solutions referenced in this report have already been rendered obsolete by still more cost-effective control options.

Additionally, the Department of Energy's (DOE) Low Emission Boiler System program (LEBS) works with major U.S. manufacturers of utility equipment to develop, among other things, higher performing NOx controls.  One goal by both DOE and the manufacturers is to develop, by the year 2000, commercially applicable combustion controls capable of reducing NOx to a rate of 0.20 lb/mmBtu and, in combination with post-combustion controls, capable of reducing NOx to a rate of 0.10 lb/mmBtu.  Further, as illustrated by a recent white paper by the Institute of Clean Air Companies (ICAC), most coal-fired boilers in Western Europe (e.g., Austria, Denmark, Germany, Finland, Italy, and the Netherlands) and Japan are permitted to emit NOx at a rate of no more than 200 mg/Nm3 (about 0.16 lb/mmBtu).  Many boilers, however, emit at or below 0.12 lb/mmBtu.

Thus, with appropriate incentives (e.g., trading, compliance flexibility, and the lack of technology mandates), the industries affected by NOx reductions can be expected to respond in innovative ways to increase NOx control performance and decrease overall costs of compliance far below those currently predicted.

STATES' REPORT

on

ELECTRIC UTILITY

NITROGEN OXIDES REDUCTION TECHNOLOGY OPTIONS

FOR APPLICATION BY THE

OZONE TRANSPORT ASSESSMENT GROUP

SECTION 1

INTRODUCTION

1.1.  BACKGROUND

This document provides a brief overview of NOx control technologies for fossil fuel-fired electric utility power generation equipment.  The information contained in this report draws upon material assembled by the Ozone Transport Assessment Group (OTAG) Control Technology Workgroup between August 1995 and February 1996.

1.2.  OBJECTIVE OF THIS REPORT

The objective of this report is to provide a succinct, simple summary of technology options to control NOx emissions in the OTAG region.  It builds upon several recent reports which provide comprehensive, in-depth overviews of NOx control technology options.  One of these, prepared for NESCAUM, MARAMA, and the EPA Office of Air Quality Planning and Standards (Phase II NOx Controls for NESCAUM and MARAMA Regions, November 1995) is a primary source for this document.  Where data is available, this report also considers actual retrofit experience to date and vendor quotation information concerning the cost and technical effectiveness of NOx control technology options.

1.3  FOREWORD

The NOx control technologies considered in this report are viable and commercially available for the indicated boiler types and fuels.  These control technologies have been proven by application at both domestic and international sites.

As with any technical solution, several key issues influence cost, effectiveness, and choice of technology regarding NOx controls.  For example, NOx controls for a large electric boiler must be tailored to reflect fuel type and composition, operating or duty cycle of the boiler (e.g., baseloaded or subject to frequent load changes), and physical characteristics of the boiler and its site (e.g., space constraints, equipment limitations, flue gas residence times, availability of secondary or alternative fuels, etc.).

Coupled with increasing regulatory flexibility in pursuit of innovation, and growing competition among manufacturers of various NOx control technologies, control options are rapidly multiplying and no single NOx control technology can be expected to always perform best at every site.

1.4.  SUMMARY AND CONCLUSIONS

The OTAG region contains almost 900 coal-fired boilers and nearly 600 oil and natural gas-fired boilers of varying age, size, and design.  However, 25% of all utility NOx emissions (about 1,400,000 of 5,600,000 tons per year in 1990) are emitted by just 7% of boilers:  approximately 110 coal-fueled cyclone and cell-fired boilers included in Group 2 of the Clean Air Act (CAA) Title IV Acid Rain program.  Almost half (45%) of total utility NOx is emitted by just 200 sources.  About 60% of utility NOx emissions (about 3,300,000 tons per year) is emitted by 47% of the boilers:  the roughly 700 coal-fueled, wall-fired and tangential-fired boilers included in Group 1.  The remaining 600 boilers--40% of all boilers--emit just 15% of all utility NOx emissions.

The intent of this report is not to address each and every conceivable retrofit scenario.  Instead the NOx control technology costs presented in the Summary Matrix (Section 8) are intended to provide a range of cost-effective solutions generally applicable to the multitude of boiler types, ages, fuels, and control technologies that currently exist across the wide geographic region of the 37 OTAG states.  Notwithstanding occasional exceptions due to extreme boiler-specific limitations, the vast majority of NOx control technology retrofits in the OTAG region should be achievable within the cost and performance ranges illustrated in the Summary Matrix.

Post-1991 commercial and field experience in the United States with both coal-fired and gas-fired boilers confirms that robust NOx control technology options are more technically feasible and cost effective than previously believed.  Recent technological advancements and innovations, increasing pressure for open transmission access and deregulation of electrical generation, and greater understanding of the profound health and environmental impacts of utility emissions have combined to shepherd a number of low capital, highly effective control technology options into proven commercial availability.

For example, the 1995 SCR retrofit of a 330 MW cyclone boiler in New Hampshire--which involved substantial difficulty and was accomplished in an extremely short timeframe which included winter conditions--demonstrates that at over 85% of NOx can be removed at a per ton cost of about $400 with capital cost under $60/kW.  Similarly, the SNCR and LNB retrofit of three boilers in Massachusetts in 1993 reduced NOx by over 65% for less than $700 per ton, with capital costs under $14 kW.  Busbar costs for the New Hampshire cyclone retrofit were about 3 mills ($0.003) per kilowatt-hour of electricity produced.  This figure is consistent with busbar costs for baseloaded units across all NOx control technologies estimated by STAPPA/ALAPCO (1994) to be typically at or below 3 mills.

Further, these costs are rapidly declining as control technology advances and its application becomes better understood.  The anticipated capital costs to control NOx emissions from 44 oil- and natural gas-fired Southern California Edison units totaling 13,000 MW, for instance, dropped from $952 million to $290 million--a 70% reduction--in just one year (between 1991 and 1992).  This was accomplished through:  (a) prudent, flexible selection among commercially available control technology options including combustion modification, ureabased selective non-catalytic reduction (SNCR), selective catalytic reduction (SCR), and repowering; (b) market driven innovations such as in-duct SCR, which eliminates the need for a full-size reactor; and (c) intense competition among suppliers of NOx control technologies.  The end result--a 90% NOx reduction from the base case--met the regulatory requirement of a system-wide average of 0.015 lb/mmBtu.

An often-overlooked sector of the electric utility industry which also merits some attention is that of peak shaving units.  Interim OTAG inventory data indicates that peak shavers comprise approximately ___% <<<what %>>> of total NOx emissions from the utilities.  Further, these units often operate at times when ozone and/or precursor levels are already elevated, thus magnifying their emissions impact.  Application of control technology equipment to peaking units has traditionally been difficult to classify as "reasonable" because their relatively limited use results in excessive amortization costs.  Technological progress in fuels, however, may now provide these sources with cost-effective NOx reduction options (i.e., $500-$2,500 per ton of NOx removed).  The availability of such options should lead to renewed regulatory consideration of NOx reductions from these high impact sources.

For overall comparative purposes, the utility average emission rate for all fuels over the northeast Ozone Transport Region (OTR) during 1990 was 0.649 lb/mmBtu:  43 times higher than rates already achieved in the United States using natural gas, and about 10 times higher than those reasonably achievable firing coal.  This extremely high NOx emission rate predictably yields extremely high daily, seasonal, and annual emissions in the eastern U.S.  As a result, OTAG has the opportunity to substantially reduce NOx emissions in a very cost effective manner.

Nevertheless, the application of NOx control technology in the OTAG region should not be accomplished by mandating the universal use of one specific control technology.  It is far more cost effective to establish performance-based standards and allow implementation flexibility and effective trading programs to achieve them.  For a small number of the 1,500 boilers in the OTAG region, for example, incremental control costs may be much higher than actual experience to date has shown.

The application of a flexible, market-based approach that allows multiple units under a single operator to be averaged together (or "bubbled"), and allows trading of emissions between different operators, provides an economical and cost-effective mechanism to meet overall regional emission reduction targets (including emission reductions for boilers that are expensive and difficult to control).  Trading alone can be expected to cut overall emission reduction costs by over 50% and performance-based standards encourage control technology suppliers to continually upgrade price/performance characteristics.

Further, these approaches are hardly unprecedented.  Averaging approaches have already been applied effectively in the Northeast to meet the RACT requirements of Title I of the Clean Air Act.  Southern California also allows system-wide averaging for all units operated by a utility.  The Title IV Acid Rain program promotes emission trading between different utilities, and a similar "Cap and Trade" approach recently developed by the NESCAUM/MARAMA states to implement the 1994 Ozone Transport Commission (OTC) NOx Memorandum of Understanding (MOU) will offer an economically attractive mechanism to meet future OTAG control requirements and responsibilities.

Finally, although by definition OTAG focuses on the transport of ozone and its precursors, other pollutants also subject to long range air transport (including fine particulate matter, mercury, and regional haze) appear to have profound human health and economic impacts--even greater than those of ozone in some cases.  It would thus be shortsighted for OTAG participants to endeavor to parse sensible, overall solutions common to multiple contaminants into distinct components in order to avoid solving overall transport issues once and for all.  OTAG's very existence, so soon after the great Acid Rain debate, illustrates that broad concerns about transported air pollutants are best addressed in an integrated and comprehensive fashion.

In short, it remains critically important to human health and environmental quality that state and federal regulatory agencies (economic as well as environmental), industry, and the varied publics represented by the OTAG region work together to achieve adequate emission reductions, in a cost effective manner, where they are most needed, for as long as they are needed.

SECTION 2

NOx FORMATION IN UTILITY BOILERS

AND COMBUSTION TURBINES

2.1.  INTRODUCTION

This section reviews the formation of nitrogen oxides (NOx) in utility steam boilers and combustion turbines.  The key mechanisms of NOx production are first summarized, followed by a discussion of control strategies.

2.2.  NOx FORMATION

NOx is formed through a chemical reaction between oxygen in combustion air and nitrogen, which is present in both the combustion air and fuel.  Two major mechanisms contribute to the formation of NOx during fossil fuel combustion:

Thermal NOx Formation.  Thermal NOx pertains to formation of NOx from the conversion of nitrogen found in the air.  The rate of thermal NOx formation during combustion is highly dependent on temperature and oxygen concentration.  In order to minimize thermal NOx formation, it is necessary to reduce combustion temperatures and to minimize oxygen concentration in the combustion gas.  For fuels which contain no inherent nitrogen (e.g., natural gas), essentially 100% of NOx is thermal NOx.  Thermal NOx formation from heavy fuel oil combustion represents approximately 20-40% of the total NOx produced.  For coal, thermal NOx can comprise approximately 20-50% of the total NOx generated from conventional pulverized coal boilers.  This contribution can vary significantly depending on boiler design and fuel properties.

Fuel NOx Formation.  Fuel NOx pertains to NOx emissions from the conversion of nitrogen organically bound in the fuel itself.  This mechanism represents 50-80% of the NOx produced from heavy fuel oil combustion, and approximately 60-80% of the NOx produced from pulverized coal combustion.  Formation of fuel NOx is also affected by fuel type, excess air, burner design, and type of boiler.

2.3.  DESIGN AND OPERATING FACTORS

Design and operating factors which affect NOx production are briefly discussed for both steam boiler and combustion turbine equipment.  These factors include burner design, combustion system heat release rate, operating load, and fuel composition.

2.3.1.  Burner Design

Burner designs that rapidly mix fuel and air promote both thermal and fuel sources of NOx.  For utility steam boilers, prior to the advent of NOx concerns over 25 years ago, burners were designed to allow compact (and inexpensive) furnaces.  These conventional burners intentionally produce short, compact flames that rapidly mix fuel and air, and utilize fuel with high efficiency.  In contrast, present day design criteria for low-NOx burners ("LNB") allow more gradual mixing of fuel and air, creating conditions that minimize NOx production.  The resultant flame shape can influence boiler performance, reliability, and operating characteristics.

For combustion turbines, design criteria prior to the advent of NOx concerns similarly demanded a high heat release, intense combustion process that produced a stable flame.  In contrast, low NOx combustion concepts specify operation at extreme excess air conditions to act as a thermal diluent, thus controlling peak temperatures.

2.3.2.  Combustion System Heat Release Rate

One frequently and widely used index of boiler design is the heat release rate per unit volume, specified in terms of Btu/ft3-hours.  This index reflects the "intensity" of the combustion process as determined by the rapidity of fuel and air mixing and the volume of furnace available to extract heat from the flame zone.  A high heat release rate per unit volume implies rapid fuel and air mixing, and limited furnace surface area to remove heat.  The higher this combustion "intensity," the higher the formation of NOx.  This concept of heat release intensity is equally applicable to combustion turbines.

2.3.3.  Operating Load

Another variable that may influence NOx is operating load, typically expressed in terms of percent of maximum capacity.  Operating a boiler at maximum load typically maximizes NOx production; both the rapidity of fuel and air mixing and the heat release rate per unit volume are maximized, thus creating conditions suitable to higher NOx formation.  There are exceptions to this relationship, particularly for tangential-fired boilers.  Higher NOx at partial load may result primarily due to the need for higher excess air levels at low load to maintain flame stability and steam temperatures.  For most steam boilers with conventional burners, NOx production increases with load.  However, recent continuous emission monitoring ("CEM") data analyzed by EPA suggests that when LNBs are installed, NOx emission rates do not significantly vary with load.

2.3.4.  Fuel Composition

As noted earlier, fuel-bound nitrogen ("FBN") is a key determinant of NOx production.  Despite significant research, the relationship between the properties of a fuel and the propensity to produce NOx is not yet fully understood.  FBN varies substantially by fuel type:

oNatural Gas and Light Fuel Oil:  These fuels do not contain nitrogen in any significant quantity, thus thermal NOx is the principle source.  Accordingly, all other factors being equal, these fuels generally produce the lowest NOx emissions.

oHeavy Oil and Pulverized Coal:  These fuels contain significant organically bound nitrogen which often represents the major NOx source.  (Heavy oil ranges from 0.4-0.7% nitrogen by weight.  Coal ranges between __-__% nitrogen by weight.  <<<what %s?>>>  Coal properties which affect fuel NOx formation are volatility, fuel nitrogen and moisture content, and the distribution of fuel nitrogen between the volatile and char fractions.

SECTION 3

ELECTRIC UTILITY NOx EMISSION CONTROLS:

REGULATORY FRAMEWORK

3.1.  INTRODUCTION

This section considers the key regulatory provisions which define current NOx emission control requirements for utility industry boilers.  It also addresses anticipated regulatory developments and other trends in the electric utility industry.

3.2.  CURRENT AND NEAR-TERM NOx EMISSION REQUIREMENTS

The Clean Air Act Amendments of 1990 (CAAA) mandated several NOx control requirements and regulatory reviews associated with NOx controls on electric utility boilers and combustion turbines.  The requirements and reviews include NOx reductions:  (a) in certain areas designated under Title I for attainment of the ambient ozone standard; (b) nationwide under Title IV (e.g., the "Acid Rain" requirements), and (c) for new sources as dictated by revised New Source Performance Standards (NSPS).  Each of these is briefly reviewed in this section.

3.2.1.  Title I--Provisions for Attainment and Maintenance of National Ambient Air Quality Standards (NAAQS)

NOx limits promulgated under this Title for ozone include the application of "reasonably available control technology" (RACT) for major NOx sources, including utility boilers and turbines, in designated ozone nonattainment areas.  RACT determinations, which are made by the States, typically specify control technologies by source type, but different determinations can be made on a case by case basis via a "RACT Order" process.  The U.S. Environmental Protection Agency (EPA) has issued guidance suggesting that NOx RACT for utility boilers is typically combustion modifications (such as low NOx burners), but States have issued their own NOx RACT guidelines and rules defining flue gas recirculation, burners out of service, SNCR, SCR, or other control options as RACT in specific situations.  For affected ozone nonattainment areas and the entire Northeast Ozone Transport Region (OTR), NOx RACT controls were required by May 31, 1995.

In the OTR, twelve of the thirteen jurisdictions (twelve northeastern states and the District of Columbia) have signed a Memorandum of Understanding (MOU) agreeing to promulgate regulations that impose NOx controls beyond the level required by RACT for utility and other boilers with a minimum gross heat input of 250 million Btu per hour.  The MOU requires boilers within the OTR to meet the least stringent of the NOx reductions listed below.  A regionwide trading mechanism is being developed for NOx emissions in order to facilitate the achievement of these reductions in the most cost-effective manner.

oThe "Inner Zone":  Reduce NOx emissions by 65% from base year levels (generally 1990 emissions) by May 1, 1999; or to meet a NOx limit of 0.20 pounds per million Btu of heat input (lb/mmBtu, no averaging time specified).  Further reductions of NOx emissions, down 75% from base year levels or meeting a 0.15 lb/mmBtu limit, are required by May 1, 2003 (unless new modeling and analyses prove before 1999 that the OTC should modify the MOU).

oThe "Outer Zone":  Reduce NOx emissions by 55% from base year levels by May 1, 1999; or meet a 0.20 lb/mmBtu limit.  Further reductions of NOx emissions, down 75% from base year levels or meeting a 0.15 lb/mmBtu limit, are required by May 1, 2003 (unless new modeling and analyses prove before 1999 that the OTC should modify the MOU).

oThe "Northern Zone":  Reduce NOx emissions by 55% from base year levels by May 1, 2003; or meet a 0.20 lb/mmBtu emission limit.  Sources in this region are required to meet State NOx RACT requirements until May 1, 2003, however.

3.2.2.  Title IV--Acid Deposition Control

This Title calls for nationwide reductions in NOx emissions by the year 2000.  Coal-fired utility boilers will be required to meet new emission standards that will be implemented in two steps.

oPhase I Control Requirements for Tangential and Dry Bottom Wall-Fired Boilers:  Phase I limits are 0.45 lb/mmBtu for tangentially-fired boilers and 0.50 lb/mmBtu for dry bottom wall-fired boilers.  The Title IV NOx limits under both phases are annual averages.  The Phase I/Group 1 limits must be met individually, or under permitted averaging plans, by January 1, 1996 for approximately 220 boilers.  Alternative emission limits (AELs) are allowed if a specific boiler proves that it cannot meet its regulatory limit after properly installing and operating the appropriate control equipment.

oPhase II Boilers and Group 2 Boilers:  NOx emission limits for all Phase II boilers and Group 2 boilers (which include wet bottom wall-fired, cyclone, cell-burners, and all other coal-fired boilers) were proposed on January 19, 1996 and are expected to be final by January 1, 1997.  The rules allow for "grandfathering" Phase II, Group 1 boilers if they meet the limits that apply to Phase I boilers by January 1, 1997.

3.2.3.  New Source Performance Standards (NSPS)

EPA is currently reviewing NOx control requirements for new utility boilers and combustion turbines, and revisions to NSPS standards are expected within the next two years.  The revised NSPS standards, coupled with "best available control technology" (BACT) requirements under New Source Review, are expected to be significantly more stringent than current requirements.  In addition, EPA is in the process of revising the NAAQS for ozone and particulate matter.  EPA is also in the process of developing standards for regional haze and has recently proposed much lower standards for mercury emissions.  Given increasing evidence of serious human health impacts, these revisions can be expected to target further reductions of NOx and other emissions from new electric utility sources.

3.3.  FUTURE NOx EMISSIONS TRENDS

Future electric industry emission trends are difficult to forecast because several simultaneous dynamics exist, each of which could increase or decrease NOx emissions.  NOx emissions growth is clearly anticipated from existing sources that increase generation or capacity factor over historical levels in the wake of newly competitive electricity markets following utility deregulation or "open access."  Emission increases could also occur when new generation capacity is constructed, but given today's over-abundance of electricity and the substantial capacity currently unused, new construction appears unlikely in the near future.  NOx emissions should decrease as a result of existing regulatory requirements for NOx emission reductions and any additional ones adopted in the future.  In addition, any new generation which is built may have significantly lower NOx emission rates.

Estimates of the magnitude of NOx emissions reductions necessary to achieve attainment in the OTR range between 50-85%.  The 2005 CAAA inventory estimate used in the Regional Oxidant Model (ROM) over the OTAG "Superdomain" predicts that the following measures will achieve only a 22% reduction in NOx emissions from utility sources between 1990 and 2005:  <<<Cichanowicz Source?>>>

oCompliance with Title IV Acid Rain Phase I limits with no further NOx emissions decrease during Phase II

oRACT controls on all boiler types

oNo Acid Rain or RACT controls on most Group 2 coal-fired boiler types, including cell burners

o65-year life for existing units

oDepartment of Energy (DOE) projections and default parameters for the emissions production rate of new units

oSiting generic new units at existing plants

The above measures are neither particularly stringent nor adequately protective of public health, and additional measures need to be considered in light of:  (a) the evident need for greater emission reductions at upwind generating stations to abate the impact of long range pollutant transport upon downwind jurisdictions; (b) increasing scientific concern regarding the human health impacts of all utility emissions (SO2, NOx, fine particulate matter, mercury, etc.) and efforts currently underway to adopt more stringent NAAQS for ozone and fine particles; and (c) the elevated upwind emissions likely to result from the changing competitive environment for electric energy.

The nation is now undergoing concurrent and extraordinarily rapid change in:  (a) the improvement of the cost and performance of emission control technologies; (b) the revision of state and federal regulatory requirements, standards (e.g., ozone, fine particulate matter, regional haze, and mercury), and even approaches; and (c) the replacement by market forces of traditional regulatory oversight of utilities.  Keeping abreast of this moving target requires that new information or better informed assumptions be brought into the OTAG process as they become available.

SECTION 4

UTILITY BOILER AND COMBUSTION TURBINES:

DESCRIPTION OF EQUIPMENT

4.1.  INTRODUCTION

This section briefly describes the important attributes of utility combustion equipment used in both steam boilers and combustion turbines which influences production of NOx.  This discussion serves as a background to the consideration of emission control options in the next section.

4.2.  STEAM BOILERS

Steam boilers are discussed below according to their classification in the CAAA.  Wall- and tangential-fired dry bottom boilers are considered Group 1 boilers; and cyclone, cell-fired, wet-bottom, and miscellaneous boilers are collectively referred to as Group 2 boilers.

4.2.1.  Wall-fired Boilers (Dry Bottom, Group 1)

There are presently approximately 350 coal-fueled, wall-fired boilers operating in the OTAG region, capable of 94,327 MW of generating capacity.  In 1990 (the latest year for which information is available), this category of boilers produced approximately 1,724,000 tons of NOx annually or about 31% of utility NOx emissions.

Wall-fired boilers were manufactured by all four major boiler vendors and represent the largest single design category (55% of installed steam generation).  Wall-fired boilers employ individual burners, resulting in the combustion of fuel in the immediate vicinity of the wall.  Burners are located in either one side (front fired) or both sides of the boiler (opposed fired).  Typically, boilers less than 300 MW are front fired while most of the larger units are opposed fired.  Uncontrolled NOx emissions from these types of boilers typically range from 0.7 lb/mmBtu to 1.3 lb/mmBtu, depending on individual boiler design and coal type; typical units run about 1.0 lb/mmBtu.  Each of the four major boiler manufacturers, as well as ancillary equipment suppliers, have recently developed and retrofit many low NOx burners to older, existing furnaces in response to the RACT requirements of Title I of the CAAA.

4.2.2.  Tangential-fired Boilers (Dry Bottom, Group 1)

There are presently approximately 350 coal-fueled, tangential-fired boilers operating in the OTAG region, capable of 112,000 MW of generating capacity.  In 1990, this category of boilers produced approximately 1,572,000 tons of NOx annually or about 28% of utility NOx emissions.

Tangential-fired boilers represent approximately 40% of the utility boiler population.  This type of boiler is characterized by fuel and air introduction from the corners of the furnace, directed toward the tangent of an imaginary circle in the center of the boiler.  This type of fuel firing system is generally believed to allow the overall furnace to act as a single burner, with the fuel and air compartments serving as injection ports.  The slower mixing of fuel and air common in these boilers results in lower NOx emissions than wall-fired equipment.  Typical NOx emission levels for boilers constructed prior to 1970 (pre-NSPS) are 0.6 to 0.8 lb/mmBtu.  NOx emissions for the relatively few units constructed after 1970 (post-NSPS) range from 0.4 to 0.6 lb/mmBtu, as many were equipped with overfire air (OFA) as described later in this document.  The typical emission rate for tangential-fired boilers--at about 0.7 lb/mmBtu--is lower than the typical emission rate for wall-fired boilers.

4.2.3.  Cyclone Boilers (Group 2)

There are presently 77 coal-fueled, cyclone-fired boilers operating in the OTAG region, capable of 22,329 MW of generating capacity.  Based on 1990 emission rates, this category produced approximately 624,000 tons of NOx annually.

Cyclone-fired boilers, which comprise the largest category of Group 2 boilers, were manufactured exclusively by Babcock & Wilcox (B&W) from the late 1940s to the early 1970s.  Cyclone boilers are characterized by the combustion of fuel in a separate, remote chamber connected to the main furnace.  Crushed bituminous and/or subbituminous coal is fed into the cyclone furnace where it is fired under highly turbulent conditions, creating the high temperatures required to melt the ash subsequently removed at the furnace bottom through slag taps.  Prior to 1971, this design was an attractive alternative to pulverized coal-fired boilers since it:  (a) allowed the burning of low grade (high ash) coals; (b) significantly reduced the amount of fly ash in the flue gas thereby reducing the size of the furnace and particulate collection equipment; (c) reduced the degree of fuel preparation (i.e., elimination of pulverizers); and (d) maintained a very high heat release rate.

Cyclone-fired boilers have some of the highest NOx emission rates of all utility boiler types.  Typical uncontrolled cyclone NOx emission rates range from 0.8 lb/mmBtu to 1.8 lb/mmBtu; averaging roughly 1.4 lb/mmBtu.

4.2.4.  Cell-fired Boilers (Group 2)

There are presently 33 coal-fueled, cell-fired boilers operating in the OTAG region, capable of 24,143 MW of generating capacity.  Based on 1990 NOx emissions rates, these units produce approximately 724,000 tons of NOx annually.

The second largest category of Group 2 units in the OTAG region, cell-fired boilers employ multiple burners arranged in compact and discrete "cells."  These units, designed and constructed by Babcock & Wilcox, employ furnaces that feature either a 2-burner or 3-burner array within one cell.  The 2-burner array dominates the cell-fired boiler inventory, and thus is the focus here.

The close proximity of burners within cell-fired arrays and their compact geometry creates an intense mixing process and high heat release rate per unit volume of furnace, which promotes NOx formation.  Unlike cyclone boilers, cell-fired units employ pulverized fuel (bituminous coal), and thus approximately 80% of coal ash is entrained in flue gas as fly ash.

In the past, conventional low NOx burners (LNBs) have been difficult to apply to these units, as the delayed fuel and air mixing patterns characteristic of LNBs create relatively long flames.  During the last four years, however, LNB concepts developed by Babcock & Wilcox and Riley Stoker have been applied to cell-fired boilers.  In addition, the original boiler manufacturer (Babcock & Wilcox) has developed a Low NOx Cell Burner (LNCB) specifically for these units.

4.2.5.  Slag Tap (Wet Bottom) Wall-fired Boilers

There are presently 23 wet bottom, wall-fired coal-fueled boilers operating in the OTAG region, capable of 4,712 MW of generating capacity.  Based on 1990 NOx emission rates, these units produced approximately 291,000 tons of NOx annually.

Slag tap (wet bottom) wall-fired boilers are similar to cyclone boilers in that the high heat release rate furnace generates slag from coal ash, which collects at the furnace bottom, and is ultimately removed through a slag tap.  These units were designed and constructed generally from 1950-1960, almost exclusively by Babcock & Wilcox and the Foster Wheeler Corporation.  Like cyclone boilers, approximately 80% of the coal ash is directed to slag, and the remaining 20% entrained in flue gas as fly ash.

Though no LNB concepts have yet been applied to slag tap (wet bottom) wall-fired boilers, American Electric Power (AEP) successfully applied air staging (overfire air) to one slag tap (wet bottom) boiler, achieving greater than 40% NOx reduction at very low cost.  In addition, Public Service Electric & Gas (New Jersey) is experimenting with several burner modification concepts that, if successful, could produce 15-25% reduction in NOx emissions.

4.2.6.  Miscellaneous Boilers (Roof-fired, Stoker-fired Fluid-Bed Group 2)

Several smaller categories of boilers cannot be classified in any of the previously discussed boiler types.  The two largest are considered in this subsection.

Roof-fired.  There are approximately 30 roof-fired coal-fueled boilers operating in the OTAG region, capable of 3,111 MW of generating capacity, which (based on 1990 NOx emission rates) produce 66,000 tons of NOx annually.  A national total of 43 roof-fired boilers comprise 4191 MW of generating capacity, representing the fourth largest category of Group 2 boilers.

Roof-fired boilers (predominantly supplied by Babcock & Wilcox) employ vertical coal nozzles located in the boiler "roof," injecting pulverized coal with combustion air.  There are a wide variety of roof-fired boiler concepts, and depending on the specifics of fuel and air admission, the flame can be J-shaped, U-shaped, or entirely vertical.  Design information on these units suggests that short furnace residence times present difficulties in accommodating significant staging or delay of fuel and air.  Nevertheless, combustion modifications have met with significant success in altering the mixing patterns to reduce NOx emissions.

Stoker-fired.  There are presently approximately 20 stoker boilers comprising a total of 1160 MW of capacity in the OTAG region.  No estimate of NOx production from this category of boilers is available; however it is undoubtedly negligible due to small generating capacity and low capacity factor (typically _% or less).  <<<What %?>>>

Stoker boilers are generally moving chain grate units that fire crushed coal or other solid fuels that require significant residence time for acceptable combustion.  Many utilities employ stokers to fire alternate fuels as a supplement to coal (e.g., peat, shredded tires, etc.), so these units often operate at a low capacity factor.  Combustion NOx control measures for stoker-fired boilers are overfire air and flue gas recirculation.

4.3.  COMBUSTION TURBINES

Combustion turbines (CT) are essentially internal combustion engines that employ a rotary rather than reciprocating motion to extract power.  Unlike boilers that provide steam for expansion in a separate steam turbine, the CT is a single unit that creates and expands hot combustion products to drive a shaft for power production.

There are three primary components to a CT:  the compressor, combustor, and the turbine.  The compressor withdraws ambient air and pressurizes it to approximately 30 times atmospheric levels since combustion at elevated pressure improves efficiency and output.  The configuration of the combustor component dictates NOx formation.

NOx control strategies for CTs parallel those used for steam boilers:  reduce peak flame temperatures to minimize NOx formation from thermal sources, and/or alternatively employ oxygen-deficient combustion conditions to minimize NOx production from fuel-bound nitrogen.  Details of these strategies are summarized in Section 5.

4.4.  RECIPROCATING INTERNAL COMBUSTION ENGINES

Compression ignition reciprocating internal combustion engines, commonly referred to as "IC engines" are typically diesel engines whose niche in electric utilities is to serve as peaking units; providing additional generating capacity during conditions of exceptionally high electricity demand.

These units are often more basic and less sophisticated than mobile source diesel engines, although they are often supplied turbocharged.  The fuel most commonly used in these units is #2 diesel fuel.

NOx control strategies for diesel IC engines are three:  targeting combustion reductions by retarding ignition timing; reducing already formed NOx through selective catalytic reduction (SCR); or employing ultra low NOx alternative diesel fuels.

SECTION 5

NOx CONTROL TECHNOLOGIES FOR UTILITIES

5.1.  INTRODUCTION

This section overviews commercially available control technologies used to curtail NOx emissions from electric utility generating units (boilers, combustion turbines, and internal combustion engines).

NOx formed during the combustion of fossil fuels can be controlled by two principal strategies:  (1) modifying the combustion process within the "flame envelope" or within the furnace to reduce NOx formation; and (2) inducing chemical mechanisms to bond with NOx after it has formed, negating or "destroying" its character as an ozone precursor.  Generally speaking, modifications to the combustion process within the "flame envelope" involve staging the introduction of air and fuel at selected points of the combustion process in order to minimize the generation of "fuel NOx."  Modifications to or within the furnace itself endeavor to reduce furnace temperatures in order to avoid producing "thermal NOx."

The second strategy uses chemical reagents to convert already formed NOx into molecular nitrogen, water, and small amounts of byproducts through a chemical reaction known as "reduction."  This chemical reduction is called "selective" because the reagent injected reacts only with NOx, not with other flue gas constituents.  Commonly used reagents are ammonia (NH3) and urea.  One process, effective in the temperature window of 1600( to 2100(F, is called "selective non-catalytic reduction (SNCR)."  A second process, known as "selective catalytic reduction (SCR)," employs a catalyst to allow the reduction process to operate at temperatures of 450( to 1100(F.  Catalysts are usually proprietary and have a limited effective life (typically 6-10 years).

5.2.  NOx REDUCTION TECHNOLOGIES FOR UTILITY BOILERS

This section describes each of the major candidate NOx control technology options:  low NOx burners (LNB), overfire air (OFA), reburning, selective non-catalytic reduction (SNCR), and selective catalytic reduction (SCR).  Fuel switching and hybrid NOx control technologies are also briefly discussed.

5.2.1.  Low NOx Burners (LNB)

5.2.1.1.  Process Description.  Low NOx burners (LNB) delay the mixing of fuel and air within the immediate "flame envelope" to:  (a) create lower combustion temperatures to control "thermal NOx;" and (b) create chemical reduction zones within the flame to reduce NOx and precursor species.  For fuels with little or no nitrogen content (natural gas and light oil), the key contribution of delayed mixing is to reduce oxygen availability and extend flame length, thereby reducing both peak and average combustion temperatures.  For fuels with significant fuel-bound nitrogen (coal and heavy oil), delayed mixing serves to create chemically reducing conditions retarding combustion of fuel-bound nitrogen to NOx within the flame envelope.

Generally, most LNBs are "plug-in" mechanical devices that do not require significant changes to boiler components.  The physical condition of the ancillary equipment that influences process conditions within the flame can affect the performance of LNBs in terms of NOx control, emission of carbon monoxide (CO) and the quantity and nature of particulate matter (e.g., level of unburned carbon) and must be properly maintained and operated.  This ancillary equipment includes fuel preparation (e.g., pulverization) hardware and combustion control systems that determine burner-to-burner variations in air/fuel ratio.

Cell-fired units represent a special case of wall-fired boilers for which special LNB systems have been developed.  Specifically, in addition to the Babcock & Wilcox Low NOx Cell Burner (LCNB) technology, conventional LNB can be retrofit to these furnaces.

For tangential-fired boilers, LNBs differ in implementation compared to wall-fired boilers.  In contrast to wall-fired boilers, where individual burners establish a separate flame within an "envelope," tangential-fired boilers employ a circular mixing pattern within the entire furnace to mix and burn fuel and air.  Thus, LNB for tangential-fired boilers influence the fuel and air mixing process through biasing the fuel and air to different regions of the furnace.

5.2.1.2.  Retrofit Experience and Control Capability.  LNBs have been implemented on approximately 75,000-100,000 MW of capacity to comply with 1990 CAAA Title IV Phase I NOx limits, as well as RACT in selected regions.  LNB is the NOx control technology option with the largest experience base in the United States.  Several generations of LNB have evolved in the last decade; the most recent designs even provide for "internal staging" to create the physical and chemical conditions to effectively control NOx within a compact "envelope" surrounding the flame zone.

The experience from these installations suggests that typically, 40-60% NOx reduction is reasonably achievable depending on boiler design, coal composition, and operating duty.

For cell-fired boilers, at least six demonstration tests and early commercial applications have employed either B&W's Low NOx Cell Burner (LNCB) technology or conventional LNBs.  Results from these activities suggest that a 50% NOx reduction is reasonably achievable.

5.2.1.3.  Technical Feasibility.  Most boilers can be retrofit with some design of LNB.  The specific design of the LNB in an existing boiler depends on boiler design characteristics and fuel properties, and whether other NOx control technologies are used.  Three key variables that LNB manufacturers consider when installing LNB are:

Furnace Size / Heat Release Rate.  Most wall-fired LNBs produce a longer flame.  A relatively small furnace per unit of fuel burned may not be able to accommodate this extended flame length before flames impinge upon an opposite wall.  For these boilers, LNBs have to be selected and operated with care to prevent impingement upon the rear wall.

This consideration presented problems for early LNBs, since flame impingement can severely damage waterwalls and increase the frequency and severity of boiler tube failures.  Also, for coal-fired boilers, the change in heat release zone and the relocation of zones of oxidation/reduction can alter patterns of slag accumulation on furnace walls and the upper regions of the convective section.  Fortunately, LNB technology has evolved to mitigate these concerns, and LNBs are now available for most applications.

Boiler Operating Duty.  The load over which a boiler must perform, defined by the frequency and extent of turndown ratio (e.g., low load operation) can influence LNB operation.  Maintaining precise balance between fuel and air mixing systems depends on precisely controlling the momentum of fuel and air introduced into the furnace.

Though current research indicates that LNB effectiveness varies with load fluctuation much less than originally expected, NOx emissions controls targeted toward units with higher capacity factors (and higher emission rates) will still provide the greatest yield in terms of NOx reductions.  Further, over-control on such units can greatly reduce system average NOx emissions, potentially avoiding the need for controls on units with lower load profiles.  In addition, over-control on high load, high emission units will generate tradable NOx emission reductions credits.

Boiler Mechanical Features.  Besides the process-related issues described above, good LNB design can also mitigate mechanical complications (e.g., waterwall locations, furnace division walls, downcomers, windbox configuration, etc.) which could otherwise diminish the cost-effectiveness of retrofit LNBs.

5.2.2.  Overfire Air (OFA)

5.2.2.1.  Process Description.  OFA is another method to further "stage" the main combustion zone to minimize the formation of NOx.  OFA also lowers combustion temperatures, thereby reducing the formation of thermal NOx.  Installing OFA generally involves additional ductwork and the opening of new ports in the furnace wall above the main burner zone.  An exception to this rule on tangentially-fired boilers is "close-coupled" OFA, which is accomplished by rearranging air buckets and coal nozzles within existing burner openings.  OFA is usually installed in conjunction with LNBs, so the following discussion reflects this combined application, denoted as LNB/OFA.

5.2.2.2.  Retrofit Experience and NOx Control Capability.  OFA experience is less than for LNB, but is still considerable (approximately 20,000 MW) and includes many boiler types and fuels.  While OFA design was initially developed over thirty years ago, it has improved in the last decade from first-generation penetrations in the upper furnace to advanced versions that provide significant control over the quantity and velocity of injected combustion air.  This retrofit experience indicates OFA provides an additional 10-20% NOx reduction beyond that achievable with LNB alone.

5.2.2.3.  Technical Feasibility.  The feasibility of retrofitting OFA to existing boilers again depends on boiler design characteristics and fuel properties.  The principal design criterion is available residence time above the burners to (1) adequately mix the OFA with the combustion gases; (2) minimize unburned carbon; and (3) minimize NOx formation.  OFA may not be practical for boilers with inadequate flue gas residence time between the top burner row and the furnace exit.  Adequate space and access to install OFA ductwork and injection ports is also necessary.

Fuel properties also exert a significant role on the amount of OFA that can be employed and hence the NOx reduction which can be achieved.  Coal selection must be carefully tailored with regard to propensity for waterwall slagging, overall slag volume, and volatile carbon content.

5.2.3.  Coal Switching:  Bituminous to Subbituminous

5.2.3.1.  Process Description.  Converting existing boilers from firing bituminous to a subbituminous coal, such as Powder River Basin (PRB) may require an extensive review of potential equipment modifications and, if necessary, additions even at less than 100% conversion.  Equipment modifications or additions needed to handle larger volumes of highly volatile, low Btu subbituminous coals can affect several areas including:  (a) boiler modifications; (b) pulverizers; (c) electrostatic precipitator (ESP) and related particulate control equipment; (d) coal storage and handling dust control; (e) inserting systems for bunker fire protection, and (e) additional fuel delivery train sets.

5.2.3.2.  Retrofit Experience and NOx Control Capability.  Since the Title IV (i.e., acid rain) provisions of the CAAA for SO2, a significant number of utilities have switched coals from higher sulfur to lower sulfur coals as an SO2 compliance strategy.  Though most coal switches were from high-sulfur bituminous to low-sulfur bituminous, some utilities retrofitted to low-sulfur subbituminous coals.  It is estimated that 50,000-60,000 MW of coal-fired capacity have switched or blended fuels to meet the Phase 1 SO2 control limits.  <<<Source of estimate?>>>

Though there appears to be no difference is NOx emissions when switching from high-sulfur to low-sulfur bituminous coals, NOx emissions can be influenced (higher or lower) when switching to subbituminous coals.  The amount of NOx production (higher or lower) resulting from conversion to subbituminous coal depends on the properties of the subbituminous fuel compared to the original fuel, the fraction of fuel consumption converted, and the impact of fuel characteristics on the boiler.  Based on experience with current coal conversions, NOx reduction on the order of 20-40% can be expected when switching to Powder River Basin subbituminous coal.  Several units in the Southern Company system--originally designed to meet NSPS--are firing Powder River Basin coal and have demonstrated NOx reduction of approximately 40%.  These units are:  (a) Plant Miller Unit 4 (660 MW, wall-fired); (b) Plant Daniel Units 1 and 2 (each 500 MW, tangential-fired); and Plant Scherer Units 3 and 4 (818 MW, tangential-fired).

5.2.3.4.  Technical Feasibility.  Converting most existing coal-fired boilers from bituminous to subbituminous coal is generally feasible, but difficult to project in terms of cost.  The cost to modify the boiler and plant fuel handling systems is highly variable, ranging from approximately $15/kW to $60/kW.  Newer boilers, such as those designed to meet NSPS, may not require significant cost ho convert to subbituminous coals, and may not incur performance penalties.  Because of highly variable cost and boiler/plant impacts, conversion to subbituminous coal is not included in the Summary Matrix.

In addition to switching to subbituminous fuels, several organizations (e.g., Shell Oil) are developing processes to produce ultra low nitrogen content fuels to provide NOx reductions in commercial systems.

5.2.4.  Fuel Switching:  Coal to Natural Gas

5.2.4.1.  Process Description.  Converting coal-fired boilers to 100% natural gas firing requires:  (a) natural gas access at the site; and (b) modifying existing burners for dual fuel capability, if that capability is not pre-existing.  For conventional or low NOx circular burners on one or opposed walls in the furnace, the retrofit of 100% gas firing can be accomplished with the addition of gas spuds, canes, or gas rings.  Tangential burners in the corners of the furnace can also be modified to accommodate gas firing without affecting coal-firing or oil-firing capability.  For units with existing gas capability, switching to natural gas is a relatively low capital cost control option; for those without natural gas availability at the site, fuel switching is unlikely to be an economic alternative.

5.2.4.2.  Retrofit Experience and NOx Control Capability.  The NESCAUM-MARAMA Phase 2 NOx Control Technology report (Castildini, 1995) lists approximately 4000 MW of coal-fired boilers that have converted to 100% natural gas firing for at least part of annual operation.  Data from these units show conversion to natural gas can reduce NOx from 25-75%, depending on the combustion firing system and operating load.  The relatively wide range of NOx reduction is due to the strong interrelationship between NOx production mechanisms and furnace design, and the method of natural gas introduction into the furnace and flame zone, as previously described.

Applying combustion modifications appropriate for natural gas-firing will provide additional NOx reduction beyond that derived simply by switching to natural gas.  These combustion modifications include techniques such as flue gas recirculation (FGR) and burners-out-of service (BOOS).

5.2.4.3.  Technical Feasibility.  Converting coal-fired boilers to natural gas is technically feasible.  Both compromises and improvements to selected performance features can accompany a switch to natural gas.  These compromises or improvements include:

oCapacity Derate or Increase.  Natural gas delivers less heat to the furnace per unit volume of combustion products.  Por boilers in which flue gas handling capacity limits heat delivered to the furnace, steam and power production will be compromised.  However, this capacity derate penalty--which can be 5-15% of maximum capacity--is not encountered in many applications.  Conversely, it is also possible that conversion to natural gas could increase net generating capacity, particularly for cases where:  (a) the significant auxiliary power burden necessary for coal-firing is removed due to the use of gas; (b) furnace slagging limits boiler steam production; and (c) draft fan capacity does not limit maximum operating load.

oSteam Production Characteristics.  Firing natural gas reduces furnace gas exit temperature (FGET), distorting the heat delivered to superheat/reheat sections, altering the characteristics of steam produced, and impacting performance and turbine efficiency, as well as generating capacity.  As noted above, however, these characteristics of conversion may represent compromises or improvements, especially in net generating capacity.

oThermal Efficiency.  Boiler thermal efficiency can be reduced by firing natural gas due to the higher hydrogen/carbon ratio of the fuel, and the higher latent heat losses.  The magnitude of this reduction can typically be 1-2% of boiler thermal efficiency.  Depending on the specific unit, however, some, all, or more than this penalty may be compensated by the reduction in auxiliary power necessary to operate equipment to support coal-firing (pulverizers, ESP, sootblowers, etc.).

There are additional benefits to switching to natural gas, related to both environmental and performance issues.  Specifically, the use of natural gas reduces emissions of SO2, opacity/particulate, and CO2.  Operating benefits are the potential for reduced maintenance expenditure, coal inventory, and the influence of ash deposition.  In addition, improvements to peak capacity, tolerance to coal type, unit availability, ash quality and resale value, minimum load achievable, and startup are also possible.

5.2.5.  Fuel Reburning

5.2.5.1.  Process Description.  Reburning redistributes a portion of both fuel and air into the upper regions of the furnace to create a second flame zone, generating chemically reducing conditions to destroy NOx.  In most fossil fuel-fired boilers, reburning is applied between the upper burner row and the furnace exit, and any fuel can be utilized as the "reburn" fuel.  Most reburn applications divert between 10-20% of the total heat throughput to the upper furnace.  Reburn installations are engineered to maintain acceptable furnace and boiler performance while diverting heat release and absorption from the lower regions of the furnace (dominated by radiant heat transfer) to the exit (dominated by convective heat transfer), minimizing unburned carbon.

At least five coal-fired demonstrations of reburn are either operating or completed, and several additional demonstrations are expected to be operational within the next 6-12 months.  Reburn technology does not impose new operating requirements upon the boiler maintenance staff, and the only modification is the relocation of fuel and air into ports in the upper furnace region.  On the contrary, reburning, particularly with natural gas, provides significant operational flexibility due its ability to be "tuned" for specific boiler conditions.  In addition, gas-based reburning provides collateral benefits through reduced emissions of air toxics, mercury, and SO2 and diminished solid waste (ash) concerns.

Further, the "winter peaking" character of the natural gas demand stands in direct contrast to the summertime peaking of ozone production.  This phenomenon, in conjunction with an emission reduction credits trading program, allows gas reburn to provide sources with substantial compliance flexibility.  In the summer, low NOx emissions can be produced since natural gas is typically plentiful.  In the winter, natural gas availability may be curtailed by high demand, but ozone production is also curtailed.  Thus, a compliance strategy combining gas reburn and credit purchases could enable utilities to achieve the requisite total NOx at a much lower cost than anticipated.  Cost savings over year round gas delivered under relatively expensive "firm" (vs.  lower cost "interruptible") contracts would be substantial, reducing compliance costs materially from those currently predicted.

NOx control for coal reburning is determined by several site-specific factors including:  flue gas residence time between the upper burner row and furnace exit, ability to locate reburn fuel injectors to allow adequate mixing with combustion products at the furnace exit, induced draft fan capacity, margin of acceptable operation of ESP and fly ash handling/disposal, availability of flue gas recirculation equipment, and space for reburn fuel supply equipment (e.g., pulverizers).  Site specific factors for gas reburning are similar for boilers themselves, though few if any--including residence time--appear to limit the applicability of reburn technology to most coal-fired boilers.  Gas reburning is also much less onerous regarding fuel-related issues and equipment (e.g., pulverization, ESP, ash, slagging, etc.).

5.2.5.2.  Retrofit Experience and NOx Control Capability.  Five demonstrations addressing natural gas and coal reburn have been either completed or are now operational that show the broad potential of the technology.

For natural gas reburn, these units are:

oIllinois Power--Hennepin Station:  approximately 75 MW; pulverized coal; complete.

oPublic Service Company of Colorado--Cherokee Station:  158 MW; pulverized coal; operational.

oOhio Edison--Niles Station:  100 MW; cyclone; complete.

oCity Water Light & Power (CWL&P):  33 MW; cyclone; complete.

Reburning with coal has been demonstrated at:

oWisconsin Power & Light (WP&L)--Nelson Dewey Station:  approximately 100 MW; cyclone; operational.

Several additional natural gas reburn demonstrations are underway and will soon be producing data.  Eastman Kodak Company's Unit No. 43 (equivalent to 60 MW) started up on February 5, 1996 and is now undergoing acceptance testing.  New York State Electric & Gas is installing gas reburn (with commercial guarantees) on Greenidge Unit 6, a 105 MW tangential-fired boiler with a current low NOx firing system; this unit is scheduled to be operational by the 1996 ozone season.  Also, the Gas Research Institute is scheduled to test low-cost gas reburn approaches at Duquesne Light's Elrama Unit 1 or 2 (112 MW, roof-fired) in May 1996, and at Commonwealth Edison's Joliet Unit 6 (a 337 MW cyclone) in September 1996.

In addition, natural gas reburn is being installed on a 600 MW unit in Scotland, and a 300 MW unit is operating in the Ukraine.  Italy has extensive experience with oil reburning and has a gas reburn installation planned.  Detailed discussion of most of these demonstrations can be found in the reburn technology sessions of the 1991, 1993, and 1995 EPRI/EPA Joint Symposia On Stationary Source Combustion NOx Control.

Reburn NOx control efficiency is the subject of some debate between reburn technology developers and potential utility end-users.  Results from the referenced demonstrations suggest NOx reductions as high as 65-70% can be achieved with natural gas reburning, and as high as 60% with coal reburning.  The NESCAUM-MARAMA Phase II report cites NOx reduction by gas reburn as 40-65% from uncontrolled levels and 25-50% in post-RACT applications.  Utility end-users consider 50-60% NOx reductions to be more accurate.  One utility analysis, however, is quite consistent with both current vendor guarantee ranges of 55-62% from uncontrolled levels and the NESCAUM-MARAMA figures.  It suggests that gas reburn NOx control for pulverized coal-firing is 54-62% for uncontrolled pre-RACT deployment, and 40-45% for post-RACT deployment.

"Utility vs. developer" disputes thus have little merit at this point.  With technology developers willing to guarantee NOx reductions in the range of 55-62%, reburn technology is now in a position to let the commercial marketplace determine first-hand what reductions are possible, at what costs, and with what guarantees.  Detailed engineering design studies have been prepared for several large boilers in the U.S. which confirm the applicability of natural gas reburning to these units.  Further, at least two vendors, Energy and Environmental Research Corporation (EERC) and Babcock & Wilcox (B&W), are actively marketing this technology to utilities for most boiler configurations, complete with performance guarantees.

5.2.5.3.  Technical Feasibility.  Generally, both gas and coal reburn can be applied to pulverized coal and most Group 2 boilers.  Technical feasibility is considered separately in the following discussion:

Gas Reburn.  Key factors influencing the technical feasibility of gas reburn are:  the boiler design; the ability of the furnace materials to resist corrosive actions created by fuel-rich conditions in the reburn zone; and the supply and availability of natural gas at the site.

oBoiler Design.  Traditionally, reburn has been considered feasible only for boilers in which sufficient residence time is available in the main furnace to allow for the injection, mixing, and subsequent reaction of secondary (reburning) fuel and combustion air.  As noted previously, adequate residence time from the top burner to where reburn fuel is injected has been believed necessary for reburning to be feasible.  For gas reburning, a residence time of about 1.2 seconds has been considered appropriate, based on general experience to date (DOE, 1994).  This duration is also consistent with a recent statement by Babcock & Wilcox that 1.0 second is necessary from the reburn burners to the furnace exit.

This traditional residence time caveat is in some doubt today, however.  Gas reburn achieved a 64% NOx reduction on CWL&P's 33 MW cyclone with only about 0.25 seconds available.  Further, a reburn installation on a roof-fired unit is currently underway at Duqesne Light's Elrama Station.  One gas reburn vendor believes that there is no minimum residence time requirement for gas reburn, though NOx removal and quantity of natural gas required could be affected for units with shorter residence times.  Experience to date suggests that most boilers will possess adequate residence time to accommodate effective natural gas reburning.

oFurnace Corrosion Resistance.  Reburning requires that a fuel rich zone within the furnace (corresponding to a reburn zone stoichiometry of 0.9) be maintained for an adequate residence time.  This can expose the furnace walls to oxygen deficient conditions, which can promote corrosion.  However, this surface chemistry is fairly well understood and detailed modeling, measurement, and testing have been directed toward this issue.  As a result, today's reburn process designs generally ensure adequate excess oxygen near the furnace walls to minimize this problem.  Experience to date with long-term reburn demonstrations has not identified serious corrosion problems.

oGas Availability.  Natural gas must be accessible at the site in sufficient quantity and under commercially acceptable conditions (e.g., cost and availability guarantees), since the price of natural gas in relation to coal for long-term use is the key reburn cost factor.  The availability and cost of providing a reliable long-term supply of natural gas must be considered in the context of local and national energy markets which, in the case of natural gas, are increasingly deregulated.  As a result, gas supply pricing, transportation, and services options open to potential utility end-users should continue to increase.

Fortunately, concerns about commodity natural gas supplies and pipeline availability are largely mooted by the fact that a large proportion of boilers suitable to gas reburn application are located in the Midwest where pipeline capacity is abundant.  For example, of the 89 Group 2 cyclone boilers affected by EPA's proposed Phase II NOx Control NOPR (Acid Rain), 77 of them are so situated.  In fact, 55% of these units either have gas service on site or are within five miles of major gas transportation pipelines.

Another interesting feature of gas reburn is the potential ability to recoup capacity losses incurred with a switch to subbituminous coal, due to a change in fuel preparation or ashing characteristics that influence fuel pulverization or boiler slagging characteristics.

Coal Reburn.  Employing coal as the reburn fuel entails feasibility issues similar to gas reburning.

oBoiler Design.  As with gas reburning, most important is upper furnace residence time, which due to coal combustion characteristics, must be greater than for gas reburning (approximately 1.5 sec).  Accordingly, boilers for which gas reburning is technically feasible may not be able to accommodate coal-reburning.  Other issues, such as the ability to retain superheat/reheat temperature, aggravated slagging/fouling characteristics, and possible corrosive actions within the fuel-rich reburn zone are also of interest.

oFurnace Corrosion Resistance.  Corrosion can be a concern for coal reburn, as the fuel-rich reburn zone contains a number of potentially corrosive species derived from sulfur and trace elements in certain types of coal.  However, results after two years operation of the WP&L Nelson Dewey demonstration do not indicate any significant furnace corrosion problems.

oParticulate Collection.  For cyclone boilers, coal reburn typically increases ash loading to the particulate collector.  Higher particulate emissions may result if the ESP is sized marginally for the inlet loading.

5.2.6.  Selective Non-Catalytic Reduction (SNCR)

5.2.6.1.  Process Description.  Selective non-catalytic reduction (SNCR) typically employs chemical injection of urea into the flue gas near the furnace exit or in the convection pass to chemically reduce NOx to nitrogen.  Ideally, reagent injection is within the 1800(-2100(F flue gas temperature window, although for nearly all commercial retrofits the injection equipment has been installed between 1700(-2400(F.  The physical location of this temperature zone in the boiler changes with load.  The relatively high temperatures of flue gas in these boiler sections promote high reaction rates so a catalyst is not required for significant NOx removal.

Reagent injection into the appropriate temperature zones sets up a series of competing chemical reactions whose aggregate "sum" at the furnace exit is:  (a) a reduction in NOx; (b) molecular nitrogen and water vapor; and (c) trace amounts of ammonia (NH3) referred to as "ammonia slip" or "residual NH3."  Ammonia slip can be more pronounced as:  (l) the reaction temperature decreases; or (2) excessive levels of reagent injection are applied in an effort to achieve NOx reductions beyond the capability of the specific unit.

Additionally, employing urea reagent (NH2COH2) may produce N2O (a "greenhouse gas") as a byproduct.  Flue gas SO3 content is also a factor influencing SNCR feasibility when firing higher sulfur fuel oils and coals due to the potential for fouling some types of air heaters.  However, this effect could also encourage less firing of high sulfur coal, with attendant benefits concerning sulfur and particulate emissions.

5.2.6.2.  Retrofit Experience and NOx Control Capability.  SNCR has significant experience on a wide variety of industrial and utility fuel burning equipment, and in recent years has been deployed extensively on utility boilers firing a wide range of fuels.  SNCR installation in Europe has been particularly widespread.  Recent utility demonstrations or commercial applications in the United States include:

oPulverized Coal-fired Boilers:

--New England Power:  Three units at Salem Harbor Station (85-155 MW)

--Eastern Utilities:  One unit at Somerset Station (112 MW)

--Pennsylvania Electric Company:  One unit at Seward Station (160 MW)

oCoal-fired Cyclone Boilers:

--Atlantic Electric:  Two units at B.L.  England Station (Unit 1, 138 MW firing 2.8% sulfur coal, is now in commercial service.  Unit 2,160 MW, will have SNCR applied in Demonstration and Test in the near future.)

--Public Service of New Hampshire:  Merrimack Unit 1 (120 MW)

oWet-bottom Pulverized Coal-fired Boilers

--Public Service Electric & Gas Corporation:  Mercer Station, Units 1 and 2 (each 320 MW units; comprised of parallel 160 MW furnaces) <<<SNCR or SCR or Both?>>>

oResidual (Heavy) Oil-fired Boilers:

--Connecticut Light & Power:  Two units at Norwalk Harbor Station (170 MW each)

--Atlantic Electric:  B.L. England Unit 3 (160 MW)

--Delmarva Power & Light Edgemore Unit 3

Acceptable ammonia slip levels and the NOx reduction points at which slip appears both vary on a case-by-case basis.  As a result, SNCR design parameters and operating procedures for any given unit are specified to maximize NOx reduction while staying below unacceptable ammonia emissions levels.

In the above cyclone demonstration units, NOx reduction of 25-40% was achieved.  NOx reduction at one permanent commercial installation was 20% at 5 ppm slip.  During initial commercial operation of SNCR at New England Power's Salem Harbor Unit 1, NOx reduction of 60% was achieved on a continuous basis with NH3 slip of 10-20 ppm.  The reductions achieved on Salem Harbor Unit 3 were somewhat lower, averaging about 55-60%.  The overall emission rates were reduced from 1.0 lb/mmBtu to 0.33 lb/mmBtu.

It is important to note that in many retrofit applications, a combination of technologies will be applied to optimize both the NOx reductions achieved and the costs incurred.  For example, prior to installing LNB at Salem Harbor Unit 2, tests indicated that SNCR could achieve a maximum of 60-70% reduction with SNCR alone, but this would have resulted in significant ammonia slip and corresponding deterioration of ash quality.  SNCR alone would have reduced NOx emissions by only about 50% before encountering ammonia slip (<10 ppm) and ash quality problems.  Since this unit was required to meet an emission limit of 0.33 lb/mmBtu on a long-term basis (i.e., about 67% reduction from its baseline of about 1.00 lb/mmBtu), the utility elected to install LNB to essentially cut the unit's baseline NOx in half and then to use SNCR to "trim" the resulting emissions to meet the regulatory limit of 0.33 lb/mmBtu.  This combination of LNB and SNCR eliminated the NH3 slip problem as well as its impact on ash quality.  Other hybrid technology applications now being demonstrated also offer great promise.

5.2.6.3.  Technical Feasibility.  SNCR feasibility for existing plants is dictated by the ability to:  (1) distribute reagent into the boiler to maintain optimum NOx removal without residual NH3 over a range of load and operating conditions; and (2) minimize the influence of any process byproducts (e.g., residual NH3) on plant equipment.

oReagent Distribution.  To achieve acceptable NOx reduction, reagent must be properly distributed within an appropriate temperature range; current commercial applications range from 1700-2400(F.

Boilers that operate in a cycling manner over a wide load range require more complex injection and control systems, which account for higher capital cost in the range presented in the Summary Matrix.  As noted previously, however, it is unlikely that SNCR would find initial application in cycling units.  NOx reduction credit (or "allowance") trading should reduce or eliminate the need for such high capital costs to be incurred.  Note also that at present, the largest successful SNCR application in the U.S. (PSE&G's Mercer Station) is comprised of two parallel 160 MW furnaces.

oByproduct Formation.  As noted previously, the level of NOx reduction attainable may be limited by site-specific tolerance limits for NH3 slip.  Excessive slip can promote deposits of ammonium sulfates and bisulfates on heat exchanger surfaces, and/or be adsorbed by and contaminate particulate in flue gas.  This is a concern when firing higher sulfur coal.

Formation of NH3 and N2O byproducts is discussed below for three categories of fuel to which SNCR can be applied:

Residual NH3 from Firing Natural Gas.  Without sulfur compounds or fly ash present in flue gas, residual NH3 becomes a local regulatory issue rather than an equipment operating limit.  Conceivably, up to 10-20 ppm slip could be tolerated, while achieving maximum NOx reduction.  No byproducts are produced that deposit on downstream equipment.

Residual NH3 from Firing Fuel Oil.  The presence of modest amounts of sulfur in fuel oil poses potential deposition and air heater fouling from ammonium sulfate/bisulfate compounds.  Possibly the most relevant experience--though now over three years old--is from Long Island Lighting Company's (LILCo) Port Jefferson (New York) Station SNCR demonstration.  Residual NH3 of 10 ppm was ultimately selected for this site as a maximum level, and most current SNCR applications in the U.S. are limited to this level.

Residual NH3 from Firing Coal.  Experience in the U.S. defining acceptable levels of NH3 slip with SNCR is growing.  At present, nine pulverized low-sulfur coal-fired stations use SNCR commercially; their experience suggests 5-10 ppm slip is the best range to maximize NOx reduction and minimize operational impact.

N2O.  SNCR may produce N2O (a contributor to global climate change) when urea is used as the reagent.  N2O production is not a fundamental flaw in urea-based SNCR, however, because methods to mitigate its production may be available.

5.2.7.  Selective Catalytic Reduction (SCR)

5.2.7.1.  Process Description.  Selective catalytic reduction (SCR) employs ammonia injected into the flue gas near the economizer exit to reduce NOx to molecular nitrogen.  A catalyst is employed to achieve significant NOx removal and ammonia utilization at flue gas temperatures that are appropriate for process reactors.  SCR can be applied to flue gas in the temperature range of 450-1100(F, but is frequently applied at 525-750(F.  Two byproducts are generated from SCR:  (a) residual ammonia or "slip," due to imperfect mixing or reaction of the reagent; and (b) SO3, which is oxidized from SO2 by the catalyst.

These byproducts are easily managed at the design stage:

oAmmonia slip is a design variable.  SCR systems are designed and operated based on the maximum ammonia slip acceptable at a given source.  Maximum ammonia slip for coal-fired designs is typically 5 ppm.  At sites where this concentration is problematic, however, additional catalyst can be employed to lower the concentration further.  Further, substantial recent progress in controlling ammonia slip is evident in the design and operation of new coal-fired boilers.  For example, U.S. Generating's Carneys Point (NJ), Logan (NJ), and Indiantown (FL) units, operating 24,18, and 5 months respectively, have ammonia slip levels under 0.2 ppm.

oSO2 to SO3 oxidation is also a design variable.  Since oxidation is controlled by catalyst selection, SO2 oxidation to less than 1% can be provided.

Generally, SCR can be applied to almost all generating units; one simply designs the installation for appropriate control of residual NH3 and oxidation of SO2 to SO3.  These process design decisions are not completely unconstrained, though, since adding catalyst to lower ammonia slip also increases SO2 oxidation.  In practice, however, a balance between these competing variables can be and has been achieved.

In Europe, coal-fired SCR installations were initially designed for a 5 ppm slip limit (Rentz, 1992).  Based on experience with absorption of NH3 by fly, ash, several units have found it necessary to increase the amount of catalyst and lower the maximum NH3 limit to 2-3 ppm (Rentz, 1992; Necker, 1989).  A residual NH3 limit of 5 ppm on an average basis (i.e., with occasional higher "spikes" allowed) may be broadly acceptable for low-sulfur coals depending on the flue gas fly ash content and composition.  Key to controlling the ammonium sulfate/bisulfate deposition byproducts is minimizing production of SO3 from SO2.

A key factor in SCR operations is the frequency with which catalyst must be replaced to meet NOx reduction and residual NH3 performance targets.  Until recently, catalyst replacement frequency was a source of debate between SCR control equipment suppliers and utility users.  However, recent catalyst technology has made substantial advances, and catalyst suppliers are now willing to subject their product life cycles to rigorous, lengthy commercial guarantees.  European experience indicates that coal-fired boilers employing a proper catalyst management strategy will enjoy an average catalyst lifetime of 6-10 years.  Vendors for PSNH's MK2 commercial SCR installation guaranteed a catalyst life of 6 years; PSNH itself anticipates an 8-year life.  New coal-fired boilers (e.g., U.S. Generating--Carneys Point and Stations in New Jersey) are securing vendor guarantees of a 10 year catalyst life.  For oil- and gas-fired boilers, catalyst suppliers are confident that an 8-12 year lifetime is possible.  Utility users typically use a 6-year life in planning exercises.  As discussed in a subsequent section, these assumptions are important in determining SCR cost.

Ammonia handling has also made significant strides.  In the past, this was a source of great concern; however aqueous-based ammonia handling systems for SCR are often less troublesome than systems handling non-aqueous ammonia, typically for SNCR applications.

5.2.7.2.  Relevant Experience and NOx Control Capability.  The design flexibility and superior performance of SCR in achieving NOx reductions has led to its adoption over a wide variety of fuel and boiler characteristics.  As noted above, SCRs are designed taking into account acceptable levels of residual NH3 and additional SO3.  These two design factors can vary between different applications and fuel types in a manner described as follows:

Coal-fired Applications.  Most early coal-fired applications are located in western Europe (notably Germany) and Japan.  Total inventory of coal-fired SCR approximates 50,000 MW.  <<<Any data on # units by country and new vs. retrofit?>>> A NOx reduction of 80% is the usual target for coal-fired applications, though some units in Germany provide NOx reductions as high as 90%.  These higher reductions have been properly targeted toward baseloaded, high-inlet NOx units.  European coals are typically of Australian, German, and Polish origin with sulfur content of 1.5%.  However, high-sulfur coal applications exist.  In some cases, American coal is used.

The success of SCR applications overseas, coupled with major recent advances in catalyst chemistry (e.g., resistance to premature catalyst "poisoning" by the arsenic commonly found in U.S. coals) has fostered a rapidly increasing experience base in the U.S., with SCR installations both on new units and retrofit applications.  Two new coal-fired units--U.S. Generating Company's Chambers and Keystone Works--are now operating with SCR.  Three additional coal-fired SCR units--U.S. Generating Company's Indiantown Station, Orlando Utilities' Stanton Station, and Southern Electric International's Birchwood Station--are under construction and will be operational within the next two years.  These five facilities total approximately 1,200 MW.

The first major U.S. retrofit installation of SCR on a coal-fired unit became operational in June 1995 on Merrimack Station Unit #2 (MK2) operated by Public Service of New Hampshire.  A cyclone boiler firing 1.5% sulfur coal, this unit generates 320 MW.  Typically baseloaded, MK2 had average hourly uncontrolled NOx emissions of 2.4 lb/mmBtu, with a maximum uncontrolled NOx emission rate of 2.66 lb/mmBtu.

Initially, MK2's NOx emissions rate was reduced from these levels to 0.92 lb/mmBtu, i.e., from 110 tons per day (TPD) to 37 TPD, for a reduction of about 65% with 5 ppm NH3 slip.  However, the unit's SCR reactor and ductwork was designed and built to meet OTC NOx MOU Phase III requirements (about 0.30-0.40 lb/mmBtu, 15 TPD, or 86% NOx reduction) simply by adding an additional layer of catalyst in the reactor.  This $18.5 million retrofit includes $14 million capital cost in 1995 and $4.5 million for future catalyst addition.  Annual ammonia and operating expenses are expected to be $1.5 million.  The capital cost for this retrofit was $57.7/kW; the cost of NOx removed is about $400/ton.

The physical layout of MK2 made its retrofit particularly challenging.  The distances between the boiler and its electrostatic precipitator (ESP), and between the ESP and the stack, are exceptionally limited, so the retrofit required splitting and extensively re-routing the pre-existing flue gas ductwork.  Also, flue gas handling ductwork was strengthened in the event the unit is ultimately converted to balanced draft gas handling.  This retrofit did not require upgraded fan capacity or air heater changes, but it was made more complex by an unusually aggressive compliance schedule.  A project of this magnitude typically takes over a year to complete; this installation was completed in about six months despite winter construction conditions.  Nevertheless, MK2's SCR has been operating above expectations since July 1995.

The cost effectiveness of the MK2 SCR retrofit has been criticized on the basis that its unusually high uncontrolled NOx emissions result in an artificially low per ton NOx removal cost.  However, even if MK2's pre-control NOx emission rate were 2.0 lb/mmBtu or 1.4 lb/mmBtu instead of 2.6 lb/mmBtu, the $400 per ton removal cost would only increase to $521 and $745 respectively, even before reduced ammonia and catalyst costs are subtracted.  Thus, even if MK2 had had an uncontrolled NOx emission rate closer to an average cyclone boiler, its cost effectiveness per ton of NOx removed would remain well within EPA's 1994 estimated RACT cost range ($160-$2,000 per ton).  Indeed, precisely because of its low per-ton retrofit costs, New Hampshire air regulators determined that RACT for this unit was SCR.

Finally, note that under the NOx emission reduction trading systems currently being developed, targeting individual coal-fired units with unusually high uncontrolled NOx emission rates for prompt SCR retrofit would maximize NOx reduction benefits for the costs incurred.  Such prudent economic and environmental behavior can be anticipated when regulatory flexibility (vs. broadly applicable technology mandates) and rational market dynamics are combined.

Dual-Fuel (Fuel Oil and Natural Gas) Applications.  Dual-fueled applications exist in Europe, Japan, and some North American sites.  Residual NH3 can react with SO3 in fuel oil since the modest quantities of sulfur in fuel oil (0.2-1%) are sufficient to generate SO3 levels similar to coal-firing.  <<<Source?>>>  A residual NH3 limit of 5-10 ppm is anticipated for fuel oil-fired SCR applications.  NOx reduction of 80-90% is possible under these conditions.

Natural Gas Applications.  Most recent SCR installations in southern California are designed for virtually exclusive firing on natural gas.  (Though natural gas is the principal fuel, SCR has been designed for 500 hours per year firing heavy (#6) fuel oil.) Natural gas firing has enabled small pitch, high activity catalysts to be applied.  Several innovative design concepts have been employed that reduce reactor size and initial cost.  These innovative "in-duct" designs are in part responsible for the decrease in capital cost witnessed for natural gas SCR applications in recent years.  For example, the overall capital cost for Southern California Edison declined by nearly three-quarters, from $1 billion to $290 million.

At present, 4,000 MW of gas-fired SCR capacity is operational in the U.S., and it is likely that significantly more capacity will be operating by 1999.  Residual NH3 of 10-20 ppm is allowed (if also allowed by the local regulatory agency).  Accordingly, NOx reduction of 90% has been achieved for many of these applications.  Southern California Edison's systemwide emission limit of 0.015 lb/mmBtu has been achieved for over two years.

5.2.7.3.  Technical Feasibility.  SCR design and cost for existing plants is dictated by:  (1) the ability to locate a reactor within the proper temperature window between the economizer and air heater (applicable to high-cost SCR retrofits only); and (2) the desire to minimize any byproduct deposition on plant equipment.  Generally, there are few technical issues with regard to the engineering and performance of the catalytic reactor in flue gas, since most performance parameters are design variables.  The principal engineering task is to integrate the SCR process and reactor into the plant in a fashion that minimizes impact on existing operations.

A major, two-year technical demonstration of SCR on high-sulfur coal (2.8%) was recently completed by the Southern Company at Georgia Power's Plant Crist.  Sponsored by the Electric Power Research Institute (EPRI) and the U.S. Department of Energy, with contributing efforts by eight major catalyst suppliers, this study demonstrated catalyst performance under high-sulfur coal process conditions to be acceptable, with catalyst deactivation rates as projected by the suppliers.  Some operating issues, however, (e.g., maintaining acceptable air heater performance and integrating reactor performance with the boiler economizer) have not yet been fully resolved for high-sulfur coal process conditions.

Thus, while several engineering issues must be faced in retrofitting SCR to utility boilers, few, if any, of these issues prevent the effective deployment of SCR.  These factors can, however, elevate the cost beyond the range expected for incorporating SCR into new coal-fired units.  Such factors include:  (a) the ability to configure an economizer bypass to provide the correct flue gas temperature range; (b) fan capabilities; (c) strengthening of ductwork to accommodate lower static gas pressure; (d) the ability of the air heater to tolerate deposition associated with residual NH3 and byproduct SO3; and (e) the ability of downstream processes (e.g., ash utilization or disposal) to tolerate specified levels of residual NH3.

Clearly, these engineering issues have been successfully overcome in Germany and Japan, where together approximately 50,000 MW of coal-fired SCR capacity has been operational for over 15 years (since 1980).  These factors have also been overcome in Public Service of New Hampshire's Merrimack Station Unit #2 SCR retrofit.  The international experience has already been useful and will likely be instrumental in addressing similar issues for the boiler designs and higher sulfur fuels utilized in the U.S., in order to determine which units can yield the greatest NOx reductions at the least cost.

At present, some debate remains between environmental control equipment suppliers and utility industry users regarding the significance of these engineering issues, the extent they have been resolved by international experience, and the ultimate impact they may have on SCR cost for U.S. applications.  A recent position paper issued on behalf of the environmental control technology suppliers cites the considerable experience internationally, arguing that this experience adequately addresses U.S. utility industry sites (ICAC, 1994).  A second paper summarizes SCR experience to date in Germany (Rummenhohl, 1994).  A position paper issued on behalf of the utility industry users elaborates upon factors that influence SCR cost for coal-fired units, dual-fuel (fuel oil and natural gas) applications, and natural gas-fired units, and the uncertainties for SCR application in the U.S. that remain despite the impressive international experience (Cichanowicz, 1995).  <<Is this paper available to OTAG?>>>

Ultimately this cost debate will be resolved by the marketplace rather than by policymakers, as environmental control equipment suppliers bid on--and guarantee the performance of--their new and retrofit control equipment installations.  Nevertheless, policymakers must be careful not to close the door of incentive on high-performance environmental solutions, given:  (1) the ability of emissions trading to simultaneously maximize environmental benefit and minimize societal cost; and (2) the historically poor correlation between early environmental cost impact predictions by industry and the actual control costs which eventuate.

5.2.8.  Hybrid Controls

5.2.8.1.  Process Description.  As the need for substantial, yet cost-effective reductions in NOx emissions has become increasingly dear, much field development has focused on compatibly combining existing NOx control technologies to yield superior reductions than individual stand-alone technologies can achieve.  These can include combustion/combustion combinations (e.g., LNB/OFA); combustion/post-combustion combinations (e.g., LNB plus downstream SCR); or most recently, post-combustion/post-combustion combinations.  The two former configurations are well established and have achieved significant penetration.  The latter combination, however, typically in the form of hybrid SNCR/SCR, has only been field demonstrated in the last year.

The strengths and weaknesses of SNCR and SCR technologies dovetail in a fashion that makes hybrid combinations of SNCR followed by downstream SCR a particularly flexible method for achieving deep reductions of NOx at reasonable cost.  Such hybridized SNCR/SCR are designed to manage the ammonia slip from the SNCR process and to utilize it as the sole NOx reductant feed entering the downstream SCR, thus eliminating the need for a separate ammonia handling and injection system to serve the SCR.  Cost savings from this hybridization principally result from the smaller size SCR reactor that is required to handle the lower NOx levels exiting the SNCR, and from the elimination of operating costs associated with stand-alone SCR ammonia injection.

Since ammonia slip from the SNCR and SCR catalyst performance are design characteristics, hybrid SNCR/SCR allows lifecycle NOx reduction costs to be minimized by determining an optimal balance between annualized capital costs (mostly attributable to SCR) and annual operating costs (mostly attributable to SNCR) for the life of the system.

5.2.8.2.  Retrofit Experience and NOx Control Capability.  As a relatively new technological option, hybrid SNCR/SCR has not yet achieved significant field penetration.  However, field demonstration work conducted during the last two years at Public Service Electric and Gas (NJ) (PSE&G) on a pulverized coal, wet-bottom boiler have provided proof-of-concept:  Hybrid SNCR/SCR NOx reduction performance was twice that of stand-alone SNCR at the same reagent feed rate.  Overall NOx reduction ranged from 86-90%.  Further, it appears that NOx reduction as high as 75% may be achieved with "in-duct" catalyst on a site-specific basis.  Utilization of existing ductwork can substantially reduce retrofit costs.

The capital costs of the stand-alone SNCR and SCR systems utilized in the PSE&G field demonstration were $14/kW (for 38% NOx reduction at 5 ppm NH3 slip) and $90/kW (for 90% NOx reduction capability) respectively.  This field demonstration verified that SNCR-related cost performance on a coal-fired unit can be improved substantially (in this case doubled), and accordingly, downstream SCR systems can be re-sized much smaller.

5.2.8.3.  Technical Feasibility.  The technical feasibility of urea-based SNCR intentionally providing ammonia slip as the sole reactant feed to a downstream SCR has been field proven, and hybridized SNCR/SCR systems should be capable of cost-effectively achieving 90% and greater NOx reductions.

The next step for field development of hybrid SNCR/SCR is to design and test an in-duct catalytic reactor downstream of a commercial SNCR installation on a pulverized coal-fired boiler.  This will allow assessment of the broad, cost-effective applicability of hybrid SNCR/SCR to various types of coal-fired units to be addressed.

NALCO Fuel Tech, which conducted the PSE&G demonstration, has commercially proposed a hybrid SNCR/SCR system for such a unit within the OTR.  This proposal promises to reduce lifecycle operating costs by increasing reagent utilization at modest catalyst capital costs.

Though as yet untested in commercial use, hybrid SNCR/SCR appears to offer great promise for large NOx reductions on coal-fired units at reasonable cost.  Hybrid SNCR/SCR is dearly among the technologies that promise to reduce actual compliance costs well below those currently anticipated by utilities in order to make the substantial NOx reductions which will be required in the future.

5.2.9.  Ultra Low NOx Fuels

5.2.9.1.  Process Description.  Most of the above NOx reduction control technologies focus on thermal NOx (via optimizing boiler and/or burner design), or on the removal of NOx already formed (whether of thermal or fuel-bound origin).  Little attention to date has been directed toward reduction of fuel-bound nitrogen, other than switching from higher to lower FBN fuels (e.g., coal to natural gas).  Sensing new market opportunities for NOx reduction solutions, some oil companies have begun to develop and market ultra low emission alternative fuels by targeting FBN content.

Such alternative fuels are particularly attractive control options for oil-fired peaking units because their comparatively low capacity factor renders equipment-based solutions difficult to amortize cost-effectively.  Alternative fuels are available as "drop in" replacements for #2 diesel fuel, reducing NOx as well as emissions of total hydrocarbons, SO2, particulate matter, and smoke.

These alternative fuels typically require no additional capital equipment.  They are simply a switch to a fuel with very low nitrogen content, which in turn can virtually eliminate NOx formation from FBN.  The absence of capital equipment costs means that emission reduction cost-effectiveness for units burning ultra low NOx fuels is independent of the amount of time they are used during the year.

5.2.9.2.  Retrofit Experience and NOx Control Capability.  As a relatively new NOx reduction option, ultra low NOx fuel replacement is just starting to penetrate appropriate markets, principally oil-fired peak shaving units.  Shell Oil, for example, has had significant success at Fort Bliss in El Paso, Texas, which has six 2,125 HP General Motors Electromotive diesel engines (approximately 35 years old) under contract to supply 9 MW of peak shaving power to El Paso Power.  A solution was required which would allow Fort Bliss to operate these engines at full output while not exceeding allowable emissions levels for NOx, CO, and opacity imposed by new operating permit requirements.  Engine tuning was unable to reach compliance, and capital equipment options (e.g., catalytic converters, natural gas conversion, or new engines) were uneconomical.  Testing determined that use of Shell's LOW NOX fuel would allow Fort Bliss to reach compliance.

5.2.9.3.  Technical Feasibility.  Though largely untested in commercial use, there is no reason to believe that ultra low NOx fuels possess any significant technical limitations that will curtail their use.  The principal limitation is one of cost, not technical concern, which is why these fuels are especially suited to peak shaving units.  Since significant utility NOx emissions are attributable to peaking units, ultra low NOx fuels represent a promising solution to a high impact source of NOx emissions.

5.3.  NOx REDUCTION TECHNOLOGIES FOR COMBUSTION TURBINES

NOx controls for combustion turbines (CTs) can employ a combination of three strategies:  (1) wet controls; (2) dry low NOx combustion controls; and (3) selective catalytic reduction (SCR).

5.3.1.  Wet Controls

5.3.1.1.  Process Description.  Injecting water into the flame of a CT provides a heat sink that limits thermal NOx.  If available, steam may be used as an alternative cooling media, depending on the particular application.

Water injection equipment consists of a water treatment system, pumps, water metering devices, injection nozzles, and the necessary plumbing.  A system to provide high water purity is essential to this process, so as to protect high temperature surfaces from deposition and/or erosion.

5.3.1.2.  Retrofit Experience and NOx Control Capability.  No accessible reference detailing commercial experience with wet controls could be found.  However, each of the major CT manufacturers offers wet controls and routinely provide process guarantees to meet a 25-90 ppm NOx limit depending on fuel fired.  Accordingly, experience should be extensive and adequate to support broad application.

Injection of water or steam into the combustor to meet the 25-90 ppm limit suggests a NOx reduction of 70-90% from uncontrolled levels.  Actual NOx reduction depends on the specifics of the combustor design, and the fuel employed (e.g., natural gas or distillate fuel oil).  Generally, CT wet controls can achieve approximate emission levels of 25-42 ppm (at 15% O2) with natural gas firing, and 42-75 ppm firing distillate oil.

The most significant factor in wet control performance is the water-to-fuel ratio (WFR), reflecting the quantity of cooling media injected.  For natural gas fired CTs, WFR for either water or steam of 0.33-2.48 is necessary to control NOx emissions to 25-42 ppm.  For fuel oil fired CT, WFR for either water or steam of 0.46-2.28 is necessary to control NOx to 42-90 ppm.

Other significant factors affecting wet control system performance are the combustor geometry and the location and design of the water/steam injection nozzles.  For maximum NOx reduction efficiency, cooling media must be uniformly injected and dispersed within the combustor to create a homogenous cooling pattern.

Wet controls reduce only thermal NOx, but this source comprises all NOx from natural gas firing and almost all NOx from distillate fuel oil.

5.3.1.3.  Technical Feasibility.  Wet controls can be retrofit to most CTs.  The most significant barrier exists for units with dual fuel capability, since the space constraints imposed by the presence of two sets of fuel injection nozzles may limit access for water or steam injection.  In addition, there have been limited episodes in which water-induced dynamic pressure oscillations have increased maintenance requirements.

Some existing CTs may employ water injection to augment power production by 6-8% in summer months.  It is possible this concept could be applied as a seasonal NOx control strategy that provides a small capacity increase, thus partially offsetting other costs.  All wet controls impact CT thermal efficiency by 2-4%.

5.3.2.  Combustion Controls

Combustion controls consist of either the Lean Combustion or Lean Premixed System which have been deployed on new CT units in recent years.  In addition, an advanced combustion control concept referred to as Rich/Lean Quench is evolving for new CT application.  The lean combustion and lean/premixed systems are most commonly deployed as alternatives to wet systems.  The rich/lean quench concept is evolving at present, so it is not addressed in detail.

5.3.2.1.  Process Description.  Both lean combustion and lean premixed systems rely upon the principle of employing significant excess air in the combustion process to provide thermal diluent, thus reducing peak flame temperature and thermal NOx production.  As a result, the primary factors affecting NOx control performance are the air/fuel ratio and the type of fuel fired.  Employing lean design concepts do not require significant modification, except for provisions to maintain a stable flame at low operating load.  Employing the premixed lean concept requires a different fuel preparation system and the fuel and air mixing strategy differs.

5.3.2.2.  Experience and NOx Control Capability.  Most major CT manufacturers offer lean and lean premixed controls, and they routinely guarantee a 9-65 ppm NOx limit depending on fuel fired.  Thus again, experience should be extensive and adequate to support broad application.

Lean and Premixed Lean system NOx reduction strongly depends on fuel type.  For natural gas-fired CT, control of NOx to 9-42 ppm has been achieved, reflecting NOx reductions similar to wet systems (70-95%).  For fuel oil-fired CT, NOx can be controlled to 42-65 ppm, depending on the combustor concept.  Control of NOx to these levels represents a reduction of 60-90% from uncontrolled values.

5.3.2.3.  Technical Feasibility.  Essentially all Lean and Premixed Lean control options are technically and commercially feasible, although primarily as part of a new unit design.  It is conceivable that these strategies can be retrofitted to an existing combustor; however the broad retrofit/ability is not clear.

5.3.3.  Selective Catalytic Reduction (SCR)

5.3.3.1.  Process Description.  Selective catalytic reduction (SCR) can be applied to CT in a manner similar to that for steam boilers.  CT applications with either a heat recovery steam generator (HRSG) or in a combined cycle application deploy SCR at flue gas temperatures similar to applications on steam boilers (550-750(F).  However, the largest number of potential applications is the "simple cycle" employing flue gas temperatures of 800-1100(F.  Recently, catalysts for this relatively high temperature application have been successfully demonstrated, and SCR is now viable on "simple cycle" CT applications.

5.3.3.2.  Experience and NOx Reduction.  There are approximately 5,000 MW of CT equipped with SCR in either combined cycle or HRSG applications for a variety of applications (e.g., industrial steam production and cogeneration).  Simple cycle or "high temperature" SCR applications are increasing, now approaching 500 MW on approximately 10-15 units.  For both HRSG/combined cycle and simple cycle applications, natural gas is the predominant fuel.  Fuel oil applications are limited.

SCR can provide 80-90% NOx reduction, depending on the amount of residual NH3 that can be introduced into the flue gas, and the SO3 that can be tolerated.  For exclusively natural gas-fired CT, 90% NOx reduction is achievable as no significant residual NH3 exists.  For distillate fuel oil applications, NOx reduction may be limited to 80% as the role of SO3 (generated from trace quantities of SO2) may present ammonium sulfate/bisulfate deposition problems.  <<<Source?>>>

5.3.3.3.  Technical Feasibility.  SCR is technically feasible for most applications employing HRSG or combined cycle application.  Recent demonstrations and commercial applications of catalysts from zeolites and other materials assure SCR feasibility for simple cycle conventional and high temperature applications.

5.4.  NOx REDUCTION TECHNOLOGIES FOR RECIPROCATING INTERNAL COMBUSTION ENGINES

Use of compression ignition (reciprocating) internal combustion (IC) engines in the electric utility industry primarily involves peak shaving units.  NOx controls for IC engines can employ three strategies individually or in combination:  (1) retarding ignition timing; (2) selective catalytic reduction (SCR); and (3) ultra low NOx diesel alternative fuels.

5.4.1.  Ignition Timing Retard

5.4.1.1.  Process Description.  Ignition timing retard lowers NOx emissions by moving the ignition point to later in the stroke.  With the piston already moving downward, the combustion chamber volume is increased and the peak flame temperature is lowered, thus reducing thermal NOx formation.  It is effected by retarding the point at which the diesel fuel is injected into the cylinder.  The amount of reduction in NOx will vary depending on specific engine design and operating conditions, but there is a limit to which any engine can be retarded.

5.4.1.2.  Experience and NOx Reduction.  Retarding IC engine ignition is a well-established emissions control procedure.  NOx emission reductions achievable with this control option can be 20-30%.

5.4.1.3.  Technical Feasibility.  The technical feasibility of ignition timing retard is clear; it is already in widespread practice.  It is limited, however, in that any amount of retard is typically accompanied by some decrease in fuel efficiency (and thus a corresponding increase in fuel consumption and cost).  Excessive retarding can lead to engine misfires and rapidly increasing levels of smoke and particulate emissions.

5.4.2.  Selective Catalytic Reduction (SCR)

5.4.2.1.  Process Description.  The nature of SCR has been extensively covered in earlier sections of this report.  Attributes of SCR which relate specifically to IC engines are considered below.

5.4.2.2.  Experience and NOx Reduction.  NOx emission reductions achievable with this control option are in the range 80-90%.

5.4.2.3.  Technical Feasibility.  Variable load IC engines require more sophisticated SCR systems, which adds to their already high capital and operating costs when applied to peak shaving units.  Fuel composition can also be a concern since fuel properties which extend engine life can reduce catalyst life and vice versa.  High sulfur fuels or the presence of phosphorus can contaminate catalyst, for example, while some engine manufacturers have expressed concerns that low phosphorus oils could reduce engine life.

5.4.3.  Ultra Low NOx Alternative Fuels

5.4.3.1.  Process Description.  Alternative diesel fuels are now available which can significantly reduce NOx and other emissions in comparison to #2 diesel fuel.  These fuels simply replace #2 diesel and require no additional capital equipment, though some resetting of existing equipment may be necessary to optimize operation.

5.4.3.2.  Experience and NOx Reduction.  Ultra low NOx alternative fuels are currently finding initial market acceptance among peak shaving units with particular emissions constraints.  NOx emission reductions achievable with the use of such fuels can be in the 80-90% range.

5.4.3.3.  Technical Feasibility.  The technical feasibility of ultra low NOx alternative fuels is relatively secure.  The higher costs which position such fuels appropriately for peak shaving units, however, will limit their use for more extended applications.

SECTION 6

INCREASING EMISSION REDUCTION REQUIREMENTS

AND DEREGULATION OF THE ELECTRIC UTILITY INDUSTRY

6.1.  INTRODUCTION

This section briefly discusses the impact of future emission control requirements and increasing competition in the electric utility industry.

6.2.  LEVEL, IMPLEMENTATION, AND TIMING OF FUTURE NOx AND

OTHER POTENTIAL EMISSION CONTROL REQUIREMENTS

The current EPA regulatory climate possesses several currently mandated and reasonably anticipated future emissions control requirements that can be expected to impact electric utility sources.  The level and implementation of these emission reduction requirements--as well as their timing--are key issues affecting the ultimate cost of the reductions to be achieved.

Major factors that must be considered in determining and implementing environmental regulations requiring electric utility emission reductions include:  (1) flexible approaches to compliance, such as allowance trading and averaging, that can achieve or exceed necessary emission reductions while minimizing their total cost to society; and (2) staging the timing of regulatory requirements for reducing emissions of the many critical public health pollutants that are emitted by electrical generating stations, particularly coal-fired units.

Flexible Compliance Approaches.  Appropriate trading, averaging, and limited banking of emission reduction allowances enables scarce resources, notably human effort and financial investment, to be directed toward the most effective emission reduction opportunities available.  Conversely, such programs allow the perpetuation of utility emissions that truly represent diminishing returns, allowing scarce resources to be expended where greater public health and environmental quality gains can be secured.

The national Acid Rain program, with its SO2 allowance-based trading, is a good example of a program that incorporates flexible regulatory approaches to reduce costs.  Due largely to this trading system, market prices for SO2 allowances are now a full order of magnitude less than originally estimated.  Trading of NOx allowances is expected to similarly reduce currently high estimates for NOx emission reductions by about one-half.

Staged Timing.  There are two somewhat conflicting dynamics which must be balanced to achieve optimal staging of environmental regulatory requirements.  First, it is essential that regulations be implemented in a fashion that allows reasonably sound science to be employed and which enables regulated entities to survive financially.  Typically this results in a basically sequential approach, with one regulation adopted after another, so the science and compliance burdens are not excessive at any given point in time.  Adherence to this dynamic reflects recognition of the risk of "doing too much at once."

The second dynamic, however, applies economies of scale to the control of several pollutants at once, thus leveraging a source's downtime and engineering investment into greater environmental and public health benefit than a purely sequential approach can provide.  Ignoring this dynamic can lead a source to do "too little at once," by not "doing it right the first time."

This second dynamic is evident in the Clean Air Science Advisory Committee's (CASAC) recent decision to form a subcommittee to investigate collectively revising the NAAQS for ground level ozone, fine particulate matter, and regional haze.  The objective of this effort is to determine new standards appropriately protective of public health, and to provide EPA with recommendations for an integrated, cost-effective, national implementation of the three new standards.  Such an approach must necessarily and comprehensively address long range transport of airborne pollutants in its implementation.  OTAG's conclusions should assist the subcommittee in achieving its goal of rational integration.  OTAG's results should similarly assist in EPA's current comprehensive examination of toxic emissions from utility sources.

6.3.  COMPETITION AND ELECTRIC UTILITY EMISSIONS

The electric utility industry may be undergoing profound changes concerning how it is regulated, especially relative to the transmission of electric energy in interstate commerce.  Discerning the need for change, the Federal Energy Regulatory Commission (FERC) issued a notice of proposed rulemaking (NOPR) on March 29,1995 regarding "Promoting Wholesale Competition Through Open Access Non-discriminatory Transmission Services by Public Utilities." In mid-November 1995, FERC issued a Draft Environmental Impact Statement (DEIS) on its open access NOPR, and FERC's interpretation of the minimal impact its NOPR would have on air emissions engendered a furious response from many quarters, particularly downwind states.

Given the development constraints imposed upon nonattainment areas by the CAAA, and its emphasis on the effects of air pollution rather than upon causes of air pollution, the reaction to FERC's NOPR rapidly and understandably turned political.  Several northeast governors have indicated approval of FERC's aims, but strong disapproval of the downwind air quality impacts of its approach.  The New England Governors Council, the Council of Northeast Governors, several U.S. Senators, and the OTC have all passed resolutions requesting that FERC, EPA, and the Administration work together to find a way to embark upon electric competition without negatively impacting downwind air quality and attainment.

This turn of events has added to the political burden which OTAG is already called upon to modulate (OTAG-related legislative efforts have been underway for some time by mining and utility interests, for example).  OTAG has become a critical venue in which the nation's tolerance for long range transport of air pollution will be juxtaposed with its tolerance of a monopoly electric utility industry.

As a result, OTAG is forced to consider a variety of issues not directly related to emission controls, but which could nevertheless have a significant impact upon transported air pollution.  These include, but are not limited to:

oWholesale competition in the electric utility industry, and its resultant emissions impact, may occur even without new FERC rules mandating open access to transmission lines.

oSubstantial unused, low cost electric generation capacity exists at relatively uncontrolled, coal-fired stations in upwind states.  Earlier authorizations of the CAA largely ignored these facilities because they were represented to be too near to retirement to control cost-effectively.  If, as it now appears, such uncontrolled, nearly-depreciated units will not be retired in the near future, then they must now be controlled.

oSubstantial power cost differences between regions is likely to result in significant shifts in generation.  However, analyses of such shifts must differentiate between currently available transmission capacity and that which can be expected in both the foreseeable and long term futures.  At present, there is little doubt that transmission capacity is adequate to meet anticipated market demand.  As a result, short term transmission constraints will probably deter huge increases in upwind generation and its associated emissions.  Nevertheless, transmission capacity can be significantly enhanced in the foreseeable future through such measures as reconductoring power lines and reducing line losses (which effectively adds capacity) through series capacitance.  In the long term, of course, if adequate markets exist and transmission constraints persist, new transmission lines will be built.

oGrowth in upwind utility NOx emissions--and its relationship to attainment of ozone and other air quality standards downwind--is an issue that must be included in the OTAG process.  These discussions should include reductions in NOx emissions expected from EPA's newly proposed Title IV (Acid Rain) regulations.  OTAG is also a proper venue to contrast the magnitude of the additional revenue potentially available to low cost, upwind utilities with the magnitude of additional control costs that would result in no net increase or even a reduction in transported pollutants.  Busbar impacts of adequate control costs do not appear to be determinative.

oOTAG is also an appropriate venue in which to consider the societal cost of emission reductions in the region.  In particular, a ton of NOx can be much more cost-effectively reduced at a relatively uncontrolled upwind generating station than through the pursuit of diminishing returns at stations already subject to more stringent requirements (e.g., the OTC MOU).

oEffective mechanisms must be developed and implemented to ensure that downwind regions experience no net emissions increase as a result of electric industry deregulation.  Ideally, such mechanisms should employ flexible, market-based concepts utilizing utility-wide and/or regional emissions averages in order to minimize the need for regulatory involvement in the achievement of this objective.

SECTION 7

STRATEGY DEVELOPMENT AND IMPLEMENTATION ISSUES

FOR ELECTRIC UTILITY SOURCES

7.1.  INTRODUCTION

This section offers recommendations regarding OTAG modeling of utility emissions and suggestions regarding implementation schedules for control technology retrofits.

7.2.  MODELING SCENARIOS INVOLVING NOx REDUCTIONS FROM

ELECTRIC UTILITY SOURCES

OTAG modeling scenarios which characterize or include NOx reductions from electric utility sources should consider several issues:

oScenarios should postulate neither generalized nor site-specific technology mandates.  Rather, modeling scenarios should be premised upon stringent performance standards for NOx emissions from utility generating stations, or for overall utility NOx emission averages.  Such approaches allow utilities to optimize the cost effectiveness of their emission reduction decisions.

oWherever possible, modeling scenarios should consider phased approaches that enhance integration with other mandated or anticipated emissions reduction requirements (e.g., new Title IV rules and revised ozone, fine particulate, regional haze, and mercury standards).

oWherever possible, modeling scenarios should separate utility and mobile source reductions (particularly heavy duty diesel engine emissions) in order to allow clear evaluation of the ozone reduction capability and cost effectiveness of each.

7.3.  RETROFIT IMPLEMENTATION SCHEDULES

An often overlooked but important consideration in requiring control technology retrofits is the time required to engineer, install, and test retrofit technologies on a schedule consistent with regulatory compliance dates.  Factors affecting implementation schedules include:

oThe number of units and generating capacity to be retrofit.

oThe availability of architectural engineering capacity and manufacturing and service support capabilities of retrofit technology suppliers.

oEngineering, procurement, and construction schedule requirements.

oThe outage requirements necessary to install retrofit technologies.

oThe potential impact of multiple unit installations on grid reliability (though existing low capacity factors, particularly for Midwest coal units, probably moot any genuine concern here).

oThe ability of serious non-attainment areas to achieve acceptable air quality in light of observed ozone and precursor levels at upwind boundaries.

SECTION 8

SUMMARY MATRIX OF

NOx CONTROL TECHNOLOGY COST AND PERFORMANCE

8.1.  INTRODUCTION

This section describes the Summary Matrix of control technologies and applications which follows.

The Summary Matrix highlights the NOx reduction efficiency ("ΔNOx %"); control cost in terms of cost per ton of NOx removed on an annual rather than seasonal basis ("$/ton"); and capital cost in terms of cost per kW "$/kW") for available NOx control technologies by various utility boiler types.

Each of these items is in turn presented as a triplet of:  (1) actual costs incurred, where installation experience exists; (2) expected costs where pre-contract market data exists such as vendor quotations for specific control technology installations on specific generating units based on detailed engineering studies.  (Since such studies typically last 3-6 months, this information is superior than generalized, hypothetical cost conclusions; the latter have traditionally overstated costs by a dramatic margin.); and (3) an industry estimate of the cost range applicable to the given control technology.  With the exception of LNB and LNB/OFA control options, cost figures are intended to reflect the incremental cost to deploy any one technology.  Some specifics of the cost estimation procedures used to develop the industry estimated cost ranges are described in Appendix A.

Care should be taken in using the industry estimated cost range figure in the Summary Matrix, since:  (1) there remains considerable disagreement between environmental control equipment suppliers and potential utility users as to the costs likely to be incurred when installing retrofit control technologies; (2) extremely high or low range endpoints may not be representative of costs applicable to the majority of applications; and (3) technological developments and retrofit application learning curves are advancing rapidly, reducing estimated control costs in some cases by as much as 1-2 orders of magnitude per year; and (4) flexible compliance options, particularly trading, will drive overall costs toward the lower end of any achievable cost range.

It is particularly inadvisable to extrapolate technology-specific costs to estimate broad, industry-wide totals because broad technology mandates are not contemplated by OTAG.  Flexible compliance strategies coupled with trading and banking of emission reductions will materially reduce cost per ton of NOx removed over the entire OTAG region.

APPENDIX A

COST EVALUATION BEHIND

INDUSTRY-ESTIMATED CONTROL COST RANGE

IN SUMMARY MATRIX

<<<Caution:  Appendix A (and its resulting "UARG Data" figures in the Summary Matrix) do not reflect consensus methodologies or up-to-date technical information such as catalyst life, gas-coal price differential, etc.  Some of these differences are reflected in the table below.  Other cost factors not yet included are represented in bold-italic characters.>>>

A.1.  INTRODUCTION

Cost figures cited in the Summary Matrix were abstracted from several sources, including information submitted to the OTAG Control Technology Committee, results in the NESCAUM/MARAMA Phase II Report, and technical literature describing NOx control (specifically, proceedings from the EPRI/EPA Symposia on Stationary Combustion NOx Control, most recently in 1995,1993, 1991).

The cost of NOx control on the basis of levelized dollars per ton was either adapted from the NESCAUM/MARAMA Phase II Report, or specifically calculated over a selected range of variables.  Levelized cost was estimated using a simplified version of the EPRI Technical Assessment Guide (TAG).  This appendix briefly summarizes the calculation methodology for the industry-derived cost range estimates in the Summary Matrix.

A.2.  KEY ECONOMIC VARIABLES

Several key economic variables in this calculation are described as follows:

Capital Recovery Factor  The annual capital recovery factor in current dollars of 0.17 was employed, reflecting a 20 year recovery period, and based on 1993 EPRI TAG values calculated for a discount rate of 9.2%.  (Note:  the capital recovery factor in constant dollars according to the EPRI TAG for the same economic conditions is 0.12).

Operating Cost Levelization Factor  The operating cost levelization factor in constant dollars by definition presumes a zero inflation rate, and a zero real escalation rate over a 20 year period, and thus is 1.0.

<<<Capacity Factor  How was capacity factor(s) used in the calculation?  EPA-Bechtel & STAPPA/ALAPCO reports use 65% default.  UARG seems to use less...>>>

A.3.  CALCULATION METHODOLOGY

The methodology to calculate the cost per ton of NOx removed involved three primary variables for most technologies:  (1) capital cost; (2) NOx reduction; and (3) capacity factor.  These were evaluated over the range indicated in the Summary Matrix.

In addition, a range of secondary variables were treated specific for each technology.  These were:

oGas reburning:  Natural gas/coal price differential, from $0.40 to $1.20/mmBtu

oSNCR:  Normalized Stoichiometric Ratio (NSR) from 0.9 to 1.5

oAverage catalyst life (retrofit application):  6-8 years

A "full-factorial" matrix of variables was not explored; rather combinations that reflected realistic scenarios were evaluated.  <<<"realistic" needs clarification.>>>

The coal sulfur content was assumed to be 2 lb/mmBtu, for the purpose of estimating cost savings from SO2 allowances.  <<<What is corresponding %S ?>>> The SO2 allowance value was assumed to be $75/ton, and the cost savings accrued after a corporate tax rate of 35%.

The following numerical values were assigned for selected inputs to the cost evaluation:

SUMMARY TABLE:  VALUES OF KEY COST VARIABLES

| Cost Variable | UARG Values | States' Values |
| --- | --- | --- |
| Coal Unit Cost | $1.50/mmBtu | $1.00/mmBtu |
| Natural Gas Unit Cost | $2.20/mmBtu | $1.50-$2.00/mmBtu |
| Anhydrous Ammonia | $250/ton | $250/ton |
| Urea Reagent | $315/ton | $315/ton |
| Plant Heat Rate | 9,600 Btu/kWh | 9,600 Btu/kWh |
| Plant Capacity Factor: | ___ | ___ |
| Baseloaded Units | 55-65% | 65% |
| Peaking Units | 50% | 50% |
| SCR Catalyst Life (Ave.) | 4-6 years | 6 years + |
| SCR Replacement Catalyst | $400/ft3 | $400/ft3 |
| SO2 Allowance Value | $130/ton | $75/ton |

SELECTED REFERENCES

Cichanowicz,J.E.  Cichanowicz, "Factors Affecting SCR Capital Costs for Coal-Fired

1995Utility Boilers," Discussion Paper Prepared for the National Mining Association and the Utility Air Regulatory Group, 1995

DOE, 1994"Demonstration Of Coal Reburning for Cyclone Boiler NOx 	Control:  Final Report." U.S. Department of Energy/PETC, Report No. DE FC 2290 PC 89659.

EPA, 1993Alternative Control Techniques Document--NOx Emissions from Stationary Gas Turbines, final report prepared for the EPA Office of Air Quality Planning and Standards, report no. EPA-453/R-93-007, January 1993.

EPA, 1995a"Phase II NOx Controls for The MARAMA and NESCAUM Regions."  Prepared for U.S. EPA/OAQPS by Acurex Environmental, September 30, 1995.

EPA, 1995b"Cost-Effectiveness of Low-NOx Burner Technology Applied to Phase I, Group 1 Boilers." Prepared for EPA (EPA contract No. 68 D3-0005), May, 1995.

EPRI, 1995Proceedings of the EPRI/EPA 1995 Joint Symposium on Stationary Combustion NOx Control; May 1995, Sessions 8A and 8B, Book 4.

ICAC, 1994a"Selective Non-Catalytic Reduction (SNCR) for Controlling NOx Emissions."  White Paper prepared by the Institute of Clean Air Companies (ICAC) SNCR Committee, July 1994.

ICAC, 1994b"Selective Catalytic Reduction (SCR) Controls To Abate NOx Emissions."  White Paper prepared by the Institute of Clean Air Companies (ICAC) SCR Committee, October 1994.

Jaerschky, 1993Jaerschky, et al., "SO3 Generation--Jeopardizing Catalyst Operation?" Paper presented at the 1991 EPRI/EPA NOx Control Symposium, March 1991.

Rentz, 1992Economic Commission for Europe, ECE NOx Task Force, December 1992.

Rummenhohl,V. Rummenhohl, et al., "Relating the German DeNOx

1994Experience to U.S. Plants:  Lessons From More Than 30,000 MW of DeNOx Retrofits."  Paper presented at the ASME Joint International Power Generation Conference, Phoenix, AZ, October, 1994.

Smith, 1995"Reburn NOx Reductions on Hennepin Unit 1 Based Upon Draft NESCAUM II Report."  Memo from L.  Smith (Energy Technology Consultants, Inc.) to Craig Harrison (Hunton & Williams), July 26, 1995.

Veerkamp, 1993Veerkamp et al., "Evaluation of SCR as a NOx Control Option for Pacific Gas & Electric."  Paper presented at the 1993 EPRI/EPA NOx Control Symposium, May 1993.

<<<Add other sources cited in footnotes...>>>

# Footnotes

Letter from Alexander L. Huhmann of PSE&G to Brock Nicholson, Chair of OTAG Control Strategy Formulation mini-group, dated April 8, 1996.

Seven of the most recent reports are:

o"Phase II NOx Controls for NESCAUM and MARAMA Regions."  November 1995, prepared for NESCAUM, MARAMA, and OAQPS.

o"Discussion of Factors Relevant to Section 407 NOx Emissions Standards for Group 2 Boilers."  May 1995, prepared for UARG.

o"Controlling Nitrogen Oxides Under the Clean Air Act:  A Menu of Options."  July 1994, prepared for STAPPA/ALAPCO.

o"Alternative Control Techniques Document--NOx Emissions from Utility Boilers."  March 1994, prepared for U.S. EPA.

o"Cost Estimates for Selected Applications of NOx Control Technologies on Stationary Combustion Boilers."  March 1996, prepared by Cadmus Group and Bechtel Power Corporation for U.S. EPA.

o"Assessment of Performance Capabilities of LNBs Based on Reported Hourly CEM Data."  December 4, 1995, prepared by Cadmus Group.

o"Capital and Annualized Costs of Low NOx Burner Technology Applied to Phase I, Group 1 Boilers."  December 8, 1995, prepared by Acurex.

Source:  "Estimated Effects of Alternative NOx Cap and Trading Schemes in the Northeast Ozone Transport Region."  Prepared by ICF Kaiser for EPA, September 1995.

According to ICF Kaiser's report for EPA (see Footnote 2), the availability of trading in the Northeast provides for significant NOx reductions at as low as one-third the cost of traditional command-and-control strategies.

Source:  "Steam."  Babcock & Wilcox, 40th Edition, 1992.

Source:  "Assessment of Performance Capabilities of LNBs Based on Reported Hourly CEM Data."  Prepared by The Cadmus Group and Bechtel Power Corporation for EPA, December 4, 1995.

For conventional pulverized coal-fired boilers (e.g., Group 1), the compliance date for NOx is determined by the SO2 status.  Specifically, a unit that must comply with SO2 reductions by 1995 must meet NOx limits by 1996.  Similarly, Group 1 units for which SO2 reduction by 2000 is mandated must comply with NOx reductions on that date.

Wet-bottom means the boiler has a furnace bottom temperature above the ash melting point and the bottom ash is removed as a liquid.

Several tangential-fired units of this design were designed and constructed by Combustion Engineering (presently ABB) in the mid-50's; however all but one have since been converted to natural gas firing.  As a result, none of these units is included in the boiler inventory.

American Electric Power and Duquesne Power and Light have achieved greater than 40% reduction through coal and air staging on roof-fired boilers.

Source:  "Assessment of Performance Capabilities of LNBs Based on Reported Hourly CEM Data."  Prepared by The Cadmus Group and Bechtel Power Corporation for EPA, December 4, 1995.

Source:  "Assessment of Performance Capabilities of LNBs Based on Reported Hourly CEM Data."  Prepared by The Cadmus Group and Bechtel Power Corporation for EPA, December 4, 1995.

Source:  "Assessment of Performance Capabilities of LNBs Based on Reported Hourly CEM Data."  Prepared by The Cadmus Group and Bechtel Power Corporation for EPA, December 4, 1995.

Tables 3-8 and 3-19, "Phase II Controls For The MARAMA and NESCAUM Regions."  September, 1995.

See Table 4, "Reducing Static Emissions by Gas Firing in Coal-Designed Boilers--Field Evaluation Results."  Folsom et al., Proceedings of the 1993 EPRI/EPA Joint Symposium on Stationary Combustion NOx Control, May 1993, Miami, FL.

Most recent is Book 4 (Sessions 8A and 8B) of the Proceedings of the 1995 EPRI/EPA Joint Symposium on Stationary Source Combustion NOx Control, May 1995.

L. Smith of Energy Technology Consultants, Inc., to Craig Harrison of Hunton & Williams (Smith, 1995) reporting short-term vs. long-term analysis of data presented in two gas reburn technical papers.  <<<Made available to OTAG CTO Workgroup?>>>

In an October 27 letter from J.M. Piepho (Marketing Manager, Babcock & Wilcox) to L. Kertcher (EPA Acid Rain Division), a furnace residence time of 1 second from the reburn burners to the furnace exit was estimated necessary with coal reburn to assure acceptable carbon burnout while achieving 50+% NOx reduction at full load.

Letter dated July 17, 1995, from Blair Folsom (Vice President, EER) to John Pratapas (Senior Project Manager, GRI), page 2.

The necessary residence time has been stated to be as long as 1.8 seconds for a certain type of coal (see final report for the WP&L Nelson Dewey demonstration, DOE Report DE FC 2290 PC 89659), and as short as 1 second by several process suppliers.  Boilers featuring less than the minimum residence time can still deploy reburn, but NOx reduction capabilities would be less.

Although misleading, it is convenient to express the catalyst replacement frequency in terms of a single number reflecting useful catalyst life in years.  In practice, a catalyst management strategy is employed to minimize the cumulative cost over the plant lifetime of providing for replacement and disposal of catalyst.  Generally, an SCR reactor when initially commissioned into service contains only a portion of the ultimate catalyst inventory, which after a number of years is gradually augmented with new catalyst to compensate for gradual deactivation.  Ultimately, the original catalyst elements are considered "spent" and replaced with fresh catalyst, which in turn augments the older catalyst in the reactor.  Specific strategies vary with site-specific design considerations.