MEMORANDUM

DATE: 	June 20, 2005

SUBJECT:	NOX Control Technologies for Stationary Diesel ICE

FROM:	Tanya Parise, Alpha-Gamma Technologies, Inc.

TO:		Sims Roy, EPA OAQPS ESD Combustion Group

The purpose of this memorandum is to present information on different types of nitrogen oxides (NOx) controls that can be applied to stationary internal combustion engines (ICE) operating on diesel fuel.

Introduction

Several control technologies capable of reducing NOx emissions from stationary ICE are discussed within this memorandum.  Add-on or post-combustion controls (also referred to as secondary methods of control) for NOx are control methods designed to treat the exhaust emissions from stationary ICE once NOx emissions have formed.  On-engine or in-cylinder controls (also referred to as primary methods of control) for NOx are control methods designed to minimize the amount of NOx formed.  Control methods that are commercially available and control technologies that are under development are discussed.  Table 1 presents a summary of the NOx emissions reductions that can be achieved for the control methods discussed in this paper.

Commercially Available

Add-On Control

Selective Catalytic Reduction

Selective catalytic reduction (SCR) has been on the market and proven reliable for over 15 years.  However, it has not been widely used for engines.  Miratech, Johnson Matthey, Engelhard, RJM, Wartsila and Catalyst Products are some manufacturers that make SCR.  Selective catalytic reduction is often used in combination with an oxidation catalyst and is the only commercially proven secondary NOx reduction method for lean burn gas and diesel engines.  The following requirements and difficulties are associated with applying SCR:

Table 1.  Summary of NOx Controls for Stationary Diesel ICE

| Control Method | NOx Reduction (%) | Applicable Engines | Cost | Other Pollutant Reductions (%) | Concerns/ Requirements |
| --- | --- | --- | --- | --- | --- |
| Commercially Available Add-On Controls |
| Selective Catalytic Reduction | >90 | Lean Burn, Diesel, and Dual-Fuel | $121/hp (capital)1 $36/hp (annual)1 | PM: 0-30, HC: 50-90, CO: 50-90 (with oxidation catalyst) | Ammonia slip a concern. Requires <500 ppm sulfur fuel. |
| NOxTech® | 90-95 | Diesel and Lean Burn Natural Gas |  | PM: 60-80, VOC: 90, CO: 50-70 | Trace ammonia of <2-5 ppmv. |
| Commercially Available On-Engine Controls |
| Ceramic Coating | 40 | Diesel2 |  | CO: 80, NMHC: 60 |  |
| Ignition/Injection Timing Retard | 0-40 (RB) 0-20 (LB) 15-30 (CI) | All Engines | $12,000-$25,000 (capital)3 $6,300-$81,000 (annual) | CO and HC: Little effect for SI engines, no definite trend in diesel, and slight increase in dual-fuel. | Combustion instability, loss of power, impacts exhaust valve life and turbocharger performance. Increase in brake-specific fuel consumption. |
| Water Injection | 25-35 | All Engines4 |  | No HAP Reduction |  |
| Exhaust Gas Recirculation | 48-80 | All Engines |  | No HAP Reduction |  |
| Under Development |
| NOx Adsorber | >905 | Diesel and Gasoline (EMx™: Natural Gas and Diesel) |  | PM: 10-30, HC: 90, CO: 906 | Sulfur degradation and catalyst durability. Requires <15 ppm sulfur fuel. |
| Ozone Injection | 85-95 | All Engines |  |  | Typically includes a heat recovery steam generator and economizer. |
| Lean NOx Catalyst | <307,8 | Lean Burn and Diesel |  | CO: 60, NMHC: 60 |  |

1Based on averaging cost information from NESCAUM and from Diesel & Gas Turbine Worldwide.

2Tests are underway to determine the effect on gas fired engines.

3Costs are based on installing an ignition system, however in certain cases the ignition system is standard equipment and no purchased equipment is required.  In this case, capital costs are expected to be $4,000 or less.

4Note that in Table 4 of the NJ SOTA Manual for RICE, water injection is listed as not applicable to SI lean burn engines.

5Note that in information from EC/R’s update to EPA’s ACT, EMx™ has been shown to reduce NOx by 95 percent from lean burn engines and 98.9 percent from diesel engines.

6Note that according to EC/R’s update to EPA’s ACT, SCONOx® has been shown to reduce CO and VOC by up to 95 percent in lean burn engine exhaust.

7Note that information from the Manufacturers of Emission Controls Association stated that one stationary diesel engine has been equipped with a lean NOx catalyst and NOx emissions are being reduced by 80 percent.

8Note that in Table 5 of the NJ SOTA Manual for RICE, the NOx efficiency for CI diesel and dual-fuel engines is listed as greater than 90 percent.

- Requires sulfur levels of less than 500 parts per million (ppm),

- Fuel penalty:  urea consumption approximately 4 percent of fuel use,

- Infrastructure,

- Requires engine integration:  NOx sensor or engine NOx map,

- Ammonia slip, and

- Possible vanadium emissions.

Emissions Reductions

Selective catalytic reduction is capable of achieving greater than 90 percent reduction for NOx, a 0-30 percent reduction for particulate matter (PM), a 50-90 percent reduction for hydrocarbons (HC), and a 50-90 percent reduction for carbon monoxide (CO) (with oxidation catalyst).

Costs

Information from the Northeast States for Coordinated Air Use Management (NESCAUM) and from Diesel & Gas Turbine Worldwide was used to estimate the costs associated with the purchase, installation, and operation of SCR on an engine.  The information from NESCAUM was based on a 1,030 horsepower (hp) diesel engine equipped with SCR at the National Steel and Shipbuilding Company in San Diego, California.  The total capital cost including installation for this system was about $179,000.  The total annual cost was about $44,000.  The information from Diesel & Gas Turbine Worldwide indicated that the total capital cost including installation for an SCR system applied to a 2,336 hp engine, achieving a 90 percent reduction in NOx emissions, was $160,000 with annual costs of about $67,000.  The cost information from both sources was averaged together to obtain average costs per hp.  Capital costs associated with SCR were estimated to be $121/hp with an annual cost estimated to be $36/hp.  Costs include capital recovery, operation and maintenance, fuel penalty, and urea.  An oxidation catalyst and a NOx continuous emissions monitoring system (CEMS) can help to reduce ammonia slip.  The capital cost for a NOx CEMS is $158,000 with an annual cost of $43,000.

Cost information is available from EC/R’s update on NOx control technologies report which was obtained from a vendor who calculated costs for two scenarios involving 2,600 hp natural gas fired SI engines.  For the first scenario, three engines each operating 400 hours were used.  For the first scenario, capital costs were calculated at $187,000.  For the second scenario, one engine operated 2,000 hours per year.  The capital cost for this scenario was calculated at $68,000.  Capital costs include catalyst, urea control, injectors, engine map, startup assistance, reagent tank, and installation.  The annual costs for the first scenario were calculated at $48,200 based on capital recovery (equipment life of 7 years and 10 percent interest rate) and reagent costs.  The annual costs for the second scenario using the same assumptions, except that an equipment life of 5 years was used, were calculated at $35,680.  Note that these costs do not include all cost elements typically included by EPA.  For example, no indirect installation costs are included in the capital costs.  Also, operating and maintenance costs are not included in the annual costs.

The RJM Corporation, a provider of emission control technologies, was contacted to obtain cost information about their SCR products.  This company provided SCR technology to a number of diesel fired engines in the country.  The product RJM installs on diesel engines for NOx control is the RJM ARIS™ SCR Technology.  The capital costs for the SCR system for a 2,336 hp diesel engine range from $140,000 to $160,000 depending on the amount of control (50 to 90 percent NOx reduction).  The cost effectiveness for the RJM SCR varies depending on number of hours of operation and amount of control desired.  For 90 percent NOx control from a 2,336 hp diesel engine the cost effectiveness is $3,130 per ton of NOx removed based on 1,000 hours of operation and ranges to $738 per ton of NOx removed based on 8,000 hours of operation.  For 75 percent NOx control from a 2,336 hp diesel engine the cost effectiveness is $3,422 per ton of NOx removed based on 1,000 hours of operation and ranges to $775 per ton of NOx removed based on 8,000 hours of operation.

Caterpillar indicated that its SCR system is capable of reducing NOx emissions by 90 percent from diesel engines, or down to a level of about 0.7 grams per horsepower-hour (g/hp-hr) from a 7.0 g/hp-hr engine.  The cost for a 1.7 megawatt (MW) (2,278 hp) diesel genset package with SCR is $228,000, or $130/ekw.  Caterpillar indicated that this cost includes the SCR itself for $133,000, plus the urea tank, control system, connections, and packaging for $95,000.  Caterpillar also provided some information on an SCR installation at EXAR, a semiconductor manufacturer in Freemont, California.  At this facility, SCR had been installed on Caterpillar gas engines to meet 2003 California rules on NOx emissions, according to Caterpillar.  The total SCR and related capital costs were $450,000, or $473/ekw, for a plant totaling 950 ekw in size, according to Caterpillar.  These costs include building modifications, civil works, fixed piping and assembly.  According to Ralph Renee (facilities manager at EXAR), the actual SCR cost was about $230/ekw.  Maintenance costs at this facility were estimated at about $0.01/ekw-hr, with the assumption of a urea price of $2-5 per gallon.  According to Caterpillar, $0.01/ekw-hr would probably cover the total SCR system over time.

Experience

Information from EPA’s Alternative Control Techniques (ACT) Document identified a total of 23 SCR installations with lean burn engines in the United States.  A total of nine SCR installations with diesel engines and 27 installations with dual-fuel engines were identified in the United States.  Note that EPA’s ACT was published in 1993.

More recent information from EC/R’s report (published in 2000), which was a partial update of EPA’s 1993 ACT indicated that at least 44 engines have had SCR installed since 1991.  Of these, 38 are compression ignited (CI) engines, of which 31 are fired with diesel fuel, four are fired with distillate fuel oil (#2), one is fired with residual fuel oil (#6), and one dual-fuel engine is fired with diesel and natural gas.  The remaining seven engines are lean burn spark ignited (SI) engines burning natural gas.

Information was received from catalyst vendor Miratech.  Miratech indicated that there are basically no problems applying SCR to either CI or SI engines.  The vendor stated that worldwide it has expertise with more than 1,000 SCR installations on engines and within the United States 70-80 SCR installations on engines.

Information regarding SCR was requested from catalyst vendor Engelhard.  Engelhard referred the request to Stephen Frasch, an independent consultant and distributor of emission control systems who has used Engelhard products for the last 10 years and who is also hired by Engelhard for installation and warranty work in the western United States.  Stephen indicated that they have successfully installed SCR systems on both diesel and lean burn natural gas engines and that they have met 0.15 g/bhp-hr for NOx for both fuel types with 10 ppm or less ammonia slip.  According to Stephen, there are over 100 SCR installations on engines across the United States.  Stephen projects to install 10 or more SCR systems in 2004.

NOxTech® Emission Control System

According to EC/R’s report, NOxTech Inc. has developed the NOxTech® emission control system, which involves chemically treating exhaust gases with a nonhazardous liquid chemical.  The system can be applied to both diesel and lean burn natural gas fired engines.  It replaces the exhaust silencer on engines with a reaction chamber.  At temperatures between 1,400 to 1,500°F the non-catalytic chemical reagent is injected into the exhaust.  Nitrogen, water vapor, and CO are formed from the reaction between NOx and the injected reagent.  There is no toxic waste associated with this process, however, there are trace ammonia emissions of less than 2-5 ppm by volume.  The NOxTech® system is fully automated, installation requires no major modifications, and the system can be installed in 2 to 3 weeks.  To achieve the temperatures required for the reactions associated with the NOxTech® system, the exhaust gas must be heated.  A heat exchanger is placed downstream from the reactor to reclaim and reuse this heat energy.  According to information on NOxTech Inc’s website, the system can be applied to both retrofit and new engines.  The system is a muffler-size device made of sheet metal and other readily available materials and parts, which can be installed easily.

Emissions Reductions

Information in EC/R’s report indicated that according to NOxTech Inc., the emission control system has been proven to remove 90-95 percent of NOx emissions, 60-80 percent of PM, 90 percent VOC, and 50-70 percent of CO from the exhaust of the 4,000 hp diesel powered generator on Catalina Island.  According to NOxTech Inc, emissions of gaseous organic, PM, and CO can be reduced by greater than 80 percent.

Costs

According to literature available from NOxTech Inc. website, NOxTech® system capital costs are about $50-150/bhp-hr for diesel engines.  The company also states on their website that NOxTech® treatment costs are not expected to exceed about $1,000/ton of NO2 equivalent NOx reduction.  The company claims that the NOxTech® system can provide the end use a 50 percent cost reduction in comparison with SCR systems.

Experience

According to EC/R’s report, the NOxTech® system is operating on several diesel generators owned by Southern California Edison.  At its Catalina Island facility, NOxTech® is used on 2.5 MW (3,350 hp) and 3.8 MW (5,092 hp) diesel electric generators.  At its Pebbly Beach generating station, NOxTech® is used on 1.5 MW (2,010 hp) and 2.8 MW (3,752 hp) diesel generators.

On-Engine Control Methods

Ceramic Coating

Ceramic engine coatings have been used for several years in stationary and mobile diesel engines to reduce PM emissions.  Ceramic engine coatings improve combustion by reflecting heat away from coated components back into the combustion gas path.

Emissions Reductions

According to the Manufacturers of Emission Controls Association (MECA), testing indicated that ceramic engine coating combined with an oxidation catalyst may reduce NOx emissions from a diesel engine, by allowing the engine timing to be retarded, by 40 percent.  According to MECA, reductions of 60 and 80 percent for non-methane hydrocarbons (NMHC) and CO, respectively, are possible with an oxidation catalyst and engine coatings.  One manufacturer of ceramic coatings for diesel engines stated that significant HC and CO reductions can be achieved, however, an estimate of the percent reductions are not available.  More tests are underway to better determine the effect of ceramic engine coatings on diesel as well as gas fired engines.

Experience

According to MECA’s report regarding emission control technology for stationary internal combustion engines from 1997, ceramic engine coatings have been used for almost 5 years in well over 200 stationary and mobile diesel engines.

Ignition/Injection Timing Retard

Ignition timing retard can be applied to all new or existing rich and lean burn engines.  This method delays initiation of combustion to later in the power cycle, leading to a volume increase of the combustion chamber and a reduced residence time.  This may lead to reduced NOx formation.  The extent to which the ignition timing can be retarded to reduce NOx emissions varies with each engine.  Ignition timing increases exhaust temperatures, which may adversely impact exhaust valve life and turbocharger performance, and extreme levels of ignition timing retard may result in combustion instability and a loss of power.  Brake-specific fuel consumption (BSFC) increases.

Injection timing retard applied to CI engines reduces NOx emissions by the same principles as those for SI engines.  Injection timing can be adjusted on all new or existing CI engines.  Retarding the injection timing leads to the fuel igniting entirely during expansion rather than igniting initially during compression and then mostly igniting during expansion.  Lower combustion temperature and lower thermal NOx is the result, however, this also causes increased fuel consumption.  In addition, certain engines may experience problems with high CO and soot emissions as a result of these changes.

Ignition and injection timing retard modifications can be performed with a very low capital cost and may also require a few hours of mechanics time.  Some additional hardware or testing is often recommended, resulting in a total cost of a few thousand dollars.  Similar NOx reductions as those obtained with injection timing retard can be achieved with ignition timing retard.  However, SI engines are typically more sensitive to timing retard than CI engines, and more operational problems are associated with SI engines when applied.  Therefore, the level of NOx reduction achievable for SI engines can be more limited than for CI engines.

Injection timing retard adjustment is not possible on all engines.  Excessive timing retard results in combustion instability and engine misfire.  The BSFC also increases with increasing levels of injection timing retard for both diesel and dual-fuel engines.

Emissions Reductions

The NOx reductions from applying ignition timing retard range from no reduction to 40 percent for rich burn engines and 0-20 percent reduction for lean burn engines.  Ignition timing retard has little effect on CO and HC emissions.  For CI engines, retarding the injection timing by about 4 degrees can reduce NOx by 15-30 percent, however achievable NOx reductions are engine-specific.  There is no definite trend for CO and HC emissions for moderate levels of ignition retard in diesel engines and there is a slight increase in these emissions in dual-fuel engines.

Costs

Costs for ignition and injection timing retard were provided in EPA’s ACT from 1993.  For rich burn engines, the capital costs associated with ignition timing retard range from $12,000 to $25,000 with annual costs ranging from $6,300 to $80,000.  For lean burn engines, the capital costs are similar, estimated to range from $12,000 to $24,000, with annual costs ranging from $7,200 to $81,000.  To obtain and maintain effective NOx reduction with changes in engine load and ambient conditions, it is required that the engine be equipped with an electronic ignition control system to automatically adjust the ignition timing.  In certain cases, the ignition system is standard equipment, in which case no purchased equipment is required, and capital costs are expected to be about $4,000 or less.  Annual costs associated with ignition timing retard are due to an increase in maintenance due to the electronic ignition control system, an increase in BSFC, emission compliance testing, and capital recovery.

For diesel engines, injection timing retard is estimated to have capital costs ranging from $12,000 to $24,000 and annual costs ranging from $6,200 to $78,000, based on varying engine sizes between 80-8,000 hp operating 8,000 hours per year.  For dual-fuel engines, the capital costs range from $12,000 to $24,000, with annual costs ranging from $10,000 to $57,000, based on engines from 700 to 8,000 hp in size operating 8,000 hours per year.  It is anticipated that injection timing retard will require an automated electronic control system similar to ignition timing adjustment for SI engines.  Capital costs are estimated on the same basis as ignition timing retard for SI engines.  Similarly, annual costs for injection timing retard are estimated using the same methodology that was used for SI engines for ignition timing retard.

The Status Report on NOx Controls developed by NESCAUM presented a case study based on Tennessee Gas Pipeline’s facility in Mercer, Pennsylvania.  Ignition timing retard was retrofitted at this facility on six 1,100 hp Cooper GMV-10 2-stroke natural gas fired engines to meet Pennsylvania reasonably available control technology (RACT) requirements.  The cost of the retrofit, including commissioning was $4,000 per engine.  The annual cost associated with this project was estimated at about $21,200.

Water Injection

Water injection as a control method can be used on any engine, but has been applied primarily to diesel engines for the reduction of NOx.  Only a few engines have been retrofitted to utilize water injection.  However, several engine manufacturers have recently offered such control systems as techniques on their new engines.  Water vapor acts as a heat sink to reduce peak temperatures, thereby reducing NOx formation.

Emissions Reductions

The SOTA Manual for RICE developed by the State of New Jersey Department of Environmental Protection stated that NOx reductions of 25-35 percent can be achieved with water injection.

Exhaust Gas Recirculation

Exhaust gas recirculation can be used on all engine types.  It has been widely used on gasoline and diesel motor vehicle engines for NOx reduction.  This method of control reduces NOx emissions by decreasing peak combustion temperatures through two mechanisms:  dilution and increased heat absorption.

Emissions Reductions

The SOTA Manual for RICE from the State of New Jersey stated that NOx reductions of 48-80 percent can be achieved with EGR on diesel engines.

Under Development

Add-On Controls

NOx Adsorber

A NOx adsorber is a catalyst technology for removing NOx in a lean exhaust environment for diesel and gasoline fired engines.  The technology is currently on the market for mobile gasoline fired engines, but still in the research and development phase for diesel.  It is expected to be on the US market 2007 at the earliest.  NOx adsorbers consist of ceramic monolith containing parallel channels, coated with precious metal catalysts.  During lean operation, NOx is stored in the form of nitrates produced by reactions between the NOx and catalyst.  At regular intervals, a momentary reducing condition (switching to rich burn) is produced inside the monolith by injecting reductant, causing the nitrates to decompose to nitrogen.

Emissions Reductions

A NOx adsorber is capable of achieving greater than 90 percent NOx reduction, 10-30 percent reduction of PM, 90 percent reduction of HC, and 90 percent reduction of CO.  Ultra low sulfur diesel fuel (<15 ppm) is required to achieve these reductions.  This is the technology that the Office of Transportation and Air Quality (OTAQ) is relying on for nonroad diesel engines to meet the Tier 4 standards.  The following requirements and difficulties are associated with NOx adsorbers:

- Requires sulfur levels of less than 15 ppm,

- Sulfur degradation and catalyst durability,

- Requires engine integration,

- Requires a means for supplemental fuel injection,

- Currently have no information on fuel penalty, performance penalty or costs,

- Tremendous system complexity & packaging, and

- Costs of precious metals.

Costs

Based on information from the regulatory impact analysis for nonroad diesel engines for NOx adsorber system costs, EPA developed NOx adsorber costs for stationary CI engines.  These costs were presented in the memorandum entitled “Control Costs for NOx Adsorbers and CDPF for CI Engines,” included in the rulemaking docket (Docket ID No. OAR-2005-0029).  The EPA estimated average total annual control costs for NOx adsorbers at $1/hp and capital control costs of $7/hp.  For example, for a 1,000 hp engine, annual capital control costs are estimated at $1,000 per engine, with capital control costs of $7,000 per engine.

Experience

The EMx™ (SCONOx®) system was developed by Goal Line Technologies (now Emerachem) and uses a single catalyst to remove NOx, CO, and VOC emissions.  The system was originally applied to gas turbines, but has now been developed for use on natural gas and diesel fired engines.  The EMxTM process uses no hazardous materials and all utilities required to operate the system (natural gas, steam, water, ambient air, and electricity) are often available at the site.  At temperatures between 300 and 700°F, nitrogen dioxide (NO2) is absorbed onto the catalyst surface through the use of a potassium carbonate coating, which reacts with the NO2 to form potassium nitrites.  Maximum NOx absorption is maintained by periodic regeneration of the EMxTM catalyst.  The catalyst is regenerated by passing a controlled mixture of regeneration gases across the catalyst surface in the absence of oxygen.  Water and elemental nitrogen are formed by the reaction between the regeneration gases and nitrites.  The regeneration gas contains CO2 which reacts with potassium nitrites to form potassium carbonate, the absorber coating that was on the catalyst surface prior to the oxidation process.

Information from EC/R’s report indicated that the vendor tested the EMxTM system which showed that NOx, CO, and VOC were reduced by up to 95 percent in lean burn engine exhaust.  Three EMxTM systems were purchased for natural gas fired engines and were scheduled to go on line in May 2000.  Preliminary testing of the EMxTM system conducted by Cummins Engine Company for use on mobile and stationary diesel engines showed that NOx emissions were reduced by 98.9 percent down to 0.4 g/bhp-hr.  Three EMxTM for diesel fired units have been sold but have not yet been commissioned.

Ozone Injection

Ozone injection can be applied to all engine types.  This control technique oxidizes NOx to nitrous pentoxide (N2O5).  A water or caustic scrubber is used to remove the N2O5 that is highly water soluble.  A heat recovery steam generator and economizer are typically used to reduce the temperature below 350°F.  Temperatures below 350°F inhibit ozone disassociation and ensure that the efficiency of the NOx oxidation is optimal.

According to the Status Report on NOx Controls, technologies such as electro-catalytic oxidation and ozone injection are emerging and offer the potential for high NOx emission reduction, as well as reduction of emissions of other pollutants.  However, because there is much less experience with these technologies, available cost information is limited.

Emissions Reductions

The SOTA Manual for RICE from the State of New Jersey stated that NOx reductions of 85-95 are achievable with ozone injection.

Lean NOx Catalyst

Lean NOx catalysts are being developed to reduce NOx emissions in the oxygen-rich exhaust of lean burn engines, particularly diesel engines.  There are two types of lean NOx catalysts; “active” and “passive” lean NOx catalysts.  The “active” lean NOx catalyst injects a reductant that converts NOx contained in the exhaust gases into nitrogen and oxygen.  Diesel fuel is typically used as the reductant.  The presence of the reductant provides locally oxygen poor conditions which allows NOx emissions to be reduced by the catalyst.

Emissions Reductions

According to OTAQ, active lean NOx catalysts can achieve NOx reductions up to 30 percent.  The passive lean NOx catalyst does not employ reductant injection.  It is therefore more limited in its ability to reduce NOx emissions.  Passive lean NOx catalysts are able to reduce NOx emissions less than 10 percent.  OTAQ noted in its report that lean NOx catalysts cannot provide the significant NOx reductions necessary for compliance with the proposed Tier 4 standards.

Information from the Manufacturers of Emission Controls Association’s status report on emission control technology for stationary engines, indicated that one stationary diesel engine was equipped with a lean NOx catalyst and NOx emissions were being reduced by 80 percent, CO by 60 percent, and NMHC emissions by 60 percent.

According to the SOTA Manual for RICE from the State of New Jersey, lean NOx catalysts are capable of achieving NOx reductions of 90 percent or greater for CI diesel and dual fuel engines.

References

1.	Status Report on NOx Controls for Gas Turbines, Cement Kilns, Industrial Boilers, Internal Combustion Engines.  Technologies & Cost Effectiveness.  Northeast States for Coordinated Air Use Management.  December 2000.

2.	Alternative Control Techniques Document -- NOx Emissions from Stationary Reciprocating Internal Combustion Engines.  Report.  EPA-453/R-93-032.  July 1993.

3.	Steve Strong, Miratech to Tanya Ali, Alpha-Gamma Technologies.  Email.  Questions Regarding SCR and NSCR for Stationary IC Engines.  January 28, 2004.

4.	Draft Regulatory Impact Analysis:  Control of Emissions from Nonroad Diesel Engines.  Assessment and Standards Division, Office of Transportation and Air Quality, U.S. Environmental Protection Agency.  EPA420-R-03-008.  April 2003.

5.	State of the Art (SOTA) Manual for Reciprocating Internal Combustion Engines.  Effective Date: 2003.  State of New Jersey Department of Environmental Protection.

6.	Steve Strong, Miratech to Tanya Ali, Alpha-Gamma Technologies.  Email.  Questions Regarding SCR and NSCR for Stationary IC Engines.  February 13, 2004.

7.	Emission Control Technology for Stationary Internal Combustion Engines.  Status Report.  Manufacturers of Emission Controls Association.  July 1997.

8.	Stationary Reciprocating Internal Combustion Engines Updated Information on NOx Emissions and Control Techniques.  Revised Final Report.  EC/R Incorporated.  September 1, 2000.

9.	Tanya Ali, Alpha-Gamma Technologies to Stephen Frasch, Stephen Frasch Consulting.  Telecon.  Information Regarding SCR and NSCR for Stationary Engines.  February 4, 2004.

10.	Stephen Frasch, Stephen Frasch Consulting to Tanya Ali, Alpha-Gamma Technologies.  Email.  IC Engine SCR and NSCR.  February 9, 2004.

11.	Stationary Diesel Engines in the Northeast:  An Initial Assessment of the Regional Population, Control Technology Options and Air Quality Policy Issues.  Northeastern States for Coordinated Air Use Management.  June 2003.

12.	SCR Economics for Diesel Engines.  Diesel & Gas Turbine Worldwide.  July-August 2001.

13.	NOxTech Inc.    March 17, 2004.

14.	Nick Huff, Miratech to Jennifer Snyder, Alpha-Gamma Technologies.  Email.  SCR Questions for RICE MACT.  October 23, 2003.

15.	Stationary Reciprocating Internal Combustion Engines Technical Support Document for NOx SIP Call.  Doug Grano and Bill Neuffer, EPA, October 2003.

17.	Interstate Ozone Transport:  Response to Court Decisions on the NOx SIP Call, NOx SIP Call Technical Amendments, and Section 126 Rules; Final Rule.  40 CFR Parts 51, 78, and 97.  69 FR 21604, April 21, 2004.

18.	Gordon Gerber, Caterpillar to Melanie Taylor, Alpha-Gamma Technologies.  Email.  Cost of Caterpillar SCR System.  April 22, 2004.

19.	Exhaust Emission Controls Available to Reduce Emissions from Nonroad Diesel Engines.  Manufacturers of Emission Controls Association.  April 2003.

20.	Caterpillar Engine Research Diesel & Emissions Technology.  2002.