## Solid Flame 1
CHAPTER 5. ESTIMATING RADIANT HEAT FLUX FROM FIRE TO A TARGET
FUEL AT GROUND LEVEL IN PRESENCE OF WIND (TILTED FLAME)
SOLID FLAME RADIATION MODEL
Version 1805.0
The following calculations estimate the radiative heat flux from a pool fire to a target fuel in the presence of wind.
The purpose of this calculation is to estimate the radiation transmitted from a burning fuel array to a target
fuel positioned some distance from the fire at ground level to determine if secondary ignitions are likely in presence of wind.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Fuel Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input
parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s).
The chapter in the NUREG should be read before an analysis is made.
INPUT PARAMETERS
| Mass Burning Rate of Fuel (m") |  |  |  | 0.039 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  |  | 46000 | kJ/kg
| Empirical Constant (kb) |  |  |  | 0.7 | m-1
| Fuel Area or Dike Area (Adike) |  |  |  | 9 | ft2 | 0.83613 | m2
| Distance between Fire and Target (L) |  |  |  | 10 | ft | 3.048 | m
| Wind Speed or Velocity (uw) |  |  |  | 700 | ft/min | 3.556 | m/sec
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F | 25 | °C
[7 empty] | 298 | K
| Gravitational Acceleration (g) |  |  |  | 9.81 | m/sec2
| Ambient Air Density (ra) |  |  |  | 1.1846 | kg/m3
Calculate
Note: Air density will automatically correct with Ambient Air Temperature (Ta) Input
THERMAL PROPERTIES DATA
BURNING RATE DATA FOR FUELS
| Fuel | Mass Burning Rate | Heat of Combustion | Empirical Constant | Select Fuel Type
|  | m" (kg/m2-sec) | DHc,eff (kJ/kg) | kb (m-1)
| Methanol | 0.017 | 20000 | 100 | Scroll to desired fuel type then
| Ethanol | 0.015 | 26800 | 100 | Click on selection
| Butane | 0.078 | 45700 | 2.7
| Benzene | 0.085 | 40100 | 2.7
| Hexane | 0.074 | 44700 | 1.9
| Heptane | 0.101 | 44600 | 1.1
| Xylene | 0.09 | 40800 | 1.4
| Acetone | 0.041 | 25800 | 1.9
| Dioxane | 0.018 | 26200 | 5.4
| Diethy Ether | 0.085 | 34200 | 0.7
| Benzine | 0.048 | 44700 | 3.6
| Gasoline | 0.055 | 43700 | 2.1
| Kerosine | 0.039 | 43200 | 3.5
| Diesel | 0.045 | 44400 | 2.1
| JP-4 | 0.051 | 43500 | 3.6
| JP-5 | 0.054 | 43000 | 1.6
| Transformer Oil, Hydrocarbon | 0.039 | 46000 | 0.7
| 561 Silicon Transformer Fluid | 0.005 | 28100 | 100
| Fuel Oil, Heavy | 0.035 | 39700 | 1.7
| Crude Oil | 0.0335 | 42600 | 2.8
| Lube Oil | 0.039 | 46000 | 0.7
| Douglas Fir Plywood | 0.01082 | 10900 | 100
| User Specified Value | Enter Value | Enter Value | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-26.
ESTIMATING RADIATIVE HEAT FLUX TO A TARGET FUEL IN PRESENCE OF WIND
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 1995, Page 3-276.
SOLID FLAME RADIATION MODEL IN PRESENCE OF WIND
q" = EF1->2
| Where | q" = incident radiative heat flux on the target (kW/m2)
E = emissive power of the pool fire flame (kW/m2)
F1->2 = view factor between target and the flame in presence of wind
Pool Fire Diameter Calculation
Adike = pD2/4
D = √(4 Adike/p)
| Where | Adike = surface area of pool fire (m2)
D = pool fire diamter (m)
| D = | 1.0318 | m
Pool Fire Radius Calculation
r = D/2
| Where | r = pool fire radius (m)
D = pool fire diameter (m)
| r = | 0.51589 | m
Flame Emissive Power Calculation
E = 58 (10-0.00823 D)
| Where | E = emissive power of the pool fire flame (kW/m2)
D = diameter of the pool fire (m)
| E = | 56.877 | kW/m2
View Factor Calculation in Presence of Wind
| p F1->2,H = | (a2 + (b + 1)2 - 2 (b + 1 +ab Sin q)/(AB)0.5 tan-1 (A/B)0.5/((b - 1)/(b + 1))0.5 +Sinq/(C)0.5 (tan-1 ((ab - (b2 - 1)Sinq)/ (b2 - 1) (C)0.5) + tan-1 ((b2 - 1) Sinq/(b2-1)0.5 (C)0.5)
| p F1->2,V = | (a Cosq/(b - a Sinq)) (a2 + (b + 1)2 - 2b (1 + a Sinq))/ (AB)0.5 (tan-1 (A/B)0.5 ((b - 1)/(b + 1))0.5 + Cosq/(C)0.5 ((tan-1 (ab - (b2-1) Sinq)/((b2 - 1) (C)0.5 + tan-1 (b2-1) Sinq/(b2 - 1)0.5 (C)0.5)) - (a Cosq)/(b - a Sinq) (tan-1 (b - 1/b + 1)
a = Hf/r
b = R/r
A = a2 + (b +1)2 - 2a (b + 1) sinq
B = a2 + (b - 1)2 - 2a (b - 1) sinq
C = 1 + (b2 - 1) Cos2q
F1->2,max = √(F21->2,H + F21->2,V)
| Where | F1->2,H = horizontal view factor
F1->2,V = vertical view factor
F1->2,max = maximum view factor
R = distance from center of the pool fire to edge of the target (m)
Hf = height of the pool fire flame (m)
r = pool fire radius (m)
q = flame tilt or angle of deflection (radians)
Distance from Center of the Pool Fire to Edge of the Target Calculation
| R = L+r = | 3.5639 | m
| Where | R = distance from center of the pool fire to edge of the target (m)
L = Distance between fire and target
r = pool fire radius (m)
Heat Release Rate Calculation
Q = m"DHc,eff (1 - e-kb D) Adike
| Where | Q = pool fire heat release rate (kW)
m" = mass burning rate of fuel per unit surface area (kg/m2-sec)
DHc = effective heat of combustion of fuel (kJ/kg)
Adike = surface area of pool fire (area involved in vaporization) (m2)
kb = empirical constant (m-1)
D = diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
| Q = | 771.5211 | kW
Pool Fire Flame Height Calculation
Hf = 55 D (m"/ra (√g D)) 0.67 (u*)-0.21
| Where | Hf = nondimensional wind velocity
m" = mass burning rate of fuel (kg/m2-sec)
D = pool fire diameter (m)
ra = ambient air density (kg/m3)
g = gravitational acceleration (m/sec2)
u* = nondimensional wind velocity
Nondimensional Wind Velocity Calculation
u* = uw/(g m" D/ra)1/3
| Where | u* = nondimensional wind velocity
uw = wind velocity (m/sec)
g = gravitational acceleration (m/sec2)
m" = mass burning rate of fuel (kg/m2-sec)
D = pool fire diameter (m)
ra = ambient air density (kg/m3)
u* = uw/(g m" D/ra)1/3
| u* = | 5.1291
Hf = 55D (m"/ra (√g D))0.67 (u*)-0.21
| Hf = | 1.8828 | m
Flame Tilt or Angle of Deflection Calculation
| COS q = 1 | for u* ≤ 1
| COS q = 1 / √(u*) | for u* ≥ 1
Since u* ≥ 1
| q= | ACOS(1/(u*)^0.5) = | 1.1135 | Rad | 63.7972 | degree
|  |  | 1.1135 | Rad | 63.7972 | degree
|  |  | 0 | Rad | 0 | degree
| a = Hf/r = | 3.6497
| b = R/r = | 6.9082
| A = a2 + (b +1)2 - 2a (b + 1) sinq = | 24.067
| B = a2 + (b - 1)2 - 2a (b - 1) sinq = | 9.5327
| C = 1 + (b2 - 1) Cos2q = | 10.1094
|  |  |  | FH1 | FH2 | FH3 | FH4 | FH5 | FH6 | F1->2,H
| F1->2,H = | 0.18593 |  | 0.85803 | 0.9771 | 0.40655 | 0.28219 | -0.65544 | 1.0925 | 0.18593
| F1->2,V = | 0.16673 |  | FV1 | FV2 | FV3 | FV4 | FV5 | FV6 | FV7 | F1->2,V
| F1->2, max = √(F21->2,H + F21->2,V) = | 0.24974 |  | 0.4435 | 1.1091 | 0.94144 | 0.13887 | -0.65544 | 1.0925 | 0.31611 | 0.16673
Radiative Heat Flux Calculation in Presence of Wind
q" = EF1->2
| q" = | 14.2045 | kW/m2 | 1.2508 | Btu/ft2-sec
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection
Engineering, 3rd Edition, 2002.
Calculations are based on certain assumptions and have inherent limitations. The results of such
calculations may or may not have reasonable predictive capabilities for a given situation, and should
only be interpreted by an informed user.
Although each calculation in the spreadsheet has been verified with the results of hand calculation,
there is no absolute guarantee of the accuracy of these calculations.
Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet,
please send an email to nxi@nrc.gov or mxs3@nrc.gov.
Prepared by: |  | Date |  | Organization
Checked by: |  | Date |  | Organization
Additional Information
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | January 2005
Note on F23: This default value (9.81) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Solid Flame 2
CHAPTER 5. ESTIMATING RADIANT HEAT FLUX FROM FIRE TO A TARGET
FUEL ABOVE GROUND LEVEL IN PRESENCE OF WIND (TILTED FLAME)
SOLID FLAME RADIATION MODEL
Version 1805.0
The following calculations estimate the radiative heat flux from a pool fire to a target fuel in the presence of wind.
The purpose of this calculation is to estimate the radiation transmitted from a burning fuel array to a target
fuel positioned some distance from the fire above ground level to determine if secondary ignitions are likely in presence of wind.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Fuel Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input
parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s).
The chapter in the NUREG should be read before an analysis is made.
INPUT PARAMETERS
| Mass Burning Rate of Fuel (m") |  |  |  | 0.039 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  |  | 46000 | kJ/kg
| Empirical Constant (kb) |  |  |  | 0.7 | m-1
| Fuel Area or Dike Area (Adike) |  |  |  | 16 | ft2 | 1.4864 | m2
| Distance between Fire and Target (L) |  |  |  | 15 | ft | 4.572 | m
| Vertical Distance of Target from Ground Level (H1 = Hf1) |  |  |  | 8 | ft | 2.4384 | m
| Wind Speed or Velocity (uw) |  |  |  | 700 | ft/min | 3.556 | m/sec
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F | 25 | °C
[7 empty] | 298 | K
| Gravitational Acceleration (g) |  |  |  | 9.81 | m/sec2
| Ambient Air Density (ra) |  |  |  | 1.1846 | kg/m3
Calculate
Note: Air density will automatically correct with Ambient Air Temperature (Ta) Input
THERMAL PROPERTIES DATA
BURNING RATE DATA FOR FUELS
| Fuel | Mass Burning Rate | Heat of Combustion | Empirical Constant | Select Fuel Type
|  | m" (kg/m2-sec) | DHc,eff (kJ/kg) | kb (m-1)
| Methanol | 0.017 | 20000 | 100 | Scroll to desired fuel type then
| Ethanol | 0.015 | 26800 | 100 | Click on selection
| Butane | 0.078 | 45700 | 2.7
| Benzene | 0.085 | 40100 | 2.7
| Hexane | 0.074 | 44700 | 1.9
| Heptane | 0.101 | 44600 | 1.1
| Xylene | 0.09 | 40800 | 1.4
| Acetone | 0.041 | 25800 | 1.9
| Dioxane | 0.018 | 26200 | 5.4
| Diethy Ether | 0.085 | 34200 | 0.7
| Benzine | 0.048 | 44700 | 3.6
| Gasoline | 0.055 | 43700 | 2.1
| Kerosine | 0.039 | 43200 | 3.5
| Diesel | 0.045 | 44400 | 2.1
| JP-4 | 0.051 | 43500 | 3.6
| JP-5 | 0.054 | 43000 | 1.6
| Transformer Oil, Hydrocarbon | 0.039 | 46000 | 0.7
| 561 Silicon Transformer Fluid | 0.005 | 28100 | 100
| Fuel Oil, Heavy | 0.035 | 39700 | 1.7
| Crude Oil | 0.0335 | 42600 | 2.8
| Lube Oil | 0.039 | 46000 | 0.7
| Douglas Fir Plywood | 0.01082 | 10900 | 100
| User Specified Value | Enter Value | Enter Value | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-26.
ESTIMATING RADIATIVE HEAT FLUX TO A TARGET FUEL IN PRESENCE OF WIND
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 1995, Page 3-272.
SOLID FLAME RADIATION MODEL IN PRESENCE OF WIND
q" = EF1->2
| Where | q" = incident radiative heat flux on the target (kW/m2)
E = emissive power of the pool fire flame (kW/m2)
F1->2 = view factor between target and the flame in presence of wind
Pool Fire Diameter Calculation
Adike = pD2/4
D = √(4 Adike/p)
| Where | Adike = surface area of pool fire (m2)
D = pool fire diamter (m)
| D = | 1.3757 | m
Pool Fire Radius Calculation
| r = | D/2
| r = | 0.68786 | m
Flame Emissive Power Calculation
E = 58 (10-0.00823 D)
| Where | E = emissive power of the pool fire flame (kW/m2)
D = diameter of the pool fire (m)
| E = | 56.5075 | (kW/m2)
View Factor Calculation in Presence of Wind
| p F1->2,V1 = | (a1 Cosq/(b - a1 Sinq)) (a12 + (b + 1)2 - 2b (1 + a1 Sinq))/ (A1B1)0.5 (tan-1 (A1/B1)0.5 ((b - 1)/(b + 1))0.5 + Cosq/(C)0.5 ((tan-1 (a1b - (b2-1) Sinq)/((b2 - 1) (C)0.5 + tan-1 (b2-1) Sinq/(b2 - 1)0.5 (C)0.5)) - (a1 Cosq)/(b - a1 Sinq) (tan-1 (b - 1/b + 1)
| p F1->2,V2 = | (a2 Cosq/(b - a2 Sinq)) (a22 + (b + 1)2 - 2b (1 + a2 Sinq))/ (A2B2)0.5 (tan-1 (A2/B2)0.5 ((b - 1)/(b + 1))0.5 + Cosq/(C)0.5 ((tan-1 (a2b - (b2-1) Sinq)/((b2 - 1) (C)0.5 + tan-1 (b2-1) Sinq/(b2 - 1)0.5 (C)0.5)) - (a2 Cosq)/(b - a2 Sinq) (tan-1 (b - 1/b + 1)
| A1 = | a12 + (b +1)2 - 2a1 (b + 1) sinq
| A2 = | a22 + (b +1)2 - 2a2 (b + 1) sinq
| B1 = | a12 + (b - 1)2 - 2a1 (b - 1) sinq
| B2 = | a22 + (b - 1)2 - 2a2 (b - 1) sinq
| C = | 1 + (b2 - 1) Cos2q
| a1 = | 2Hf1/r = 2H1/r
| a2 = | 2Hf2/r = 2 (Hf - Hf1)/r
| b = | R/r
F1->2,V = F1->2,V1 + F1->2,V2
| Where | F1->2,V = total vertical view factor in presence of wind
R = distance from center of the pool fire to edge of the target (m)
Hf = height of the pool fire flame (m)
r = pool fire radius (m)
q = flame tilt or angle of deflection (radians)
Distance from Center of the Pool Fire to Edge of the Target Calculation
| R = L+ r = | 5.2599 | m
| Where | R = distance from center of the pool fire to edge of the target (m)
L = Distance between Fire and Target
r = pool fire radius (m)
Heat Release Rate Calculation
Q = m"DHc,eff (1 - e-kb D) Adike
| Where | Q = pool fire heat release rate (kW)
m" = mass burning rate of fuel per unit surface area (kg/m2-sec)
DHc = effective heat of combustion of fuel (kJ/kg)
Adike = surface area of pool fire (area involved in vaporization) (m2)
kb = empirical constant (m-1)
D = diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
| Q = | 1648.6952 | kW
Pool Fire Flame Height Calculation
Hf = 55 D (m"/ra √(g D))0.67 (u*)-0.21
| Where | Hf = flem height (m)
m" = mass burning rate of fuel (kg/m2-sec)
D = pool fire diameter (m)
ra = ambient air density (kg/m3)
g = gravitational acceleration (m/sec2)
u* = nondimensional wind velocity
Nondimensional Wind Velocity Calculation
u* = uw/(g m" D/ra)1/3
| Where | u* = nondimensional wind velocity
uw = wind velocity (m/sec)
g = gravitational acceleration (m/sec2)
m" = mass burning rate of fuel (kg/m2-sec)
D = pool fire diameter (m)
ra = ambient air density (kg/m3)
u* = uw/(g m" D/ra)1/3
| u* = | 4.6601
Hf = 55 D (m"/ra (√g D))0.67 (u*)-0.21
| Hf = | 2.3262 | m
Flame Tilt or Angle of Deflection Calculation
| COS q = 1 | for u* ≤ 1
| COS q = 1 / (√u*) | for u* ≥ 1
Since u* ≥ 1
| q = | ACOS(1/(u*)^0.5) = | 1.0892 | Rad | 62.4038 | degree
|  |  | 1.0892 | Rad | 62.4038 | degree
|  |  | 0 | Rad | 0 | degree
| A1 = a12 + (b +1)2 - 2a1 (b + 1) sinq = |  | 16.3724
| A2 = a22 + (b +1)2 - 2a2 (b + 1) sinq = |  | 79.8728
| B1 = a12 + (b - 1)2 - 2a1 (b - 1) sinq = |  | 10.9185
| B2 = a22 + (b - 1)2 - 2a2 (b - 1) sinq = |  | 48.1293
| C = 1 + (b2 - 1) Cos2q = |  | 13.3328
| a1 = 2Hf1/r = 2H1/r = |  | 7.0898
| a2 = 2Hf2/r = 2 (Hf - Hf1)/r = |  | -0.3263
| b = R/r = |  | 7.6467
| F1->2,V1 | 0.13854 |  | FV1 | FV2 | FV3 | FV4 | FV5 | FV6 | FV7 | F1->2,V1
| F1->2,V2 | 0.047161 |  | 2.4088 | 1.0206 | 0.82089 | 0.12687 | 0.11794 | 1.073 | 1.7339 | 0.13854
| F1->2 = F1->2,V1 + F1->2,V2 = | 0.1857 |  | FV1 | FV2 | FV3 | FV4 | FV5 | FV6 | FV7 | F1->2,V2
|  |  |  | -0.019047 | 1.0322 | 0.84612 | 0.12687 | 0.11794 | 1.073 | -0.01371 | 0.047161
Radiative Heat Flux Calculation in Presence of Wind
q" = EF1->2
| q" = | 10.4935 | kW/m2 | FV1: 0.92401; FV2: Btu/ft2-sec
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection | bar: FV1 to FV2
Engineering, 3rd Edition, 2002. | bar: FV1 to FV2
Calculations are based on certain assumptions and have inherent limitations. The results of such | bar: FV1 to FV2
calculations may or may not have reasonable predictive capabilities for a given situation, and should | bar: FV1 to FV2
only be interpreted by an informed user. | bar: FV1 to FV2
Although each calculation in the spreadsheet has been verified with the results of hand calculation, | bar: FV1 to FV2
there is no absolute guarantee of the accuracy of these calculations. | bar: FV1 to FV2
Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet, | bar: FV1 to FV2
please send an email to nxi@nrc.gov or mxs3@nrc.gov. | bar: FV1 to FV2
Prepared by: |  | Date |  | FV1: Organization
Checked by: |  | Date |  | FV1: Organization
Additional Information
Revision Log | Description of Revision |  |  | FV2: Date
1805.0 | Original issue with final text. |  |  | FV2: January 2005
Note on F24: This default value (9.81) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.