AGRICULTURAL RESEARCH SERVICE

-- PACIFIC WEST AREA--

Western Regional Research Center

Albany, California

# TABLE OF CONTENTS

Section		Function							  Page No.

C.1	General Information	1

C.1.1	Program Areas 	1

C.1.2	Performance Work Statement 	3

C.1.3	Operating Conditions 	3

C.1.4	Training	 4

C.1.5	Interference with Government Business 	4

C.1.6	Identification of Contractor Personnel	 4

C.1.7	Strike Contingency	5

C.1.8	Conduct of Contractor Employees	5

C.1.9	Transition of Contract Performance	6

C.1.10	Safety  	6

C.2	Work Management	7

C.2.1	Routine Work	7

C.2.1.2	Preventive Maintenance	8

C.2.1.3	Additional Work	9

C.2.2	Work Priorities 	9

C.2.2.1	Priority 1 (Emergency)	9

C.2.2.2	Priority 2 (Urgent) 	9

C.2.2.3	Priority 3 (Routine)	9

C.2.2.4	Alterations and Changes	10

C.2.3	Estimating Work	10

C.2.3.1	Preparation of Estimates	10

C.2.3.2	Labor Estimates	10

C.2.3.3	Total Labor Cost	10

C.2.3.4	Material and/or Subcontract Estimates	10

C.2.4	General Work Management Duties	10

C.2.5	Quality Control Program	11

C.3	Administrative Services	12

C.3.1	Stockroom and Receiving Operations	12

C.3.1.1	Stockroom Tasks	12

C.3.1.2	Receiving Tasks	13

C.3.1.3	Stockroom Reporting	13

C.3.2	Receptionist	14

C.3.3	Mail Service	14

C.3.4	Vehicle Dispatching	15

C.3.5	Messenger Services	15

C.3.6	Flag Duties	16

C.3.7	Lost and Found Property	16

C.3.8	Key and Key Card Control	16

C.3.9	Certification and Licenses	16

C.3.10	Registration	17

C.4	Environmental Health and Safety Program (EH&S)	17

C.4.1	Asbestos	17

C.4.2	Accident Program	18

C.4.3	Environmental, Health, and Safety Tasks	18

C.4.4	Safety Training Activities	19

C.4.5	Management of Chemical Storage Activities	20

C.4.6	Management of Hazardous Waste (HW) Disposal Programs	20

C.5	Facilities Services	21

C.5.1	Maintenance and Repair Services	21

C.5.2	Housekeeping	22

C.5.2.1	Housekeeping Tasks	23

C.5.3	Painting	24

C.5.3.1	Painting Tasks	25

C.5.4	Grounds Maintenance	25

C.5.4.1	Grounds Maintenance Tasks	26

C.5.5	Fire Protection	27

C.6	Utilities Services……………………………………………………….. ……..  27

C.6.1		General………………………………………………………………….. 27

C.6.1.1   	Electrical Tasks…………………………………………………………..28                                                                                                C.6.1.2   	Telecommunications Service and Maintenance	28

C.6.2		Plumbing and Pipefitting 	29

C.6.3		Heating, Ventilation, Air Conditioning (HVAC) & Refrigeration Tasks	30

C.7	Government-Furnished Items	32

C.8  APPENDICES

# APPENDIX 1:  GLOSSARY

# APPENDIX 2:  MAPS AND AREA LAYOUT

# EXISTING AND FUTURE LANDSCAPE PLANS

APPENDIX 3:  HISTORICAL WORKLOAD DATA

APPENDIX 4:  HISTORICAL SUBCONTRACTED WORK

APPENDIX 5:  FACILITIES INVENTORY

APPENDIX 6:  PM EQUIPMENT LISTING

APPENDIX 7:  PM TASK DESCRIPTION MASTER LIST

APPENDIX 8:  GOVERNMENT FURNISHED EQUIPMENT

APPENDIX 9:	  GOVERNMENT VEHICLE LISTING

APPENDIX 10: EQUIPMENT TEST/CERTIFICATION

APPENDIX 11: REQUIRED REPORTS

# C.1.	General Information

# C.1.1	Program Areas

The Western Regional Research Center (WRRC), herein after referred to as the Albany Research Location, is part of the Agricultural Research Service (ARS) United States Department of Agriculture (USDA). The Albany Research Location is comprised of six primary entities located at 800 Buchanan Street, Albany, California.  These entities and their missions are as follows:

Western Regional Research Center (WRRC) - The mission of the WRRC is to solve researchable food and agricultural problems of national scope. WRRC conducts mission oriented research directed toward maintaining and improving the healthfulness and safety of the food supply, and enhancing the competitiveness and utilization of agricultural commodities through the development of new, improved plant crops, processes and products which are commensurate with sustainable agriculture and maintain or improve environmental quality. The research program of WRRC is administered in eight research units; (a) Bioproduct Chemistry and Engineering, (b) Crop Improvement Utilization, (c) Exotic and Invasive Weeds, (d) Foodborne Contaminants Research, (e) Genomics and Gene Discovery, (f) Plant Mycotoxins Research, (g) Processed Foods Research, and (h) Produce Safety and Microbiology.  The major WRRC research program areas address:

Health and Safety Issues that range from the identification of food and food constituents which promote health to the alteration and/or removal of components that threaten the safety of the food supply.

New or improved crops processes and products which maintain U.S. competitiveness 	in world and domestic markets and enhance the utilization of agricultural commodities 	as well as provide a renewable natural resource base for commercial and/or industrial 	products.

Environmental Issues which range from research which leads to the development of 	new/modified crops, adaptive to the changing global ecology, to new and safer methods of 	protecting crops from various pests.

The goal of the WRRC’s research is sustainable systems for food which insure the production of safe and healthful foods and industrial products while maintaining or improving the quality of the environment. Major interdisciplinary approaches used in pursuing issues of food and agriculture rely on expertise in molecular biology, biochemistry, chemistry, and process chemistry and engineering. Biotechnological approaches focus on controlling or modifying the biosynthesis of enzymes or other constituents which enhance healthfulness and quality of the food supply and the utilization of value-added products, derived from agricultural sources.  WRRC has 285 employees (of about 482 total at the Albany Research Location); 90 of which are PH.D.-level research scientists.  The WRRC Center Director, also, serves as Location Coordinator for the Albany Research Location, and as such supervises various support personnel including the Location Administrative Officer, who manages the WRRC administrative and personnel offices; the Facilities Engineer, who serves as chief engineer for the Albany Location; and Computer Information Services which includes a 3-4 person group overseeing information technology (IT) for WRRC and elements of the Albany Research Location.

# Western Regional Research Center, Location Support Services - This office has the responsibility for providing administrative services, including personnel, purchasing, and property support, to the WRRC Location.

Plant Gene Expression Center (PGEC) - The mission of the PGEC is to provide the means to control plant gene expression to develop plant germplasm with inherent increased productivity and quality characteristics. The PGEC is a joint venture of the USDA Agricultural Research Service, the University of California, Berkeley, and the California Experiment Station. This unique laboratory employs both USDA and University of California personnel. The PGEC is structured with a core program of 7 investigations (only 6 are presently staffed), and a consortium program which is the institution for technology transfer into field agriculture. The core programs conduct research on central plant biological problems under the general mandate of the identification, isolation, manipulation, insertion and regulation of expression of genes of agriculturally important traits in plants. The specific programs are (a) the molecular mechanism by which the regulatory photoreceptor phytochrome controls genes expression; (b) the application of transposon technology to elucidate the developmental genetics of plant development; (c) the regulatory control of gene expression during pollen development and the determination of the functions of pollen-expressed proteins during pollen development, germination and pollen-pistil interactions; (d) the development of advanced plant biotechnology tools to manage the molecular biology of heavy metal tolerance and the development of new technology in DNA recombination technologies; and (e) a program on hormonal regulation of plant gene expression with special emphasis on the role of ethylene and auxin; and the use of isolated genes for the investigation of the molecular basis of the host-plant resistance to disease.

The Pacific Southwest Research Station - Headquarters (PSW) - This office has responsibility for research programs in California, Hawaii, and the Western Pacific. The Station Director, Assistant Directors, and Research Support Services staff have responsibility for planning, direction, evaluation and administrative services for the research programs.

The Pacific Southwest Research Station - Forest Sciences Laboratory (PSW-AFSL) - This laboratory has national and regional responsibility for research in the area of natural resources. The Research Units comprising the Albany Forest Services Laboratory are (a) Genetics of Western Forest Trees, (b) Cumulative Watershed Effects and Inland Fisheries, (c) Disease Pests of Forests, (d) Chemical Ecology of Forest Insects, (e) Forest Insect Population Genetics and Biochemistry, and (f) Structure and Function of Urban Forests.

The Pacific West Area, Office of the Director - This office has responsibility for programs in California, Hawaii, Alaska, Washington, Oregon, Idaho, Nevada, and Arizona. The Area Directors responsibilities include operational planning, direction and evaluation of research programs, and the overall research excellence of the Pacific West program.

The Pacific West Area, Area Administrative Office - This office has the responsibility to provide administrative services to the Pacific West Area on an oversight basis.

# C.1.2 Performance Work Statement

The performance work statement (PWS) specifies the services required to provide the full range of operational and maintenance support to the Albany Research Location. These services shall be provided to the entire complex, including existing buildings, greenhouses, structures, and appurtenances; renovated facilities and new construction.  Facilities operations and maintenance functions shall include, but are not limited to, the areas of work management, preventive maintenance, building maintenance, alteration and repair, installations, grounds maintenance, utilities, including heating ventilation air conditioning and refrigeration, electrical, plumbing; housekeeping, environmental, health and safety; and administrative services.  The Contractor shall provide all labor, supervision, supplies, materials, and equipment (with the exception of those identified by the Government) for facilities operations and maintenance, administrative, security and safety support services to the Albany Research Location, including materials such as lubricants, coolants, refrigerants, chemicals and other necessary parts and supplies in providing operations and maintenance support.

The Contractor shall perform all work described in this performance work statement in accordance with all Federal, State, and local laws, regulations, codes, technical manual specifications, manufacturer’s guidelines, USDA and ARS directives. The Contractor shall perform all related services necessary to carry out the provisions of this contract, including quality control, financial control, work order management, management of records, files and libraries of documents including Federal, State and local regulations, code laws, technical manuals, and manufacturers’ instructions and recommendations. The Contractor shall prepare reports, compile historical data, perform administrative work, and submit any necessary information, as specified or requested.  Provide facilities design review/assistance on site construction projects, as requested, by the Facilities Engineer.  Such functions are in direct support of the research mission of the Albany Research Location.

The Government shall provide use of facilities (office and shop space), general utilities and water services, and telephone services for use in performing contract requirements.

C.1.3	Operating Conditions

Federal holidays are listed below for information. When any holiday falls on a Saturday, the preceding Friday is observed. When any holiday falls on a Sunday, the following Monday is observed.  Observance of such days by Government personnel shall not by itself be cause for an additional period of performance, or entitlement of compensation except as set forth within the contract.

| NEW YEARS DAY | LABOR DAY |
| --- | --- |
| M.L. KING JR. BIRTHDAY | COLUMBUS DAY |
| PRESIDENT’S DAY | VETERAN’S DAY |
| MEMORIAL DAY | THANKSGIVING DAY |
| INDEPENDENCE DAY | CHRISTMAS DAY |
| Other days or partial days designated by Federal statute, Executive Order, and Presidential Proclamation. |

The Government reserves the right to close the facilities due to safety, health, security, or medical emergencies as necessary. Contractor personnel may be required to remain on duty to maintain the facility in the event of such adverse safety conditions or emergencies. Services are required 24 hours per day, 365 (or 366) days per year, on an uninterrupted basis, including all National and religious holidays. Utility operations and maintenance personnel must provide continuous services.

NOTE: Unless otherwise noted, the regular Government workday at Albany Research Location is from 8:00am to 4:30pm.

C.1.4	Training

The Contractor shall:

(A)  	Be responsible for all required training of their employees, including OSHA Class III O&M Abatement Worker certification for minor asbestos removal under O&M glove-bag procedures (16-hr initial and 4-hr annual refresher), as appropriate.

(B)  	Ensure that appropriate Contractor employees performing work under this contract have annual physical examinations including respirator fit exams and training on proper respirator usage.

(C) 	Provide training in boiler operations, equipment operations, forklift operation, and 	    	asbestos removal, to obtain licenses or certifications required by Federal, state or 		local regulations.

C.1.5	Interference with Government Business

The work described in this PWS is to be performed in support of the research conducted at the Location. The work shall be performed in such a manner that there will be minimal interruption or interference with the proper execution of Government business.  Coordinate any interruption of utility/facility service with the ACO or Quality Assurance Specialist (QAS) at least 2 weeks prior to interruption.  The ACO reserves the right to schedule performance of Contractor work during the evenings and weekends should interference/ disruption with research become too great during weekday performance.

C.1.6	Identification of Contractor Personnel

Contractor personnel must be recognizable while on the facility. The Contractor is responsible for providing a photo identification badge to each employee working at the facility. These badges shall be prominently displayed at all times and easily distinguishable from badges of Government employees.  Contractor’s subcontract personnel must wear identification badges while on site.

Prior to commencement of services under this contract the Contractor shall furnish to the Contracting Officer, a list of employee names proposed in the performance of on-site work.

During the course of the contract, the names and qualifications of any new employees must be submitted to the Administrative Contracting Officer prior to the start of work.

C.1.7	Strike Contingency The Contractor shall:

(A) 	Implement a strike contingency plan for the continuation of services required by the contract in the event of a work stoppage, slowdown, or similar action by the Contractor’s employees. This plan shall provide for the continuation of subcontracted services in the event a subcontractor is unable or unwilling to satisfactorily complete an assignment, or satisfactorily implement their strike contingency plan.

(B) 	The strike contingency plan must be submitted with the proposal for Government review and approval.  ACO approval is required on any changes in this plan prior to implementation.

C.1.8 	Conduct of Contractor Employees

The Contractor shall:

(A) 	Ensure that each employee and subcontractor adheres to standards of competency, conduct, appearance, and integrity.

(B) 	Initiate disciplinary action as necessary with respect to its employees and immediately report to ACO, in writing, any termination of contract personnel and the reason for termination.

(C) 	Ensure that Contractor personnel comply with the Location’s traffic and safety rules and other regulations/instructions pertaining to conduct of persons on Government facilities. The Contractor shall not disturb papers in offices, on desks, open desks or cabinets, or use telephones or office equipment that is not provided for their use.

- Place their employees on notice that infraction of any of the above rules, regulations, or prohibitions may be grounds for removal from Government property.

- Ensure its personnel adhere to conservation policies and turn off lights in unoccupied

areas unless otherwise directed.  Encourage its employees to look for new opportunities to conserve energy or materials and implement a mechanism for suggestions to be initiated.

(F)	Ensure all employees exercise care to wear appropriate protective clothing and equipment during the performance of this contract.  Contractor personnel shall, in no event, enter restricted areas except with approval from the ACO or QAS.

C.1.9    Transition of Contract Performance

The Contractor shall:

(A) 	Assist the Government in the transition of contract performance within thirty (30) days of the start of contract performance. Such transition tasks shall include, but are not limited to, procedures and operations of the facility, repair and maintenance operations, inventory, records, government furnished property/equipment, and any other operations to become knowledgeable in, and familiar with, assigned areas of

responsibility.

- Ensure during the transition period that: (1) They shall not interfere with the productivity of the incumbent Contractor; (2) All visits shall be coordinated in advance and arrangements made to be accompanied by a Government employee, and; (3) Activities are confined to those which can take place prior to the initial period of performance.

- Within 15 days after contract award, and during the contract closeout, the QAS shall jointly prepare an inventory to be used as the basis for turning over Government-furnished items.  Thereafter, an annual joint inventory shall be conducted.  The Contractor is responsible for inventory management.

- The Contractor is responsible for maintaining an equipment certification log, including test data and actual certification documentation; and an equipment warranty log with documentation of periodic PM as established by the manufacturer to preserve warranties.  These logs shall be available during work hours for Government review.  The equipment certification log, warranty log, QC inspection documentation, and government furnished equipment shall be transferred to the Government upon contract close-out or termination of the contract.

C.1.10 	Safety

The Contractor shall:

- Conduct all work in a safe manner in accordance with the Environmental Protection	Agency (EPA), Occupational Safety and Health Administration (OSHA), Federal, 	State, county and USDA requirements, and in compliance with the Albany Research 	Center Safety Manuals. Citations of the Contractor for noncompliance with 	environmental standards shall be resolved amongst the Contractor and the issuing 	office of the EPA, or the state of California. Payment of fines or penalty charges 	associated with citations issued by Federal, State or local officials will be paid by the 	party against whom the fines or penalties are assessed. If the Government pays 	the fines or penalty and the citations are issued due to faulty operation, neglect, or

maintenance practices of the Contractor, the Contractor will be held liable for the 	cost of the fine or penalty. If the Contractor pays the fines or penalty and the 	citations are issued without any fault by the Contractor, then upon the submission 	of proper invoices, the Government will reimburse the Contractor for the cost of 	such fines or penalties.

- Provide its personnel with a preventive medical program to ensure medical 	surveillance and consciousness by its employees of the work environment in and 	around the research laboratories.

- The Contractor shall prepare a comprehensive safety plan that outlines company

safety policies and practices as well as on-the-job recommendations and expectations for employee wellness and injury prevention.  The Contracting Officer may issue an order to stop all or part of the work if the Contractor fails or refuses to promptly correct or comply with safety requirements.

# C.2		Work Management

# General.

The Contractor shall use the existing Government-owned DataStream MP2, 5.0 computerized maintenance management system to identify and track all work requests, schedule and perform preventive maintenance, track labor and material costs, ensure quality control, and schedule personnel. Work orders are required for additional tasks to set priorities; estimate and requisition material; regulate and coordinate work tasks; promote timely scheduling; and ensure availability of labor, materials, facilities and equipment. The DataStream MP2 automated work management system includes inventory control and purchase order capabilities.  The Government will be responsible for maintaining the system server and software upgrades, as well as having input on 	DataStream MP2 configuration. The computer hardware/software for use by the Contractor is identified in Appendix 8.

The Contractor shall be responsible for updating work management data including all work performed on each work request and work order on a daily basis. The ACO and QAS will enter customer-generated work orders and have “read only” access to the management system for obtaining status on work orders and task data.

C.2.1.		Routine Work

The operations and maintenance of buildings, grounds, facility systems and support equipment/systems, corrective maintenance/repairs, preventive maintenance, installations, rental equipment and emergency work (may require after-hours response); and minor tasks (i.e., less than $4,000) for installations, alterations, modifications and repair of buildings, structures, or equipment is considered routine work.  This work may be initiated by task/work order and trouble calls.

# C.2.1.2.	Preventive Maintenance

The Contractor shall:

(A)	Perform preventive maintenance (PM) of buildings and structures, plant 			and equipment. Work consists of systematic and cyclic checks, 				inspections, and repairs/corrections/maintenance of minor deficiencies 			(less than $4,000) as well as the recording and reporting of deficiencies 			beyond the scope of PM. Historical data indicating average quantities of 			PM are shown in Appendix 6.

(B)	Develop and maintain a PM Plan. The PM plan should include a listing(s) of items and components to be maintained; inspection and maintenance schedules and shutdown schedules. The schedules will remain constant except for equipment additions or deletions.

(C)	Develop PM plan in accordance with the following order of precedence: (1)		manufacturers' recommendations and standards; (2) Federal, State and Local 		codes, industry standards; and (4) good laboratory practices. The plan shall 		include a listing(s) of items and components to be maintained; inspection and 		maintenance techniques; personnel schedules for performance; system 		shutdown and coordination requirements, as necessary; PM checkpoints, 		services, and frequencies; and recording methodology.

(D) 	Maintain PM and repair records on all building equipment and systems. The records shall include scheduled and accomplished dates, and be made available to the Government. Logs, records, checklists, and any other documentation maintained by the Contractor shall be available during normal work hours for ACO/QAS review.

(E)	Execute the PM program and maintain documentation accurately and up to 				date.  Update the PM program as necessary to reflect changes in equipment 				inventory, with such updates being subject to ACO approval.

(F) 	Determine and initiate a PM Program on all new equipment and systems; 		proposed revisions shall be provided to the ACO for approval within 15 days 		after the need is identified by the Contractor.

(G)	Submit a report of scheduled PM, completed PM, and outstanding PM to the QAS on a monthly basis.

(H)	The Contractor shall submit an equipment malfunction report to the Facilities Engineer and QAS within 4 hours after detection of equipment failure/malfunction.  This report shall include a description of the equipment including serial number, the date of failure, an assessment of the failure, system(s) affected by the failure and action taken.

# C.2.1.3		Additional Work

Additional Work is defined as major fabrication, modification, alteration or repair of plant, facilities, buildings and structures that exceeds $4,000.  Routine work that exceeds $4,000 will be treated as additional work. The Government may request the Contractor to provide detailed plans, engineering design, time schedules and cost estimates; and perform the work to accomplish both construction and nonconstruction support projects.  Additional Work shall be submitted to the ACO for review prior to release to the Contractor for estimating; original quotes/invoices are required for materials and subcontracted work.  The Additional Work shall be completed and inspected by the Contractor prior to inspection and acceptance/approval by the Government for payment. The Contractor shall not exceed the approved estimates for labor and material without prior approval from the Government. Service contract wage rates and/or Davis-Bacon wage rates apply to this work and contracted on a delivery order basis.

All damage caused by storms, floods, wind, hail, earthquakes, etc. requiring more than $4,000 in labor and materials will be handled by additional work order. Additional Work will be initiated by work orders approved by the ACO. The QAS or ACO will review Additional Work, and assign priorities. The Contractor shall schedule Additional Work for completion in accordance with assigned priority. Changes to additional work require ACO approval.

C.2.2      Work Priorities

C.2.2.1   Priority 1 (Emergency)

‘Priority 1’ maintenance and repair work requires immediate action, including diverting personnel from other jobs. Usually work is necessary for the protection of health or safety, biosafety and biosecurity, protection of ongoing experiments and research programs, or prevention of damage to property. Immediate corrective action shall be taken and pursued on a continuous basis until permanent repairs are completed unless otherwise directed by the ACO. The Contractor shall maintain or provide essential services to critical equipment and facilities or environmental conditions, or as otherwise required by the ACO.

C.2.2.2   Priority 2 (Urgent)

‘Priority 2’ work shall be accomplished by the first available craftsman. Personnel shall not be diverted from scheduled work. This work shall start within one workday and be completed within five working days, unless otherwise authorized by the ACO.

C.2.2.3   Priority 3 (Routine)

‘Priority 3’ work shall be accomplished in the most economical and efficient manner, on a “first come-first serve” basis. Prompt response to routine work is essential to smooth operation of research and support elements.  At a minimum, 50% of these requests shall be completed within ten working days of receipt. The remainder shall be completed within fifteen working days unless otherwise authorized by the ACO. Routine work requests may be either oral or written. Routine Work does not require prior ACO approval for scheduling or commencement of corrective action.

C.2.2.4   Alterations and Changes

Alterations and changes to additional work requests may be made by Government fund holders and approved by the ACO.

C.2.3       Estimating Work

C.2.3.1    Preparation of Estimates

The Contractor shall prepare all estimates in a standardized format approved by the ACO. All estimates must be documented. The Contractor's estimates will be evaluated to determine if (1) the scope has been clearly and accurately identified; (2) additional work has been properly estimated and supported with appropriate documentation; (3) labor and equipment/material estimates are reasonable and properly documented; and (4) unit prices and proper wage determinations were used for estimating; and (5) estimated completion schedules provided.

C.2.3.2   Labor Estimates

Labor estimates shall be expressed in man-hours by trade/craft. Estimated man-hours shall be supported from a documented source. All estimates for labor shall be clearly identified in the appropriate wage determination and work classifications verified by the Contractor.

C.2.3.3   Total Labor Cost

The total labor cost estimate will be determined by totaling the time for each craft and multiplying the appropriate hour unit price from Schedule B for the appropriate wage rate of Service Contract Act or Davis-Bacon Act. This procedure shall be followed for each craft required to perform the job including the sum of all crafts involved.

C.2.3.4   Material and/or Subcontract Estimates

The estimated material cost shall be based on current pricing data or from vendor quotations. Vendor quotes shall be obtained from no less than three vendors for material and subcontract estimates exceeding $2,500. Documentation of quotation and actual invoices shall be submitted as evidence with cost estimates.

C.2.4	General Work Management Duties:

The Contractor shall:

(A) 	Maintain a point of contact to be present at the Albany Research Location for receipt of work orders during workdays from 8:00am – 5:00pm.

(B) 	Review each work request for completeness, understanding, and clarity. Vague and incomplete work requests shall be returned to the QAS for description/additional information.

All work orders will be issued by the QAS or ACO to the Contractor. They will be in sufficient detail, with descriptions of work and sketches or drawings as necessary, to allow the Contractor to develop an estimate of man-hours, materials, and comply with established priority. The estimate of time and materials for additional work will be approved by the ACO prior to scheduling and commencement of work.

(C) 	Develop and submit weekly Work Order Report on all work in the backlog to the ACO, including a schedule of all routine and additional work by assigned priority, and work status.  Schedules shall indicate work order number, task description, and location of work by building and room number or area.  Separate reports will be provided for ‘open’ additional work, ‘open’ routine work, and a cumulative report of completed additional work.  The ACO or designated Government Official will inspect the work schedule and revise to meet specific Location needs.

(D)	Ensure that work to be redone is not assigned and treated as “new work,” but counted as part of the original work order; and deficiencies documented and additional time noted. The Contractor shall re-perform all intentional or negligent defective work.

(E)	Maintenance materials, tools/equipment and spare parts shall be procured, stored, and controlled in an effective and efficient manner.

C.2.5	Quality Control Program

The Contractor shall:

(A) 	Establish and maintain a Quality Control Program to ensure the requirements of the contract are provided as specified and a record of performance can be inspected by the Government to ensure compliance.

(B) 	Ensure the program includes: 1) a quality control inspection system covering all required contract services; 2) a method of identifying deficiencies in the quality of services performed and corrective actions to prevent recurring unsatisfactory or deficient performance.

(C)	Maintain a record of all Quality Control inspections, results and any corrective 	action. 	This file shall be the property of the Government and made available to the 	ACO or his/her representatives at all times. The file shall be turned over to the 	Government upon contract close-out or termination of the contract.

- Enter all QC inspection reports into the work management system.

- Upon receiving any complaints, including negative QA monitoring forms the 	contractor shall: (1) notify the ACO, (2) investigate the complaint, (3) take 	appropriate corrective action, (4) report resolution to the COR within 5 working 	days and document how the contractor’s QCP will prevent a similar complaint in 	the future.

- Report the overall service level via customer satisfaction results as a part of the 	monthly report, including the metrics and AQL’s in the QASP, Attachment 1.

# C.3	ADMINISTRATIVE SERVICES

# GENERAL

The Contractor shall be responsible for stockroom, shipping and receiving, receptionist, mail-room operations, vehicle, and messenger support at the Albany Research Location.

C.3.1  Stockroom and Receiving Operations

The Contractor shall operate and maintain the Albany Research Location “self check-out” stockroom, which consists of approximately 650 Government-owned stock materials/ supplies (both administrative and scientific).

C.3.1.1	   Stockroom Tasks

The Contractor shall:

(A) 	Manage and operate a computerized inventory system Government furnished (Datastream MP2 inventory software module) in providing an updated inventory and accounting of materials charged to the appropriate organizational element/account, including a monthly summarization of group usage/charges (there are approximately 47 Location accounts).  During the fourth quarter (July through September), group usage/charges will be reported to the ACO every two weeks.

(B)	Update and maintain proper stock levels in an orderly manner on shelves/bins.  The Contractor shall request stockroom materials as needed, maintain updated stockroom catalogs; monitor and maintain cylinder and ‘house’ gases, dry ice, laundry (towel) exchange, and copier supplies for central copy rooms 0020 and 2029 in the Main Building; copier supplies will be delivered to the West Annex Building upon request.  The Government will purchase/fund stockroom materials, including gases, dry ice, and copier supplies; the Contractor shall be responsible for providing laundry (towel) service as routine work under the contract.

(C) 	Provide customer service, including review of self check-out cards for accuracy and completeness and providing “over-the-counter” assistance, between the hours of 8:00 a.m. to 4:30 p.m.

# C.3.1.2    Receiving Tasks

(A)	Receive, unpack and verify all Procurement Office items; bar-code and enter all chemicals into the computerized chemical inventory and management (CHIM) system. Customer orders will be hand-delivered to requestors and shipments for maintenance and new projects will be transported to appropriate storage areas; responsible for document accountability.  Hours of operation are 8:00am-4:30pm.

(B)	Check each shipment against appropriate purchase documents or requisitions for quantity, accuracy and condition; complete and sign the receiving report and send it to the appropriate procurement office; incomplete or damaged shipments will be so noted on the receiving report, and a copy of the receiving report or the packing list sent to the appropriate procurement office.

(C)	Deliver routine items to requestors within one working day of receipt. Overnight, 			express, and UPS parcels; and items marked “perishable” or “refrigerate” shall be 			delivered to the requestor within one hour of receipt and the recipient shall sign proper 			document receipt.

(D)	Attach government property labels on capitalized property (i.e. acquisitions over 			$5,000) and submit a copy of the purchase order, property number and applicable 			information to the Procurement and Property Office on a bi-monthly basis.

(E)	Package, crate and ship outgoing material and equipment; notify the Procurement and 	Property Office for the proper shipping documentation; maintain logs of outgoing 	materials including arrangements made with the appropriate carrier.

C.3.1.3    Stockroom Reporting

The Contractor shall prepare reports for the Location Management Program Analyst consisting of the following:

o 	Summary by laboratory of the amount of money spent on chemical and supplies with a month and year to date total. The Stockroom Usage/Chargeback Reports shall be as follows:

October 1- December 31	Report due January 5th

January 1- March 31	Report due April 5th

April 1- June 30	Report due July 5th

July 1- July 31	Report due every 2 weeks

August 1- August 31	Report due every 2 weeks

September 1 - September 30	Report due every 2 weeks

- Semi-annual report of stockroom inventory to identify items that are inactive and slow moving according to Federal Property Management Regulations (FPMR) 101-27.4. This report is due to the ACO in February and August.

C.3.2	Receptionist

The Contractor shall provide receptionist support, in directing visitors, maintaining the 		visitor sign-in/out log and routing telephone calls to appropriate personnel in the Main 	Building lobby continually from 7:30 a.m. to 5:00 p.m., Monday through Friday, except 		Federal Holidays.

(A)	Ensure that unauthorized persons are not permitted into the building and report 			unauthorized entry immediately to the Location Administrative Officer (LAO).

- Take messages, receive packages, and make telephone calls when necessary; 	periodically make visual checks of the security monitors.

- Maintain a log assuring that all visitors register in and out.  Ensure that visitor log 	entries are complete and legible prior to issuing (temporary) ID badge; visitors 	must show photo identification and reprint name if necessary.  Visitors shall be 	detained in the lobby for government escort.  Receptionist must be familiar with 	all areas of the buildings and surrounding grounds to ensure a quick response to 	emergency calls.

C.3.3	Mail Service

The Contractor shall provide incoming and outgoing mail service, including express 		mail such as Airborne, Federal Express or United Parcel Service (UPS).  These services 		shall be performed between the hours of 8:00 AM to 4:30 PM, Monday through Friday 	excluding Federal holidays. All mail shall be handled in accordance with applicable 		U.S. Postal Regulations.

The Contractor shall:

- Monitor the meter (mail) machine to ensure adequate postage.

- Distribute incoming mail by placing items in appropriate addressee box for interoffice distribution.

- Pick up incoming mail from Berkeley Post Office by 10:00AM and place in appropriate addressee box for interoffice distribution; first class mail shall be distributed by noon each workday.  The Contractor is allowed use of Government vehicles in performing this task.

- Mail delivered by the US Post Office shall be distributed within 2 hours of receipt.

(E)	Express and UPS priority mail shall be delivered to addresses within one hour after receipt in the receiving room. Express mail will be processed for pickup by the individual carrier; current carrier picks up mail daily, Monday - Friday at 3:00 PM.

(F)	Outgoing mail shall be sorted into three categories - international, domestic and pouch mail, and processed for postal pick-up each workday.

1.        International mail shall be weighed, customs slip filled out and attached 	(if necessary), postage affixed by meter and placed in mail bag/box.

2.	Domestic mail shall be weighed (if necessary), metered postage affixed and placed in mail bag/box.

3.	Pouch mail should be consolidated and appropriately addressed/metered for mailing.

(G) 	All outgoing mail is picked up from the mailroom by U.S. mail carrier daily at 3:00 PM.  Outgoing mail received in the mailroom after 2:30 PM shall be taken to the Berkeley Post Office on the morning of the following workday when mail is picked up at 10:00 AM.

C.3.4 Vehicle Dispatching

The Contractor shall:

(A)	Schedule/reserve Government-owned vehicles, including maintaining a daily dispatch record with the name of the person the vehicle is assigned to, time out, destination, time in, and ending mileage.  Ensure vehicle operation records, including mileage, maintenance and repairs are maintained on a daily basis through use of the ARS Form 715 (booklet).  These booklets shall be submitted to the ACO upon completed.

(B)	Report (verbal or electronic) odometer readings of each vehicle to the General Services Administration on a monthly basis.

(C)	Call GSA for instructions on where to have the vehicle taken for repairs/maintenance (the Government is responsible for fuel and vehicle repair costs). When service is due GSA will send the required maintenance service forms on each vehicle.  Survey exterior condition and report any damage to ACO/QAS within 24 hours of inspection and file report documentation to GSA.

C.3.5	Messenger Services

The Contractor shall:

(A)	Deliver and pick-up scientific and library material or supplies between the Albany Research Location and the University of California at Berkeley services three times per week at 10:00 AM.  A round trip is estimated at one hour daily.

(B)	Provide messenger service for local stockroom materials upon request, and washing and cleaning vehicles (interior and exterior), refueling, and servicing vehicles, including monitoring fluids, tires, etc.  Trips shall not interfere with mail processing and distribution. These services are needed an average of once per day.  The Contractor is allowed use of Government vehicles in performing Messenger Services.

C.3.6	Flag Duties

The Contractor shall raise (by 8:00 AM) and lower (at 5:00 PM) Government-furnished flags according to regulations or as modified by the Administrative Contracting Officer. There is one flagpole at the Albany Location.

C.3.7	Lost and Found Property

The Contractor shall ensure that all articles of personal or monetary value found on the premises by the Contractor’s employees are tagged to identify the date and the location at which they are found and turned over to the Administrative Contracting Officer.

C.3.8	Key and Key Card Control

The Contractor shall:

(A) 	Establish and implement methods to ensure that all keys and cardkeys issued by the Contractor and approved by the Government are controlled and accounted for, and are not used by unauthorized personnel.

(B) 	Manage, control, issue, and keep records for all keys and cardkeys. No keys or

cardkeys shall be duplicated without ACO approval.

(C) 	Report the occurrence of a lost key or cardkey immediately to the Administrative

Contracting Officer; and prohibit the use of Government-issued keys by any persons other than the Contractor’s designated employees.

(D) 	Replace the core/lock at no cost to the Government if the Contractor loses a standard or electronic key; a lost master (standard or electronic) key requires all locks and keys for that system to be replaced by the Contractor with the total replacement cost borne by the Contractor.

- Prohibit the opening of locked areas by Contractor employees to permit entrance of persons other than the Contractor or Government employees engaged in the performance of assigned work in those areas.

- The Government will provide an initial access cardkey; thereafter a $10 replacement fee is required.

C.3.9	Certifications and Licenses

The Contractor shall:

(A)	Ensure that Contractor personnel possess all the requisite training and certifications in 	    such areas as boiler operations, asbestos removal, equipment operations (heavy equipment, forklift, etc.), CPR/First Aid Training and submit proof to the Administrative Contracting Officer (ACO) prior to commencement of services.

(B)	Ensure that all Contractor personnel operating equipment/vehicles in the performance 	     of work under this contract are properly licensed for operation of each equipment/ vehicle type with which they will work.

- Update all licenses and certifications prior to their expiration in a manner that is not     disruptive to accomplishing the work of the Albany Research Location.

(D) 	Certify all equipment in accordance with Federal, state and local codes and submit 	        certifications to the Administrative Contracting Officer. These certifications include but are not limited to: elevators, fire alarm system, fire extinguishers, SCBA units, emergency generators, above-ground and underground storage tanks, backflow preventers, boiler/pressure vessels, fume hoods, respirators and cranes.  Refer to Appendix 10 for equipment certification and frequency.

C.3.10	Registration

All Contractor employees shall register with the Administrative Contracting Officer before starting work under the contract. The Contractor shall maintain a daily sign-in/sign-out register for subcontractor employees and ensure visitor ID badges are provided.  Contractor shall also require on-site subcontractors to submit Form ARS 230 (Non-citizen Data Sheet) to ACO/QAS as necessary.

# C.4	Environmental Health and Safety Program (EH&S)

The Contractor shall:

(A) 	The primary role of the EH&S Manager is to provide Government safety support services to the Location.  Develop, maintain, update and administer an EH&S Plan which encompasses site policies and procedures in accordance with applicable regulations and standards.

(B) 	Manage and administer the occupational health maintenance program, safety and health education/training program, hazardous waste management program, asbestos abatement program, industrial and chemical hygiene programs, hazardous materials handling/storage program, community right-to-know program, safety and health orientation program, and hazard communication program.

(C)	The EH&S Manager may be required to provide safety support at ARS field locations in Davis, California and Reno, Nevada.

C.4.1	Asbestos

The Contractor shall:

(A) 	Comply with current regulations issued by OSHA, EPA, the National Institute for Occupational Safety and Health, California Department of Environmental Quality, and the USDA’s General Technical Provisions for Asbestos Hazard Abatement Work.

- Ensure that employees performing asbestos work under this contract have 	annual physical examinations and use respirators while performing such work.

C.4.2	Accident Program

The Contractor shall:

(A)	Notify LAO immediately of accidents considered emergencies; and within four (4) hours of any accident considered a non-emergency; and provide a written report to the LAO and ACO within three (3) days of the incident.

(B)	Coordinate, if required, transportation to a medical facility.

(C)	Investigate all unsafe acts or hazardous conditions; file report within (1) day with the ACO; open and maintain a file on the condition; and submit weekly report until condition is resolved.

C.4.3	Environmental, Health and Safety Tasks. The Contractor shall:

(A)	Administer and monitor environmental, chemical hygiene, and occupational health programs in accordance with USDA, ARS, OSHA, EPA, the State of California, and local agencies.

(B)	Train, advise, assist, and coordinate activities of the First Aid, Spill Response Team, and Emergency Response Team; advise and assist the Location Coordinator, Research Leaders, Principal Investigators, Project Leaders, and other Location management and administrative staff in EH&S.

(C)	Monitor laboratory air quality, noise pollution, and fume hood performance tests.

(D)	Assist the Location Radiation Program Official (LRPO) and the biological and toxic substance activities; provide radiological technical assistance to users in the LRPO’s absence and act as backup support.

- Advise, assist, coordinate, and chair activities of the Location Safety Committee.

- Investigate accidents and maintain Location accident files for unbiased 20 investigations or reported unsafe and hazardous conditions

(G) 	Administer and monitor occupational/environmental safety and employee health program files; maintain records and provides follow-up for any medical monitoring or baseline medical and check-up programs.

(H)	Schedule medical examinations and consultations with outside medical facilities and physicians in accordance with ARS Manual 230, “Occupational Health Maintenance Program Procedures”.

(I)	Prepare written report, graphs, or photographs; conduct random inspections and investigations; conduct annual inspection and prepare analyses and recommend solutions or corrective action to the Location Coordinator.

(J)	Prepare Location wastewater permit application (current 5-yr permit expires 2007).

(K)	Maintain the safety library; ensure all changes, additions, and deletions are promptly posted to the latest edition of the laboratory Safety Manual; assist in updating the MSDS laboratory safety cabinets.

(L)	Participate in Area Safety and Health Manager’s teleconferences.

- Participate in the Environmental Management System (EMS) committee as required by Location management. Provide site recommendations in support of Executive Orders 13148, Greening the Government Through Leadership in Environmental Management; Executive Order 13101, Greening the Government Through Waste Minimization, Recycling and Federal Acquisition; and Executive Order 13123, Greening the Government Through Efficient Energy Management.

C.4.4  Safety Training Activities

# The Contractor shall

(A)	Maintain a safety-training program designed to achieve awareness of safety hazards 	and corresponding preventive procedures as required by legal regulations.

(B)	Review employee training requirements and provide appropriate courses and 	seminars.

(C)	Develop training on proper use for specialized equipment and analyses of new or modified work practices, methods, techniques, standards and equipment.

(D)	Instruct employees on a variety of environmental, safety, occupational, chemical, 	radiological, biological and physical safety, various laboratory safety needs and 	ventilation requirements.

(E)	Ensure Contractor safety and health personnel are certified as instructors in first aid and CPR; conduct first aid, CPR training quarterly refresher courses (annually) for Center personnel; biannual refresher radiation safety training; bloodborne pathogens annually and respiratory protection training annually.

(F)	Conduct safety orientations twice a year and no more than four times a year, to 	include location of material safety data sheets (MSDA), Right-to-Know compliance 	training, and Departmental guidelines for all new employees.

(G)	Prepare, update, and maintain safety-training records for all employees; and 	provide safety-training materials to all new employees.

(H)	Take advantage of free safety presentations, films, tapes, and 				demonstrations available from vendors and companies and attend on-site 			training courses offered by the OSHA Training Institute.

(I)	Conduct safety training for Location response teams (ERT, Spill Response, 			First Aid).

C.4.5	Management of Chemical Storage Activities

The Contractor shall:

(A)	Manage all chemical storerooms and storage facilities including the chemical 			storage building, hazardous waste storage building/marshaling facility, 			chemical stockroom, radioactive waste storage building, fluorescent tube 			storage/recycling area, corrosive chemical storage, above-ground/underground 			storage tanks monitoring and permits.

(B)	Coordinate identification, labeling, shelf placement, and disposal of 			chemicals, solvents, gases, and fuels with the Location safety committee

(C)	Maintain chemical inventory logs/lists.

(D)	Rotate or dispose of chemical inventories to prevent accumulations of out-of-date materials. Ensure that all stockroom, receiving, tradesmen and janitorial personnel are trained in the safe handling, storage, and movement of chemicals, solvents, gases, and fuels.

(E)	Inspect the chemical storage areas quarterly, and present results at the next Safety Committee meeting.

C.4.6	Management of Hazardous Waste (HW) Disposal Programs

The Contractor shall:

(A)	Collect/handle and storage of all hazardous wastes; the HW disposal program and the operation of the HW storage site/marshaling facility. This effort will be coordinated with the hazardous waste coordinators. (The Government subcontracts HW disposal and the Contractor monitor’s the waste pickup/removal.)

(B)	Oversee the movement of HW to the designated holding facilities and collection of the HW inventory logs.

(C)	Maintain, review and submit hazardous waste logs to the ACO for Government disposal every two months; no HW shall be stored in the marshaling facility more than 90 calendar days.

(D)	Inspect the hazardous waste storage site and handling sites to ensure that HW containers/drums are properly sealed, secured and identified/labeled.

(E)		Maintain hazardous waste inventory logs.

(F)	Ensure that wastes are processed in such a manner that all possible waste substances are removed from the site, and that any spills are appropriately contained, cleaned and reported to the ACO and the Location Coordinator.

- Perform general maintenance and housekeeping of the marshaling facility.  Ensure HW and chemicals are stored properly and that the site is neat, orderly, and free of debris.  Maintain pertinent records, such as HW inventory logs and HW manifests; ensure inventories are accurate and up-to-date.

- Maintain the OSHA required PCB log associated with PCB-containing oil used in circuit breakers, switches, and transformers.

# C.5.	Facilities Services General

The Contractor shall perform the following general services (maintenance, installation, repair, etc): carpentry, masonry, painting, and locksmith services.  All debris associated with O&M construction, modification, repair, or maintenance shall be removed from the facility by the Contractor; excess metals shall be recycled.  When materials are in good shape and could be reused, they shall be stored for future usage.  All work must meet applicable building codes such as those of the city, county, state, national and trade.

# C.5.1	Maintenance and Repair Services

The Contractor shall:

- Assemble, relocate, mount/install, cut, shape, erect, repair and maintain, wood, and non-wood items and structures, including but not limited to:

| Door and door frames | Window pane/frame repair, replace |
| --- | --- |
| Structural joints | Hardware-locks, closers, stops |
| Sheet Metal closures | Staircases, awnings, shades |
| Interior walls and trim | Cabinets, bookcases |
| Subflooring | Shelving |
| Welding, caulking | Masonry structures |
| Tiling (Ceiling & Floor) | Roofing/gutters/flashings |
| Carpeting | Trusses, beams, rafters |
| Furniture/equipment | Fire extinguishers |
| Systems furniture | Wall decorations, pictures, etc. |

(B)		Maintain, modify, adjust and repair roofs that are built up, shingle, single-ply, 	rolled,  	metal, or membrane, including repairs, flashings, repair and clean 	gutters and down spouts, and maintain lightning protection systems.

(C)	Maintain and repair floors (finished and unfinished) and floor coverings/baseboards including linoleum, tile, carpet, concrete, and other masonry products in accordance with accepted trade and industry standards.

(D)	Maintain, repair, adjust, and install locks in accordance with the approved key control plan including locks in doors, closets, desks, and file cabinets; and rekey lock, repair or rebuild lock mechanisms; unstick and unfreeze locks; and install new locks.

- Keep the Albany Research Location free of pests, including cockroaches, ants, 	silverfish, fire ants, termites, rodents and gophers. Pest 	control/extermination excludes

the Small Animal Facility (SAF) and interior Greenhouse space. Office/Laboratory pest control and exterior Greenhouse pest control (e.g., spraying at greenhouse foundation) must be coordinated with the Government. Inform occupants prior to chemical applications.

- Set-up/dismantle audio equipment/tables/chairs/platforms for outdoor events and                   move equipment, furniture, and supplies, anywhere within the Location.

# C.5.2	Housekeeping

# General.

The Contractor shall furnish and maintain all equipment and supplies to perform housekeeping services for the Albany Research Location (except areas containing animal laboratories and biocontainment areas) which includes keeping the buildings free from trash, litter, dirt, lint, scuff marks, spots, and any foreign matter that might preclude an acceptable appearance/ condition. The Location shall be cleaned in a manner that is visibly appealing to employees and visitors. The Contractor shall exercise caution and safety when performing housekeeping tasks and use OSHA approved cleaning products. Environmentally-friendly products are preferred (i.e., bio-degradable).  An EPA-registered hospital disinfectant is preferred in floor cleaning of microbiology laboratories in the West Annex Building (labs 305 – 310, 312, 313, 334 and 408).  Floor cleaning in 408 is performed upon customer request which is approximately once per month.  Wet areas from mopping shall be clearly posted with cautionary signs.  Housekeeping tasks include but are not limited to:

| Trash removal/disposal/recycling | Carpet shampoo/cleaning |
| --- | --- |
| Sweeping and mopping floors/stairs | Cleaning entrance mats |
| Dusting | Glass cleaning |
| Cleaning drinking fountains | Wet mopping |
| Spot cleaning | Exterior ashtray/trash receptacle disposal |
| Cleaning light fixtures Drapery/blind cleaning | Setting-up conference rooms and audiovisual equipment |
| Sidewalk, steps and entryway pressure washing | Changing light bulbs Cleaning elevator cabs |
| On-site furniture/equipment/office Relocation | Cleaning conference rooms/furniture Floor refinishing (after- hours) |
| Cleaning/disinfecting/deodorize restrooms | Spill cleaning (non-hazardous spills) |
| Exterior/interior window cleaning Vacuuming carpets | Remove/dispose/relocate excess and discarded/salvaged items |

# C.5.2.1 Housekeeping Tasks

The Contractor shall perform facility-wide housekeeping services, except in the secured area of the small animal facility (SAF) and first floor computer room in the West Annex Building:

(A)	Notify the ACO of problems or items that require maintenance or repair.

(B)	Store and secure cleaning supplies and equipment in a safe, sanitary, and neat manner; cover containers securely.

(C)	Replace mops, cloths and sponges before offensive odors are noticeable.

(D) 	Post a schedule of housekeeping tasks, including building/area day and time when task shall be accomplished during the workday (from 8:00 AM - 4:30 PM).

- Empty all trash and recyclable receptacles daily; including cigarette butt receptacles, 	bulk waste (drums, barrels, bags, broken glass) receptacles, and other trash containers; 	remove daily any boxes, cans, and papers placed near a trash receptacle and marked 	“TRASH or RECYCLABLES”; and replace any soiled or torn plastic trash 	receptacle liners.

- Maintain/empty waste bins/trash containers/dumpsters and provide neat appearance 	of adjacent areas.

(G)	All floors throughout the Location without carpet shall be swept and mopped at least weekly except for restrooms and stairwells or cafeteria/lunchroom floors that must be cleaned/sanitized daily.  Epoxy floors shall be scrubbed and cleaned at least monthly; buff corridor floors monthly. Refinish floors whenever necessary to maintain clean and attractive appearance.  All finished floors shall be stripped and waxed at least annually; submit a schedule of stripping/waxing to ACO and QAS prior to services.  Any furniture, wastebaskets, or equipment that Contractor employees move to perform cleaning, shall be placed back in their appropriate location.

(H) 	Vacuum weekly all rugs, and carpeting to remove surface dirt/debris from edges and corners; maintain entry mats in a clean manner; care should be given to not damage furniture or baseboards.  Annually steam clean or chemically dry clean all carpet; provide cleaning schedule prior to services.

(I)	Respond immediately to assist in non-hazardous spill clean-up (e.g., coffee, water, 		etc.).

(J)	Clean and disinfect daily all restrooms including includes commodes, urinals, fixtures, wash-basins, using an acceptable nonpungent, germicidal disinfectant solution; polish metal fixture units and plumbing/piping; all partitions, wash-basins, walls, mirrors, lights and other components of each restroom shall receive thorough cleaning.  Stock restrooms with supplies such as toilet tissue, paper hand towels, seat covers, liquid hand soap, and sanitary napkins as needed.

(K)	Ensure that dust/dirt does not accumulate on horizontal and vertical surfaces such as radiators, heaters, door panels, railings, pipes, louvers, fire extinguishers, sills, phone booths, light fixtures, windows, grilles; dust and clean executive office suites weekly; do not disturb papers, books or other materials located on desks, tables, cabinets, or files; and do not damp-wipe desks.  Also maintain areas such as entryways, doorways/landings, rooftop landings, steps, vestibules, and elevator cabs.

(L)	Ensure that conference rooms are maintained in a neat and orderly fashion.  Tables, furniture, and surfaces shall be kept clean and organized; arrange furniture and audiovisual equipment for various meetings and training sessions.

(M)	Set-up/arrange and clean up after each event, conference rooms in the Main Building and West Annex Building, including tables, chairs, and presentation equipment for seminars, meetings, training sessions and miscellaneous gatherings, e.g. retirements, USDA Club functions.

(N)	Clean all interior and exterior windows including mini and Venetian blinds; develop a schedule to perform this service and submit to the Administrative Contracting Officer on an annual basis prior to scheduling. All sills and stone panels shall be cleaned of spots, streaks or runs; window tracks shall be cleaned by vacuum cleaning or scraping to assure that all windows function properly.

# C.5.3	Painting General.

The Contractor shall maintain and paint offices, laboratories, and facility buildings/structures such that finished surfaces are free of peeling, cracking, chipping, running, flaking or other defects. Common areas such as corridors, stairwells, doorways, elevator cabs, lobbies, copy rooms, restrooms, conference rooms, cafeterias/lunchrooms, and front steps shall be painted, decorated, and refinished at least once every 5 years; a Painting Plan shall be submitted to the ACO and QAS prior to service. Painting/refinishing of exterior (outdoors) building surfaces, except for curbs and pavement signage/crosswalks, and entryway steps shall be performed as additional work; all other painting/refinishing shall be routine work.

# C.5.3.1 Painting Tasks

The Contractor shall:

(A) 	Move, cover or otherwise protect equipment, furniture, and like items within the work area prior to start of painting/refinishing tasks.

(B) 	Remove highly sensitive and valuable laboratory equipment only upon approval by ACO.

(C) 	Cover equipment and furniture that cannot be readily removed with drop cloths to prevent splatter damage.

(D) 	Return items to their original arrangement or as instructed by occupant(s), upon completion of painting/refinishing tasks.

(E)	Prepare, paint and refinish laboratory cabinets as necessary.   Construct and paint signs/sign supports as needed.

(F)	Observe safety and biosecurity precautions at all times when working in laboratory modules and restricted areas.

(G) 	Paint/refinish such that surfaces are free from runs and misses, and remain smooth.

(H)	Maintain, at an acceptable level, all painted surfaces including curbs and pavement markings, exterior piping, panels, and concrete berm (at the hazardous waste storage building/lockers).

(I)	Maintain and repaint road markings/stripes, crosswalks, curbs, fire lanes, fire hydrants/standpipes so that they are readily visible (not worn or peeling).  Road markings, curbs, fire lanes, fire hydrants/standpipes shall be painted every two years; wood deck, benches, tables should be refinished/preserved annually.

# C.5.4 Grounds Maintenance

The Contractor shall:

The Contractor shall maintain all grounds, road and parking surfaces, sidewalks, storm drainage systems, fencing, and signs.  The Contractor shall furnish all grounds equipment, materials (including fertilizers, herbicides, insecticides), fuels and supplies for exterior grounds. All personnel engaged in mowing shall wear safety equipment (shoes, glasses, hearing protection, gloves and employ OSHA safety practices). All work accomplished under the provisions of this section shall be charged to routine maintenance for Grounds Maintenance, unless otherwise stated in this section.  The Government intends to redevelop the east lawn area through an outside contractor (design plans in Appendix 2) which will significantly reduce the grounds maintenance; the projected completion date is 2007.

# C.5.4.1 Grounds Maintenance Tasks

The Contractor shall:

(A) 	Maintain grounds that are appealing to employees and visitors to the 					Location.

(B) 	Mow all lawn areas in a uniform fashion of 1.5 to 3 inches in height while leaving no patches of uncut grass and preclude scalping; clean all sidewalks, steps, entryways and walkways of grass leaves and debris immediately after mowing.

(C) 	Trim and edge during each mowing. Any vegetation or grass extending over the edges of walks, curbs, passageways, hedgerows or flower beds shall be neatly cut, using equipment especially designed for this purpose, and removed to leave a neat, uniform edge between the lawn area and adjacent curb, walk or roadway.

(D) 	Thatch and replant as needed. Trim around buildings, trees, shrubs, parking signs, fire hydrants, and other obstructions.

(E)	Water lawns, shrubs and ground coverings on a schedule to maintain healthy vegetation dependent on California drought situation.

(F)	Repair and seed damaged or worn areas of the lawn.

(G) 	Trim and prune trees and bushes to maintain desirable shape and growth characteristics as well as protecting the building and/or wires, walkways, and roadways.

(H)	Seasonally prune, condition soil, trim and fertilize trees, shrubs, and plants.  Provide mulch in flowerbeds as needed.  Replacement of annual flowers is additional work and shall be coordinated with the ACO.

(I)	Remove leaves/debris from the grounds, parking areas, rain gutters, drains; remove weeds from the grass and flower beds and apply herbicides/insecticides, fertilizer, soil conditioners; apply necessary treatment to avoid infestations of insects and/or disease. Storm drainage systems including grates shall be maintained to permit drainage.

(J)	Remove/dispose of all debris and litter from the grounds, sidewalks, walkways, entryways, landings, steps, exterior vestibules, parking areas; remove vegetation from walkways, courtyard, and parking areas.

(K)	Apply herbicides, insecticides/pesticides, and fertilizers so not to harm or interfere with research and the intake and contamination of the air supply. ACO/QAS approval is required one week in advance of the scheduled work. All chemicals shall be approved by the ACO before being used.

(L)	Maintain and inspect the security fence and gates (approx 4155 feet of fence; manual gates; cardkey auto-gates; cardkey operated, electric industrial barrier gates).

(M)	Quarterly clean the quarantine greenhouse “moat” which contains small fish to control algae.  Remove at least 80% of the settlement, leaves and debris to maintain a suitable condition.

(N)	Road and parking signage will be repaired/replaced as needed.

# C.5.5    Fire Protection

- Establish a schedule for the inspection (including visual inspections) of fire extinguishers and fire hoses in accordance with the National Fire Protections Association.  Maintain fire protection equipment, including fire extinguishers and fire hoses, for ready use; recharge fire extinguishers after each use and hydrostatically test every 5 years.

- The Contractor shall be responsible for the maintenance, repair and certification of all fire protection systems, including pull stations, fire alarm annunciator and control panels, magnetic door-hold system for smoke protection, hood/building sprinkler systems, fire standpipe systems, smoke and heat detectors, fire hoses and assemblies, CO2 and Halon systems, control panels, valves, safety devices, testing devices, activating devices, relief valves, nozzles, etc.

(C) A list of Government personnel to contact when the fire alarm sounds after-hours, will be   made available following contract award.

# C.6	Utilities Service

# C.6.1	General.

The Contractor shall install, relocate, modify, repair, replace, test, and maintain all electrical systems, facilities, and distribution equipment adhering to the National Electric Code and sound electrical engineering standards. Services include but are not limited to electrical controls, motors, lines, systems, fixtures, outlets, panel boxes, switchboard, power circuits, transformer vaults, and other related equipment, located at the Albany Location.  Repair and maintain research equipment and install utility services/connections for research equipment.  The type of electrical equipment installed, modified, and maintained includes but is not limited to:

| High and low voltage distribution systems | Elevators PA system |
| --- | --- |
| Lighting, systems; energy efficient florescent tubes/lamps | Automatic doors Automatic projector screens |
| Full spectrum incandescent/mercury/sodium bulbs | Automatic gate barriers Automatic window coverings |
| Facility HID lighting/security lights/lamps | Keyless (cardkey) access system Uninterruptible Power Systems (UPS) |
| Research equipment (centrifuges, freezers, refrigerators, coolers, chillers, fume hoods, biosafety cabinets/hoods, laminar flow hoods, tissue culture hoods, incubators, shakers, environmental chambers, sterilizers/autoclaves, dishwashers, ovens, dryers, x-ray equipment) Switches, stations relays, wiring and related parts | Exit /Emergency exit signs CCTV system Intrusion detection system Telephone system, raceway and conduit Re-set/adjust facility clocks/timers Emergency power generators Electrical systems Dispose/recycle spent fluorescent tubes Install Government-furnished greenhouse HID lamps |

The Government shall furnish necessary materials in repairing laboratory freezers, refrigerators, coolers, reach-in environmental chambers, dishwashers, ovens, dryers, and laboratory pumps; labor is routine work.

The site’s electrical service is picked up at the corner of Buchanan and Filmore Street from an overhead wire, from the local utility company, Pacific Gas and Electric (PG&E) Company. Power is supplied at 12 KV, goes underground to the main electrical vault located in the Administrative Wing basement, and is distributed to the following transformers: (1) Greenhouse Complex, (2) North Wing, (3) South Wing, (4) Administrative Wing and (5) Western Annex Building. Transformers are 3 phase, 208V and 408V.

# C.6.1.1   Electrical Tasks

The Contractor shall:

(A)	Maintain and repair the electrical distribution system and its component parts from the main electrical vault throughout the Albany Research Location. Basic components of the electrical distribution system consist of underground cable runs between buildings, power manholes, power and distribution transformers, emergency power generators, primary and secondary metering equipment, batteries/uninterruptible power system, control panels, circuit breakers, safety switches, relays, power poles, and relays.

(B)	 Schedule power outages (date/time to be approved 2 weeks in advance by the ACO).

# C.6.1.2  Telecommunications Service and Maintenance

# General.

The Contractor shall provide telecommunications support services including installations, modifications, repair, replacement, and maintenance of the T1 line, CSU/DSU interface; and the Mitel 2000 Lite system with MS2007-F-NA-00, edition SX.N.6.4.1 software.

The Contractor shall:

(A) 	Perform system programming including backup of existing data files and adding new telephone stations, changing the location of existing telephone stations and deleting telephone stations as needed.

(B)	Efforts must be made to prevent interruptions to service. If interruptions should occur, the Contractor shall re-establish telecommunications service as soon as possible and immediately inform the ACO or QAS of occurrences of prolonged or serious interruptions in service.

(C) 	Provide maintenance and repairs on an as-needed basis during work hours, to include trouble-shooting telephone malfunctions such as line noise, dead station lines, constant busy signals. Maintain a malfunction incident log that includes: (a) Date and time notified, (b) Date and time of telephone response, (c) Description of problem, (d) Explanation of repair, and (e) List of applicable replacement parts.  Replacement parts shall be either new or refurbished parts in warranted, as-new condition.

# C.6.2  Plumbing and Pipefitting

The Contractor shall:

Maintain, install, modify, inspect, lubricate, troubleshoot, test, check, clean replace seals and valves, insulate piping, and apply protective sealant/paint to exposed piping and valves, including:

| Water (domestic hot, domestic cold, fire sprinklers, chilled water systems, demineralized, distilled, ultra-pure, deionized, reverse osmosis (RO) systems, and purified water systems) | Underground potable water distribution system Sanitary sewer and storm drain systems Flow/backflow tests (including backflow prevention devices) |
| --- | --- |
| Water meters | Compressed air systems |
| Special compressed (cylinder) gases for scientific equipment; high-pressure nitrogen system | Vacuum systems Services for equipment/instruments Grease traps |
| Steam and condensate systems | Venting and draining |
| Lavatories | Emergency shower/eyewash stations |
| Faucets (hand and foot controls) and fixtures | Water coolers Irrigation systems |
| Natural gas systems | Clear piping obstructions in accordance with equipment specifications and manufacturer’s instructions, local, state and national plumbing codes. |

# C.6.3	Heating, Ventilation Air Conditioning (HVAC) and Refrigeration Tasks

# General.

The Contractor shall ensure that heating and cooling, ventilation, refrigeration, hot water services, steam and chilled water services, boiler plant and high purity water systems are provided in accordance with all Federal, state and local codes and all applicable standards. Operate and maintain systems which provide heating, cooling, ventilation, refrigeration, steam or high-temperature water, chilled water, boiler plant and high purity water systems.

High pressure steam (30-120 psi) will be provided year round, including weekends and holidays, twenty-four (24) hours a day; steam pressure shall be adjusted as required to satisfy Location demand.

The Contractor shall:

(A)	Operate, maintain, repair, overhaul, replace, and secure equipment providing steam, hot and chilled water, compressed air, vacuum, and refrigeration.

(B)	Operate boiler plant and high purity water systems which includes performing daily operational and maintenance checks, steam, feedwater, water levels/quality, and equipment checks, and maintaining operating logs.

(C)	Maintain one boiler in an operational status and one boiler in a back-up status at all times. The Government reserves the right to request either of the two boilers to be placed in a down or active status at any time. High purity water shall be supplied on a continuous basis unless it is in a down status for scheduled preventive maintenance, or Administrative Contracting Officer approved unscheduled maintenance services.

(D) 	Maintain chillers on automatic control, as required to satisfy Location space cooling demands. Chiller operation is typically between the hours of 8:00AM and 5:00PM daily; chillers are normally shutdown during the cooler/winter months.

(E)	Perform routine maintenance and repair of the boilers, auxiliary equipment and steam generating equipment, including replacing discs, packing valves, overhauling blow down valves, feed water regulator and feed water heater, packing expansion joints on steam lines, replacing gaskets.

(F) 	Schedule and perform an annual overhaul of each boiler to include cleaning and repairing or replacing tubes and steam drums, gaskets, gauge glass, sight glass, valves, fan units, controls and heaters.

- Ensure that one of the two boilers is operational at all times while the other is

undergoing maintenance or repair.

(H) 	Perform daily water sampling for each boiler, water testing and water treatment for pH, causticity, phosphate, sulfite, and total dissolved solids; maintain daily logs.  Ensure the boiler water and feedwater stay within their recommended quality limits.

(I)	Operate and maintain the water softener system manually, in the event that the automatic controls fail to perform as intended.

(J)	Collect water sample from each operating boiler once a month and submit these samples to a certified lab for testing and certification.  Daily test sample results, together with the monthly test results, shall be submitted to the Administrative Contracting Officer, Facilities Engineer, and Quality Assurance Specialist on a monthly basis. Cooling tower test results shall be included in the latter report.

(K)	Install, modify, maintain and repair hot water heating systems, heating coils, circulating pumps steam heating systems, and forced air heating systems, including space heating units (Univents), insulation of ducts, tanks, pipes, fittings, components and equipment for the purpose of heat conservation, condensation and sound absorption.

(L)	Notify the ACO when refueling is required to maintain the boiler plant operations or readiness of Location emergency power generators.  Submit a monthly report on the volume of fuel on hand as of the end of the previous month, volume of fuel received during the reporting month, and the total volume of fuel on hand as of the reporting date.  Maintain and monitor pressurized vessels and fuel-holding tanks, including underground and above-ground fuel distribution and storage systems.

(M)	Prepare water chemistry report for boilers and cooling towers on a monthly basis.  Submit fuel and water meter readings and usage reports to the ACO, FE, and QAS on a monthly basis.

(N)	Operate, install, repair, replace, adjust, overhaul and maintain commercial and industrial refrigeration and air-conditioning systems, including motors, compressors, fans, pumps, control systems, and all related equipment for maximum operating efficiency.  (See Appendix 6 for a list of refrigeration and air-conditioning equipment).

(O)	Establish a daily monitoring and maintenance schedule for refrigeration 		equipment to inspect, lubricate, clean, maintain, recharge refrigerants (recording 	amounts of refrigerant added), and test controls of motors, fans, condensers, 	evaporators, and all related equipment.  The Contractor shall be responsible for 	diagnosing malfunctions and making necessary repairs.

(P)	Install, modify, maintain and repair air conditioning, air handling, air and water filtration systems, and refrigeration systems, including maintenance, testing, and repair of all components, devices, equipment and associated systems, consisting of chillers, compressors, blowers, fans, valves, VFDs, dampers, condensers, cooling towers, chemical treatment systems, pumps, purge units, control systems, ductwork, water treatment systems, air handling units, piping, motors, evaporators, air filters, coils, circulating pumps and all other  equipment necessary for the proper operation of the air conditioning, air handling, and refrigeration systems.  All cooling towers shall be cleaned, along with chemical treatment testing, and a total bacteria-count test performed at that time.

(Q)	Provide new or factory-reconditioned parts and components for the repair of all equipment, equal to or exceeding the manufacturer’s original equipment specifications or comply with applicable industry standards.  Supply all lubricants, coolants, refrigerants, chemicals, and other consumables necessary for the proper operation of building systems.

(R)	Maintain laboratory equipment, including refrigerators, freezers, coolers, chillers, shakers, incubators, hoods, growth chambers, dehumidifiers, centrifuges, freeze dryers, autoclaves/sterilizers, ovens, dishwashers, cooling/heating baths, and small apparatuses containing heating/cooling elements.

- Perform annual preventive maintenance on fume hoods and notify the ACO of all 	fume hoods requiring repair or replacement.

- Perform facility/building patrols every 2 hours during weekends and holidays and in 	the after-hours on workdays for suspicious or unusual activity.  Maintain a log and 	contact the Albany Police Department and LAO for emergencies.  Submit daily 	patrol logs to QAS on a weekly basis.

(U)	Construction is in-progress to replace a temporary greenhouse with a new greenhouse facility similar to WRRC GH #1.  This new 3000 square foot facility will be phased-in by the summer of 2006 and include an emergency eyewash/shower station, evaporative cooling modules, an energy curtain, gas-fired unit heaters, a domestic hot water heater, motor-operated rack and pinions and ridge vent system with screens.

(V)	Perform leak rate calculations per EPA requirements for refrigeration systems containing greater than 50 pounds of refrigerant. Maintain documentation of leak rate calculations as required by EPA and corrective actions. Maintain documentation of technical training on refrigeration systems.

# C.7	GOVERNMENT-FURNISHED ITEMS

C.7.1	The Government will provide with no additional cost to the Contractor the

Government furnished items listed in Appendix 8-Government Furnished Equipment; and Appendix 9– Government Furnished Vehicles. A map depicting the work areas offered to the Contractor as a physical location to reside while performing required services as well as the identification of work areas where current operations are performed are identified in Appendix 2, Maps and Area Layouts. The Contractor shall ensure neat, sanitary, and serviceable conditions of Government furnished items (work areas, facilities, tools and equipment) while performing the work prescribed in this PWS.

The Contractor shall operate Government-furnished equipment in a safe and proficient manner. The use of equipment for other purposes separate from this contract is prohibited. The Contractor shall promote self-maintenance to the maximum extent possible without jeopardizing personnel, and vehicle safety. The Contractor shall protect equipment with frequent cleaning and use preventative maintenance and minor repairs to minimize breakdowns, depreciation, and the need for costly major repairs (the Contractor is responsible for equipment maintenance and consumables such as lubricants, belts, fuses, tires, etc.). The Contractor shall communicate with equipment manufacturers and authorized maintenance elements to ensure that equipment is maintained properly and that warranties are valid. The Contractor shall operate equipment in accordance with appropriate industry practices and techniques.

The Contractor shall provide qualified drivers/operators for the equipment that possesses a state operator’s license, and permits.  The Contractor shall ensure operators are skilled and knowledgeable of the equipment and its safety requirements. The Contractor shall ensure all vehicles are in compliance with required certifications and inspections.

Government –furnished equipment will not be replaced if it can be repaired or rebuilt to return the equipment to the existing condition at the time of acceptance by the Contractor. If the repair estimated is 50% of the replacement cost, the Contractor shall contact the ACO or QAS for replacement approval. All maintenance records and documentation providing service history shall be provided to the QAS. The Contractor shall identify all Government-furnished equipment not used or unusable due to normal usage to the Government for disposal instructions. No Government –furnished equipment shall be disposed of without Government consent. All equipment deemed to be an inherent part of a facility in the provision of services, such as air conditioning, will remain with the facility upon completion or termination of the contract and title to the equipment.

Government-furnished equipment/property is provided on an “as-is” basis in its current condition and location where the Contractor will not be reimbursed for transporting, installing, modifying, repairing, consumables, or otherwise making the property ready for use.