| United States Government | Department of Energy |
| --- | --- |
|  | Bonneville Power Administration |

| DATE: | April 5, 2005 |
| --- | --- |
| REPLY TO ATTN OF: | TOM/PPOC2 |
| SUBJECT: | 2005 Spring / Summer PDCI Probing Signal Test Plan |

| John Haner – TOM Peggy Olds – TOT | Melvin Rodrigues – TOP Rich Ellison - TOD | Tedd Snodgrass – TOV |
| --- | --- | --- |

##### SUMMARY

Under this test plan probing signal tests will be applied regularly to the Pacific HVDC Intertie during the late spring – early fall 2005 operating period. This will be continuation of regular probing tests conducted during 2003 and 2004 summer operating seasons.  The tests are conducted to get early detection of abnormalities in system damping.

The main objectives of these tests are:

- measure system damping levels to correlate them with the system loading conditions

- correlate recorded and simulated mode shape and damping to improve/validate study models

- use probing tests for generator control and performance validation.

The test duration is from May 9, 2005 to Septmber 20, 2005.

The test will be performed every day at 14:20, 15:20 and 16:20 if any of the following conditions is met:

- Grand Coulee – Malin phase angle is greater than 52 degrees, or

- California – Oregon Intertie flow is greater than 3,700 MW, or

- a test is requested by a WECC member to verify generating unit performance (>500 MW). Such request should be given a day ahead of the scheduled test.

Please see attached historic data for 2003 - 2004 seasons on COI flows and Coulee-Malin phase angle.

PDCI Probing Signal:

Three-cycle 0.25 Hz +/- 125 MW probes will be used to stimulate the power oscillations. The probe will be repeated within one minute. This is similar to the tests done during 2003 and 2004 operating seasons.

PDCI has to be above 900 MW to perform the test.

II. TEST INITIATION

Test coordination will be as follows:

- Jim Burns will schedule the tests through the BPA outage dispatcher.

- Jim Burns (BPA technical staff) will post proposed test dates on the BPA Web page.

- The day before each test, BPA will send a message on the WECC Net notifying of the tests.

- 10 minutes proior to the test time, BPA dispatcher verifies that system conditions are met (Grand Coulee-Malin phase angle is greater that 52 degrees, or COI flow is greater than 3,700 MW, or a power plant performance test is conducted) and confirms the test with Celilo operator.

- If there are concerns about abnormal system conditions, BPA dispatcher should be contacted as early as possible to cancel a test.  The test will be resumed the next hour after the system returns to normal.

- The probing signal will be injected by an operator of Celilo converter station. The operator will clear with the BPA dispatcher before the signal injection.

Submitted by:

William A. Mittelstadt – TOM			Dmitry Kosterev - TOM

Approved:  ____________________________	Date: _______________

Manager, Suppport Services for Network Planning – TOM

Approved:  ____________________________	Date: _______________

Manager, Network Planning – TOP

Approved:  ____________________________	Date: _______________

Manager, Technical Operations –TOT

Approved:  ____________________________	Date: _______________

Manager, Dittmer Dispatch - TOD

Approved:  ____________________________	Date: _______________

Manager, Munro Dispatch - TOV

cc:

V.VanZnadt – T/DITT2

B.Silverstein - TO

J.Haner – TOM

R. Ellison – TOD/DITT1

P.Olds - TOT/DITT2

T. Snodgrass - TOV/MEAD

B.McManus  – TOT/DITT2

J. Burns - TOT/DITT1

R. Spence – TOT/DITT2

S.Wiggerhaus - TOT

J.Gronquist – TOT

M.Rodrigues – TOP

G.Keenan – TOM

W.Mittelstadt – TOM

C.Taylor - TOM

D. Kosterev – TOM

D. Chase – TFRS/CELILO

L. Anderson – TFRS/CELILO

W.Litzenberger – TNP-PPO2-1

J. Bernhardsen – TO/DITT2 - NWSC

Dittmer Outage Dispatcher – TOD/DITT1

Dittmer System Dispatcher – TOD/DITT1 (2 copies)

Official File - TOP (ED-21-15)

WAMittelstadt/DKosterev  4/04/05 (ProbTesting.doc)

# Historic System Conditions

# Text boxes

DOE F 1325.8 e    Electronic Form Approved by CGIR - 01/20/95(VB)
(8-89)

memorandum

TO: