### LARGE-SCALE PC MANAGEMENT AND CONFIGURATION FOR SNS DIAGNOSTICS [1]

Darryl J. Murphy, ORNL, Oak Ridge, TN 37830, USA

J. David Purcell, ORNL, Oak Ridge, TN 37830, USA

Abstract

The Spallation Neutron Source (SNS) Project’s diagnostics group has begun its implementation of more than 300 PC-based Network Attached Devices (NAD) [2].   An implementation of this size creates many challenges, such as distribution of patches and software upgrades; virus/worm potentials; and the configuration management, including interaction with the SNS relational database.  As part of the initial solution, a base operating system (OS) configuration has been determined and computer management software has been implemented.  Each PC requires a unique configuration, but all are based on a common OS and supporting applications.  The diagnostics group has started with an implementation of an XP Embedded (XPe) OS and uses Altiris® eXpress Deployment Solution™ [3].  The use of XPe and Altiris gives the diagnostics group the ability to easily configure, distribute, and manage software on a large scale.  This paper describes the initial experience and discusses plans for the future.

1 INTRODUCTION

The SNS project is a partnership involving six U.S. Department of Energy (DOE) national laboratories: Argonne, Brookhaven, Jefferson, Los Alamos, Lawrence Berkeley, and Oak Ridge. The project is described in more detail on the SNS Web site [4].

The SNS diagnostics group is in the process of installing more than 300 PC-based NADs.  Several factors were considered in determining an approach to the configuration management of the PCs.  Although many of the devices are similar in application (e.g., there will be 157 Beam Position Monitors), the time scale of PC acquisition assured us of quite different base hardware configurations.  Modifications for future implementations as well as deployed applications will occur as the accelerator goes through its commissioning phases.  OS updates will be required.  Finally, it is expected that time will affect the PC’s hardware, and replacement of parts or entire new chassis will be needed.

It was obvious very early on that tight control had to be exercised to successfully manage such a large, diverse group of PCs.  With a challenging objective of potential push-button PC imaging and updates, it was determined that tools like Altiris and an XPe OS would lead us to the configuration control required.

2 DEPLOYMENT TOOLSET

2.1 Altiris Deployment Solution

Altiris Deployment Solution provides OS deployment, configuration, and software deployment across hardware platforms and OS types.  We leveraged the SNS Technical Information Systems Group’s experience with Altiris Deployment Solution in their  thth environment, which includes approximately 500 desktops and laptops, and tailored the PC management solution to our PC-based NADs.  Altiris Deployment Solution is a client/server PC management tool that has many features, some of which include the ability to create disk images of the PCs hard disk and to distribute that image across the network to a NAD that is configured to Wake on LAN and PXE boot.  This can be done to one or more of these devices simultaneously.  With our current OS, this process, regardless of the number of machines being configured, takes about 15 minutes.  Figure 1 shows how many PCs can be stacked and imaged at one time.  This software also allows us to deploy software, run specific scripts and configure each device from one console.  Altiris gives us the ability to take a PC from its box and, assuming the supplier has set up the bios correctly, set it in a rack where it will boot and receive its appropriate image.

2.2 Windows Server 2003

Windows Server is required for the Altiris software.  We have installed it on a dual processor 2.8 GHz server with 2 GB RAM and 140 GB of storage for disk images.  This configuration exceeds initial hardware requirements and allows for future growth.

2.3 Windows XP Embedded

Windows XP Embedded is an operating system that is based on a subset of components which has been derived from the Windows OS.  Based on the same binaries as Windows XP Pro, XPe enabled us to choose the individual components needed to achieve optimum functionality.  XPe was also chosen as the OS platform because of its ability to run with only the needed services and because of the small footprint on disk.  Currently the embedded base OS stands at approximately 300 MB compared to approximately 1 GB for the basic XP Pro installation.  This smaller image eliminates potential network security concerns as well as enables better utilization of system resources (i.e., memory).  Using the Task Manager, you can see that the number of processes running and the memory required, although varying, is half that of the standard XP Pro installation.  Conveniently, this lean image also speeds up the imaging process.

Figure 1: XPe Image Deployment Using Altiris

2.4 Support Structure (ORACLE, Controls or ORNL implementation of Network Registration [NetReg])

Network security is important to the operation of both the accelerator and to these devices.  The Diagnostics group cannot allow others uncontrolled access to the network or these machines.  The SNS Controls group has implemented NetReg, a process that requires all devices that use the network to go through a registration and scan procedure.  The use of NetReg ensures that the network does not have devices attached to it that are not meant to be.  It also scans devices prior to being attached to make sure they are virus free and properly patched.

2.5 Backup

The images are stored on a RAID 5 Storage Array and backed up to tape.

3 CONFIGURATION PROCESS

3.1 Determining Base Configuration

The deployment of all the diagnostic PCs is based on a standard base configuration.  Instead of using XP Pro or Windows 2000 as an OS, we have used the components of XP Pro to make up our embedded OS.  Determining baseline components is an ongoing process that starts with the analysis of a functioning complete OS on your planned hardware.  We analyzed functioning systems using XPe tools and use only those XP Pro components that are needed.  As work continues, it becomes obvious that certain excluded components are needed and that some included components can be omitted.  An example of this includes the use of specific control panels.  These control panels are not necessary to a running OS but are useful on our machines.  At this point, we have a base list of components that provides an OS capable of not only running the required device applications but also directly supporting development.

As the base OS becomes stabilized, other standard tools, settings, or conveniences are added to the base configuration as required.  These include major applications like LabVIEW, Altiris, Timbuktu, and the EPICS toolsets.  Settings included are the EPICS environment variables and some basic windows settings.  Other conveniences include a program that identifies which computer you are on, shortcuts to network Web pages (logbook), and a list of IP addresses for all machines that can be used with Remote Desktop or Timbuktu.

3.2 Cloning Process – Distribution

During the distribution of the devices, one has to consider the fact that the base configuration is going to be greatly distributed but that the security IDs have to be different for each implementation of XPe.  One of the components included with XPe is the System Cloning Tool.  This component is used to ensure that each device has a base image containing a unique computer security ID.  The use of the tool gives us the ability to use Altiris and distribute images without having to touch each machine.  The following image gives an example of the process.

Figure 2: Cloning Process XP Embedded [5]

3.3 Database Interaction

One problem with deploying PCs and allowing them to boot and receive an appropriate image is that a unique security ID does not identify the device and that somehow an accelerator device ID has to be assigned to the machine.  Because the PCs have to be registered with the network to function, the IP and MAC addresses are known.  At boot up time, a Java application using the JDBC thin client accesses the SNS Oracle production database to retrieve the configuration file for the Input Output Controller.  The application uses a global read-only account to access IP address of the IOC making the connection.  This IP is contained in the database and is used to look up the IOC record in the IOC_DVC table.  The application then writes the configuration file from the IOC_DVC table into a directory and file name, which are also specified in the IOC_DVC table.  No software other than the Java Runtime Environment is required to be installed on the IOC for this process.

4 CONTROL OF DEPLOYED DEVICES

Because the NADs are PC-based, many changes will have to be made to the systems over the life of the machine.  This toolset allows us to maintain control of the devices while keeping them up to date with current applications and hardware.

Because XPe is based on the Windows XP OS, it is necessary to have the ability to apply security patches to the devices in operation.  To keep device downtime to a minimum, the patches will only be applied when appropriate, but we still need the ability to quickly patch our devices in the event of an emergency.  Windows XP Embedded SP1 includes a method for this called Device Update Agent (DUA).  There are at least a couple of ways to configure DUA.  Because we have hard disks in our devices, we chose to copy the updated files to the specified directory using an Altiris Job.  This “job” can be dropped on one or many systems simultaneously.  Once the files are in place, DUA takes over the task of installing the patch.  DUA is in a constant wait mode and does nothing until the specified directory is “loaded” with the appropriate files.

Similar to Microsoft patches, the deployed devices will also require updated applications or additional software.  Again, this can be accomplished in a couple of different ways.  DUA can be triggered to run an executable that has been loaded on to the machines via Altiris.  Altiris can also deploy updates/additions in a manner similar to any type of file management.

Many of these deployed devices will also have to undergo hardware changes because of failures or upgrade needs.  Again, Altiris allows the software changes to be handled with relative ease.  Altiris can take a known configuration and monitor the changes made to it during any kind of upgrade.  This is known as a Rapid Install Package (RIP).  Upon completion of the upgrade, the RIP can be applied to any similarly configured devices.

Using Altiris as the management tool of the deployed images also gives us the ability to rapidly redeploy a device’s current configuration to replacement hardware.  As with any new configuration, applying the OS to a device takes under 20 minutes.

5 INITIAL EXPERIENCE AND FUTURE PLANS

5.1 Initial Experience

Our initial exposure to the use of these tools and their implementation required little learning time.  This was particularly true when it came to Altiris.  Previous SNS use of this application allowed us to quickly deploy it.  It was not obvious to us at all during the start that XPe was going to be of any use at all.  XPe was initially a very cumbersome tool.  Initially, it required some patience and it took us time to ramp up and use it effectively.  However, after using it for a short time, we began to see the base OS take shape and the designer tools and components have become easy to use.

Overall, the combination of these two major components have given us the ability to safely deploy an XP Pro-like image, maintain configuration control, and easily update images.  The time required to deploy an image is far shorter than using standard installation methods.  The OS runs just as an XP Pro image but without any unnecessary overhead.    And because of this process, our standard NAD is configured in a way that allows us to comfortably continue with our installation of diagnostic systems.

5.2 Future Plans

One future idea is to move to a diskless solution.  This would allow the NADs to boot up and operate from a unique disk image file located on a networked server or servers.  The OS would still be Windows XP Embedded and would allow for quick (about the same as hard disk) boot times.  This solution will be considered because of the gain in the ability to deploy new images to the same hardware.   Before completely converting to a diskless deployment, diskless operation would provide a reliable backup system in case of hard disk failure.  Currently we are evaluating a product called BXP from Venturcom[6] that can give us this ability.

The interaction with the relational database gives us the opportunity to expand the database role and use it to capture and house device images as a whole.  Although Altiris provides a simple way to handle images and 300-400 images is not that great of a number overall, the relational database naturally lends itself to be the repository of all data related to a device.

Because these machines are configured with an XP Pro-like image, we have included the Remote Desktop Feature.  This has given us the ability to log on to the machines over the network and has not required the use of monitors within each rack.  However, XPe allows the devices to be headless (no graphical interface).  Using a headless configuration may give us increased stability and/or increase the efficiency of the operating system.

6 REFERENCES

[1] Work supported by the U.S. Department of Energy under contract DE-AC05-00OR22725.

[2] “Network Attached Devices at SNS”, W. Blokland and T. Shea, ORNL, Oak Ridge, TN, USA, M. Stettler, LANL, Los Alamos, NM, USA. DIPAC 2003.

[3] SNS Web site: http://www.sns.gov/.

[4] http://www.altiris.com/products/deploymentsol/.

[5] Sean D. Liming, “Windows XP Embedded Advanced”, RTC Books, 2003.

[6] http://www.vci.com.