June 18, 2001

To:	Distribution

From:	Bob Ducar

Re:	Update of Communication Duct Cabling Requirements for MiniBooNE and NuMI

# MI-10 Service Building to MI-12 MiniBooNE Target Hall	~525 ft

| Utility | Type of Cable | Comments |
| --- | --- | --- |
| Accelerator Computer Network | Fiber Optic Trunk 24 Singlemode Fibers | Sourced from MI-10. |
| Main Injector CAMAC Link Tevatron Clock (TCLK) Main Inj Beam Sync (MIBS) Machine Data (MDAT) MiniBooNE Beam Permit NuMI Beam Permit DDC Utility Monitor Sys (?) | Fiber Optic Trunk 36 Multimode Fibers | Sourced from MI-10 |
| Innerduct for Above Two Fiber Trunk Cables | 1.25” ID Plastic Innerduct with Pull Rope | One is Enough Here |
| Bstr Extraction Sync (BES) Booster RF (BRF) | Qty 2 – 1/2” Cablewave/Heliax 50 Ohm Coaxial Cable | Sourced from MI-10 |
| Beam Pos Monitor Signal Spare 50 Ohm Mon Cable | Qty 2 – 7/8” Cablewave/Heliax Foam Dielectric 50 Ohm Coaxial Cable | Sourced from MI-10 |
| Safety Interlock | Qty 4 – 20 Conductor 18 AWG Cable | Two of these stop at MI-12. The other two continue on to MINOS |
| Safety Data Links and Audio Warning | Qty 2 - Four Twisted Pairs, 18 AWG | Sourced from MI-10. Stops at MI-12 and Continues on to MINOS |
| FIRUS | Qty 3 – 1/2” 75 Ohm Hardline Coax Cable. | Sourced from MI-10 |
| CATV | Qty 3 – 1/2” 75 Ohm Hardline Coax Cable. | SWYD A System, a B System for Cameras, and a Spare. These are Minimum Requirements. Sourced from MI-10 |
| Telecommunications | Telephone Trunk Cable 25 or 50 Pair, 24 AWG | Sourced from MI-10 |
| NuMI Fire Protection Connectivity between NuMI Target and MINOS Bldgs | Qty 1 – Several Twisted Pairs, 16 or 18 AWG | Passes through MI-12 to MINOS |

# MI-12 MiniBooNE Target Hall to MiniBooNE Detector Building	~1,800 ft

| Utility | Type of Cable | Comments |
| --- | --- | --- |
| Accelerator Computer Network and Connectivity to Feynman via Detector | Fiber Optic Trunk 24 Singlemode Fibers | Sourced from MI-12 |
| Main Injector CAMAC Link Tevatron Clock (TCLK) Main Inj Beam Sync (MIBS) Machine Data (MDAT) MiniBooNE Beam Permit NuMI Beam Permit DDC Utility Monitor Sys (?) | Fiber Optic Trunk 36 Multimode Fibers | Sourced from MI-12 |
| Innerduct for Above Fiber Trunk Cables | Qty 1 (or 2?) 1.25” ID Innerduct with Pull Rope | Consider Pulling a Spare Innerduct Here to Facilitate Future Pulls |
| Bstr Extraction Sync (BES) Booster RF (BRF) | Qty 2 – 1/2” Cablewave/Heliax 50 Ohm Coaxial Cable | Sourced from MI-12 |
| Beam Pos Monitor Signal Spare 50 Ohm Mon Cable | Qty 2 – 7/8” Cablewave/Heliax Foam Dielectric 50 Ohm Coaxial Cable | Sourced from MI-12 |
| Safety Interlock | Qty 2 – 20 Conductor 18 AWG Cable | From MI-10 on the way to MINOS. |
| Safety Data Links and Audio Warning | Qty 2 - Four Twisted Pairs, 18 AWG | From MI-12 on the way to MINOS. |
| Telecommunications | Telephone Trunk Cable 25Pair, 26 AWG | From MB Detector Bldg. Cable exits this ductbank at Giese Road manhole on the way to Kirk Road Cell Tower. |
| NuMI Fire Protection Connectivity between NuMI Target and MINOS Bldgs | Qty 1 – Four Twisted Pairs, 16 or 18 AWG | From MI-10 on the way to MINOS. Part of the connection path. |
| CATV | Qty Unknown of 1/2” 75 Ohm Hardline Coax Cable. | At least 1 cable will be needed if connection to 8GeV A System is desired. |

Lederman Education Center to MiniBooNE Detector Building	~1,500 ft

| Utility | Type of Cable | Comments |
| --- | --- | --- |
| FIRUS | 3 – 1/2” 75 Ohm Hardline, Coax Cable. | FIRUS already at Lederman Education Center. The FIRUS Mini is located in the utility closet near the center of the building. |
| CATV | 3 – 1/2” 75 Ohm Hardline, Coax Cable. | SWYD & 8GeV Systems already at Lederman Education Center. SWYD A System, SWYD or 8GeV B System, and 1 Spare. |
| Telecommunications | Telephone Trunk Cable 100 Pair, 26 AWG | A spare 100 pairs connected to Tel-Switch room inside WH are available in existing manhole CM-LEC-1 by Lederman Education Center. Splice at CM-LEC-1 to support MiniBooNE Detector, MINOS, and Kirk Cell Tower. |
| Computing Data-Communications | ~7/8” OD ABF Air Duct with 7 Interior Cells, each with 8mm ID to Accommodate Blow In Fiber Will contain 12 Singlemode Fibers. 6 Each for MiniBooNE and MINOS. | Will Connect at New Handhole by CM-LEC-1 with 7 Cell ABF to WH. 2 Cell ABF from CM-LEC-1 to Lederman Education Center. Supports Required Connectivity to Feynman for MB Detector, MI-12, and MINOS |

# Duct Bank Between NuMI Target and MI-10 Service Buildings	~2,500 ft Max

| Utility | Type of Cable | Comments |
| --- | --- | --- |
| NuMI Fire Protection Connectivity between NuMITarget Bldg and MINOS Bldg | Qty 1 – Four Twisted Pairs, 16 or 18 AWG | Part of the connection path. |

MiniBooNE Detector Building to MINOS Service Building	~1,775 ft

| Utility | Type of Cable | Comments |
| --- | --- | --- |
| Accelerator Computer Network | Fiber Optic Trunk 24 Singlemode Fibers | Sourced from MB Detector Bldg. Supports desired connectivity to Feynman. |
| Main Injector CAMAC Link Tevatron Clock (TCLK) Main Inj Beam Sync (MIBS) Machine Data (MDAT) NuMI Beam Permit DDC Utility Monitor System | Fiber Optic Trunk 36 Multimode Fibers | Sourced from MB Detector Bldg. |
| Innerduct for Above Fiber Trunk Cables | 1.25” ID Plastic Innerduct with Pull Rope | One is Enough Here. But May Want to Pull a Spare Between Building and Exterior CMH-MN-3 |
| Safety Interlock | Qty 2 – 20 Conductor 18 AWG Cable | Sourced from MI-10 and via MI-12 and MD Detector Bldg. |
| Safety Data Links and Audio Warning | Qty 2 - Four Twisted Pairs, 18 AWG | Sourced from MI-10 and via MI-12 and MD Detector Bldg. |
| FIRUS | Qty 3 – 1/2” 75 Ohm Hardline Coax Cable. | Sourced from MB Detector Bldg. |
| CATV | Qty 3 – 1/2” 75 Ohm Hardline Coax Cable. | SWYD A System, a B System for Cameras, and a Spare. These are Minimum Requirements. Sourced from MB Detector Bldg. |
| Telecommunications | Telephone Trunk Cable 100 Pair, 26 AWG | Sourced from MB Detector Bldg. |
| NuMI Fire Protection Connectivity between NuMITarget and MINOS Bldgs | Qty 1 – Four Twisted Pairs, 16 or 18 AWG | Passes through MI-8, MI-10, MI-12, and MB Detector Bldg on the way to MINOS. |

Required at NuMI Target Building 	Exact Routing Partially Undefined

| Utility | Type of Cable | Comments |
| --- | --- | --- |
| Accelerator Computer Network | Fiber Optic Trunk 24 Singlemode Fibers | Sourced from MI-62 |
| Main Injector CAMAC Link Tevatron Clock (TCLK) Main Inj Beam Sync (MIBS) Machine Data (MDAT) NuMI Beam Permit DDC Utility Monitor System | Fiber Optic Trunk 36 Multimode Fibers | Sourced from MI-62 |
| Innerduct for Above Fiber Trunk Cables | 1.25” ID Plastic Innerduct with Pull Rope | One is Enough Here. |
| Safety Interlock | Qty 2 – 20 Conductor 18 AWG Cable | Sourced from MI-62 |
| Safety Data Links and Audio Warning | Qty 2 - Four Twisted Pairs, 18 AWG | Sourced from MI-62 |
| FIRUS | Qty 3 – 1/2” 75 Ohm Hardline Coax Cable. | Sourced from MI-62 or MI-8 |
| CATV | Qty 3 – 1/2” 75 Ohm Hardline Coax Cable. | Sourced from MI-62 or MI-8 |
| Telecommunications | Telephone Trunk Cable 50 or 100 Pair, 24 AWG | Sourced from MI-62 or MI-8 |
| NuMI Fire Protection Connectivity between NuMITarget and MINOS Bldgs | Qty 1 – Four Twisted Pairs, 16 or 18 AWG | Passes by or thru MI-8, MI-10, MI-12, and MB Detector Bldg on the way to MINOS. |

Stated distances are subject to refinement and do not necessarily include excess for interior building routing.

Distribution:

Aesook Byon-Wagner 220

Bruce Baller 220

John Anderson 371

Ron Cudzewicz 369

Fernanda Garcia 122

Tim Gierhart 360

Terry Hendricks 307

Carolyn Hines 228

Larry Jackson 108

Cat James 220

Dave Pushka 220

Tom Lackowski 214

Jeff Sims 214

Al Legan 307

Bill Marsh 360

Jim Niehoff 214

Dan Stenman 360

Al Thomas 368

Greg Vogel 307