Here is the text from the document I have that was published on the web at http://www.rhic.bnl.gov/phenix/project_info/safety/publish-info/Electrical_review.htm.  I have not been able to locate this since I printed it out! I printed it 2/6/98 and it was dated 11/9/97.

The title was "Electrical Design Safety Concerns"

Anything that is specifically listed as approved for your particular application in the RHIC SEAPPM 1.5.0.1 is ok.

All potentially combustible parts might fuel a fire. You need to tell the committee what your circuit boards, etc. are made of (provide MSDSs for the fire protection engineer). Choice of cabling (including fiber optic cabling) is an area of concern. You will need to specify, preferably in advance of a review, how much cable you will be using, will it be in cable tray or conduit or raceway, horizontal, vertical, what is its NEC flammability rating and/or its UL code.  It is your responsibility to obtain the flammability information from the manufacturer.  Cable is not usually "acceptable" or "unacceptable". Rather, it is acceptable under conditions of use and not for others.  The concern is greatest for large quantities of cabling that is bundled together. The hazard is decreased if the cable is in a conduit or raceway rather than a cable tray.  The table listed in the SEAPPM gives uses that are definitely ok.  Unfortunately, they don't apply to some of our cabling. Rules apply to both internal and external cabling.

Note: Much of what we refer to as "cable tray" is not cable tray according to the NEC (National Electrical Code) definition, and the distinction can be important in getting approval for cabling. Cabling running in open trays is supposed to be rated at least CL2.  Even CL2 rating is no guarantee of acceptance.  You need to let the committee review it.  VW1 is not considered acceptable for open trays.  In a raceway. which is closed, or inside a detector, VW1 may be ok. It needs a case by case evaluation.  Cable trays and raceway should be non-combustable. The tray or raceway itself needs UL listing or approval by the committee.

The committee will also need to be sure you do not have exposed components that could be a shock hazard (>10 V AC or > 50 V DC and at least 10 ma or 10 Joules of stored energy) or a flash hazard (low voltage but high current >10 A)

Now, from the RHIC Safety and Environmental Administrative policy and Procedures Manual (SEAPPM) Dated Oct 30, 1996

Temporary Electrical Power and Lighting Wiring (NEC Article 305)

Temporary wiring for experiments, tests, and development work power and lighting cable shall be NM, S, SE, SEO, SJ, SJE, SJO, SJEO, SJOO, SO, SOO, ST, STO, or STOO. It shall be installed for no more than 1 year.

Optical Fiber cables

Shall be permitted to be installed in cable trays. Type OFN or OFC shall be used for general purpose installation (NEC Article 770)

Coaxial and Multiconductor Cables fro Data and Signal

Type CM general purpose communications cables shall be permitted to be installed in cable trays.

High Voltage Coaxial Connectors

Systems up to 5KVDC

The standard coaxial cable connector for use with RG-59B/U, red jacketed, shall be Kings Electronics 1705-01 Plug and 1702-1 jack or equivalent.  BNL Stock # A-69852 and A-69855 respectively.

Red jacketed RG59-B/U coaxial cable is BNL stock # A-30304

Cables Acceptable for use in Cable Trays at BNL  (Condensed from a set of tables)

Power Cable

Single conductor, minimum conductor size is AWG 1/0 (for Equip Grounding Conductor: AWG 4) Type MI, AC, MC or Welding Cable

or the following when marked "for CT use": THW, THHN, THWN, XHHW, RHW, RHH, and Diesel locomotive or Transit cable. UL Standards: UL-44, UL-83 or AAR S-501

Multi-conductor, minimum conductor size is AWG 18, Types TC, NM, NMC, SNM, SE, USE, UF, PLTC and MV.  UL Standard 1277 for TC Cables

Control Cable

Multi-conductor, minimum conductor size is AWG 24, Types TC, PLTC, CM, and MP (Not CMX or MPX).  UL Standard 1277, 13 or 444

Signal Cable

Coaxial, minimum conductor size is AWG 20, Types CM, CL2, CL3, CATV, or PLTC (But not CL2X, CL3X or CATVX), UL Standards 444, 13

Twisted Pair, minimum conductor size is AWG 24, Types CM, PLTC or MP (But not CMX or MPX), UL Standards 444, 13

Multi-Conductor, minimum conductor size is AWG 24, Types TC, PLTC or CM  (But not CMX or MPX), UL Standards 1277, 444, 13

Optical Fiber Cable

Types OFN or OFC