## Instruments
type | tag | tag | Service | range | mfr | model | signal | Maximum pressure | Notes
AE | 36 | Ar | Oxygen Analyzer | 0 - 5000 ppm | Delta F | DF-310 | 4-20 mA | 20 psig
AE | 37 | Ar | Oxygen Analyzer | 0 - 20 ppm | Delta F | DF-560 | 4-20 mA | 20 psig
AE | 52 | HAr | Filter regeneration moisture monitoring (close to exhaust) | -80 to + 20 C | Vaisala | DMT242A | 4-20 mA | 290 psig
AE | 151 | HAr | Filter regeneration moisture monitoring (close to filter) | -60 to + 60 C | Vaisala | DMT242B | 4-20 mA | 290 psig
HTR | 8 | HAr | Purifier regeneration heater | 1000W / 240 VAC | Omega | ???
HTR | 21 | Ar | LAr transfer from detector | 100 W /a20 VAC | Watlow | Firerod
HTR | 22 | Ar | LAr transfer from pbar dewar | 100 W /a20 VAC | Watlow | Firerod
HTR | 55 | HAr | Purifier pre-heater | 150 W / 120 VAC
LT | 2 | N2 | Pbar storage dewar condensor LN2 level | 0-20.5 inches | American Magnetics | Model 286 Controller | 4-20 mA
LT | 5 | Ar | Pbar storage dewar Lar level | 0-63 inches | American Magnetics | Model 286 Controller | 4-20 mA
LT | 10 | N2 | MVE detector dewar condensor LN2 level | 0-20.5 inches | American Magnetics | Model 286 Controller | 4-20 mA
LT | 13 | Ar | MVE detector dewar Lar level | 0-39.62 inches | American Magnetics | Model 286 Controller | 4-20 mA
PI | 4 | Ar | Pbar storage dewar Ar pressure | VAC-0-30 psig | AMETEK | 1535-V-0-30-PSI/KPA-CBM-FVCR-FR | ---
PI | 12 | Ar | MVE detector dewar Ar pressure | VAC-0-30 psig | AMETEK | 1535-V-0-30-PSI/KPA-CBM-FVCR-FR | ---
PI | 38 | Ar | Argon purge dewar supply pressure
PI | 39 | Ar | Argon purge dewar supply regulated pressure
PI | 40 | Ar | Argon purge dewar supply pressure
PI | 41 | Ar | Argon purge dewar supply regulated pressure
PI | 42 | Ar | Argon purge dewar supply regulated pressure
PI | 43 | Ar | Argon purge dewar supply line regulated pressure
PI | 44 | N2 | LN2 transfer line pressure
PI | 45 | H2Ar | H2Ar bottle pressure
PI | 46 | H2Ar | H2Ar regulated pressure
PI | 47 | H2Ar | H2Ar regulated pressure
PI | 48 | H2Ar | H2Ar line pressure
PI | 100 | N2 | LN2 dewar pressure
DPT | 100 | N | Liquid Nitrogen Dewar | 0 - 80" wc | Barton | ITI3 | 4-20 mA
DPT | 67 | Ar | Luke Vapor Pump | 0 - 5 psid | Setra | C239 | 4-20 mA
PT | 1 | N2 | Pbar storage dewar condensor LN2 pressure | 0-50 psig | Setra | C206 | 4-20 mA
PT | 3 | Ar | Pbar storage dewar Ar pressure | 0-50 psia | Setra | GCT-225 (2251-050P-A-D4-11-B1) | 4-20 mA
PT | 9 | N2 | MVE detector dewar condensor LN2 pressure | 0-50 psig | Setra | C206 | 4-20 mA
PT | 11 | Ar | MVE detector dewar Ar pressure | 0-50 psia | Setra | GCT-225 (2251-050P-A-D4-11-B1) | 4-20 mA
PT | 14 | V | Rough Vacuum at pump inlet | 10-4- 760 Torr | Varian (Controller Part# L8350301) | ConvecTorr gauge board (Part# L9887301) | 0 - 7 VDC, 1 V per decade log-linear |  | 37 pin connector, might need cable
PT | 15 | V | LAr transfer line insultating vacuum | 10-4- 1Torr linear & 10-4- 1000 Torr non-linear | Granville-Phillips | 275857-EU | 0-10 VDC
PT | 16 | V | MVE detector dewar insulating vacuum | 10-4- 1Torr linear & 10-4- 1000 Torr non-linear | Granville-Phillips | 275857-EU | 0-10 VDC
PT | 17 | V | Pbar storage dewar insulating vacuum | 10-4- 1Torr linear & 10-4- 1000 Torr non-linear | Granville-Phillips | 275857-EU | 0-10 VDC
PT | 18 | V | Pbar storage dewar Argon volume rough vacuum | 10-4- 760 Torr | Varian (Controller Part# L8350301) | ConvecTorr gauge board (Part# L9887301) | 0 - 7 VDC, 1 V per decade log-linear |  | 37 pin connector, might need cable
PT | 19 | V | MVE detector dewar Argon volume rough vacuum | 10-4- 760 Torr | Varian (Controller Part# L8350301) | ConvecTorr gauge board (Part# L9887301) | 0 - 7 VDC, 1 V per decade log-linear |  | 37 pin connector, might need cable
PT | 27 | N2 | Nitrogen transfer line pressure | 0-100 psig | Setra |  | 0-5 DC
PT | 30 | V | Pbar filter dewar insulating vacuum | 10-4-1Torr linear & 10-4-1000 Torr non-linear | Granville-Phillips | 275857-EU | 0-10 VDC
PT | 31 | V | High Vacuum at pump inlet | 10-11 Torr to 10-3 Torr | Varian (Controller Part# L8350301) | UHV Bayard-Alpter gauge board (Part# L8321301) | 0-10 VDC, 1 V per decade log-linear |  | Needs coaxial cable with microjax plug
PT | 32 | V | Pbar storage dewar Argon volume high vacuum | 10-11 Torr to 10-3 Torr | Varian (Controller Part# L8350301) | UHV Bayard-Alpter gauge board (Part# L8321301) | 0-10 VDC, 1 V per decade log-linear |  | Needs coaxial cable with microjax plug
PT | 33 | V | MVE detector dewar Argon volume high vacuum | 10-11 Torr to 10-3 Torr | Varian (Controller Part# L8350301) | UHV Bayard-Alpter gauge board (Part# L8321301) | 0-10 VDC, 1 V per decade log-linear |  | Needs coaxial cable with microjax plug
PT | 51 | N | LN2 dewar pressure transmitter | 0-100 psig | Setra |  | 0-5 DC
PT | 53 | V | Rough pump inlet pressure | 10-4-1Torr linear & 10-4-1000 Torr non-linear | Granville-Phillips | 275857-EU | 0-10 VDC
PT | 58 | Ar | AE-36-Ar inlet pressure | 0-50 psia | Setra | 2231-050P-A-BA-11-B1-F | 4-20 mA
PT | 59 | Ar | AE-37-Ar inlet pressure | 0-50 psia | Setra | 2231-050P-A-BA-11-B1-F | 4-20 mA
PT | 60 | Ar | Zero gas line pressure after filter | 0-50 psia | Setra | 2231-050P-A-BA-11-B1-F | 4-20 mA
PT | 61 | Ar | Argon purge / analyzer purifying line pressure | 0-50 psia | Setra | 2231-050P-A-BA-11-B1-F | 4-20 mA
PT | 62 | V | AE-37-Ar gas switching manifold vacuum | 10-4-1Torr linear & 10-4-1000 Torr non-linear | Granville-Phillips | 275857-EU | 0-10 VDC
PT | 63 | V | AE-36-Ar gas switching manifold vacuum | 10-4-1Torr linear & 10-4-1000 Torr non-linear | Granville-Phillips | 275857-EU | 0-10 VDC
PT | 64 | Ar | Argon purge / analyzer purifying gas bottle pressure | 0-3000 psia | Setra | 2231-30CP-A-BA-11-Ba-F | 4-20 mA
PT | 65 | Ar | Argon purge / analyzer purifying dewar pressure | 0-500 psia | Setra | 2231-30CP-A-BA-11-Ba-F | 4-20 mA
PT | 66 | Ar | Argon span gas bottle pressure | 0-3000 psia | Setra | 2231-30CP-A-BA-11-Ba-F | 4-20 mA
PT | 68 | V | Luke dewar insulating vacuum | 10-4- 1Torr linear & 10-4- 1000 Torr non-linear | Granville-Phillips | 275857-EU | 0-10 VDC
PT | 69 | V | Luke seal monitoring | 10-4- 1Torr linear & 10-4- 1000 Torr non-linear | Granville-Phillips | 275857-EU | 0-10 VDC
PT | 70 | V | Seal pump inlet vacuum | 10-4-1Torr linear & 10-4-1000 Torr non-linear | Granville-Phillips | 275857-EU | 0-10 VDC
PT | 71 | V | Seal monitor vacuum | 10-4-1Torr linear & 10-4-1000 Torr non-linear | Granville-Phillips | 275857-EU | 0-10 VDC
PT | 399 | N2 | Nitrogen gas bottle pressure for pneumatic valves | 0-3000 psia | Setra | 2231-30CP-A-BA-11-Ba-F | 4-20 mA
TE | 6 | N2 | LN2 transfer line cooldown temperature | 70-400K | Omega | Platinum RTD (PR-19-2-100-1/8-6-E) | 100 ohm
TE | 7 | Ar | Purifier internal temperature |  | Minco | 100 ohm platinum RTD (Part # S201PD) | 100 ohm
TE | 23 | Ar | HTR-21-Ar internal temperature (read out) |  | Watlow | Type K thermocouple
TE | 24 | Ar | HTR-21-Ar internal temperature (interlock) |  | Watlow | Type K thermocouple
TE | 25 | Ar | HTR-22-Ar internal temperature (read out) |  | Watlow | Type K thermocouple
TE | 26 | Ar | HTR-22-Ar internal temperature (interlock) |  | Watlow | Type K thermocouple
TE | 54 | Ar | Purifier internal temperature (read out) |  | Minco | 100 ohm platinum RTD (Part # S201PD)
TE | 56 | Ar | Regeneration pre-heater temperature (read out) |  | Minco | 100 ohm platinum RTD (Part # S201PD)
TE | 57 | Ar | Regeneration pre-heater temperature (interlock) |  | Minco | 100 ohm platinum RTD (Part # S201PD)
EV | 104 | N2 | LN2 transfer line into Pbar condensor | 40 psig max differential | Asco | 8263G209LT (120 VAC) (normally closed) | 120 VAC
EV | 105 | N2 | LN2 transfer line into MVE condensor | 40 psig max differential | Asco | 8263G209LT (120 VAC) (normally closed) | 120 VAC
EV | 106 | N2 | LN2 transfer line vent | 40 psig max differential | Asco | 8263G209LT (120 VAC) (normally closed) | 120 VAC
EV | 268 | Ar | Luke Vapor pump | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed)
EV | 270 | N2 | EP-205-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 271 | N2 | EP-206-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 272 | N2 | EP-251-V actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 273 | N2 | EP-252-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 274 | N2 | EP-253-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 275 | N2 | EP-254-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 276 | N2 | EP-255-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 277 | N2 | EP-256-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 278 | N2 | EP-257-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 279 | N2 | EP-258-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 280 | N2 | EP-259-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 281 | N2 | EP-260-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 282 | N2 | EP-261-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 283 | N2 | EP-262-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 284 | N2 | EP-263-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 285 | N2 | EP-266-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 286 | N2 | EP-267-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 287 | N2 | EP-265-V actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 292 | N2 | EP-290-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 293 | N2 | EP-291-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 395 | N2 | EP-396-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EV | 397 | N2 | EP-398-Ar actuation | 200 psig max differential | Asco | 8320G132 (24 VDC) (normally closed) | 24 VDC
EP | 205 | Ar | MVE detector dewar Ar vent | Normally Closed - 100 psig actuation pressure | Swagelock | SS-6UW-V19-TF-6C |  | 2500 psig
EP | 206 | Ar | Pbar detector dewar Ar vent | Normally Closed - 100 psig actuation pressure | Swagelock | SS-6UW-V19-TF-6C |  | 2500 psig
EP | 251 | V | AE-37-Ar switching manifold vacuum isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 252 | Ar | AE-37-Ar switching manifold sample isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 253 | Ar | AE-37-Ar switching manifold MVE dewar sample isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 254 | Ar | AE-37-Ar switching manifold pbar dewar sample isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 255 | Ar | AE-37-Ar switching manifold isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 256 | Ar | AE-37-Ar switching manifold zero gas sample isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 257 | Ar | AE-37-Ar switching manifold vacuum measurement isolation | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 258 | Ar | AE-36-Ar switching manifold sample isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 259 | Ar | AE-36-Ar switching manifold pbar dewar sample isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 260 | Ar | AE-36-Ar switching manifold MVE dewar sample isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 261 | Ar | AE-36-Ar switching manifold sample isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 262 | Ar | AE-36-Ar switching manifold isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 263 | Ar | AE-37-Ar switching manifold vacuum measurement isolation | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 265 | V | Gas sample manifold vacuump pump isolation | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 266 | Ar | AE-36-Ar switching manifold zero gas sample isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 267 | Ar | Purge panel isolation valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 290 | Ar | P-bar dewar gas sample valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 291 | Ar | MVE dewar gas sample valve | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 396 | Ar | AE-36-Ar N2 purge | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
EP | 398 | Ar | AE-37-Ar N2 purge | Normally Closed - 75 psig actuation pressure | Parker | 930-AOPLPNC-S-TS |  | 125 psig
125 psig
CV | 90 | N | LN2 dewar fill line check valve
CV | 214 | Ar | Air contamination prevention during Ar purge dewar change | 1 psig setpoint (cryo)
CV | 217 | Ar | Argon purge dewar supply | 1 psig setpoint
CV | 218 | Ar | Argon purge dewar supply | 1 psig setpoint
CV | 223 | Ar | Air contamination prevention during Ar purge dewar change | 1 psig setpoint (cryo)
CV | 225 | Ar | Filter check valve
CV | 226 | Ar | Filter check valve
CV | 138 | N2 | Air contamination prevention in MVE Ar condensor N2 vent
CV | 139 | N2 | Air contamination prevention in Pbar Ar condensor N2 vent
CV | 150 | N2 | LN2 transfer line vent air contamination prevention
CV | 100 | N2 | LN2 dewar liquid use line
CV | 107 | N2 | 1000 Liter LN2 dewar supply check valve
CV | 108 | N2 | 160 L LN2 dewars supply check valve
CV | 109 | N2 | Air contamination prevention during 160 L LAr dewar change
CV | 110 | N2 | Air contamination prevention during 160 L LAr dewar change
CV | 247 | Ar | Ar supply for filter regeneration check valve
CV | 410 | H2Ar | H2Ar bottle pigtail contamination prevention
CV | 401 | H2Ar | H2Ar supply check valve
MV | 80 | N | LN2 dewar pressure gauge isolation
MV | 85 | N | LN2 dewar vapor line pressure sensing isolation
MV | 86 | N | LN2 dewar level gauge equalization
MV | 87 | N | LN2 dewar liquid line pressure sensing isolation
MV | 88 | N | LN2 dewar pressure building regulator isolation
MV | 89 | N | LN2 dewar pressure building loop isolation
MV | 90 | V | LN2 dewar vacuum pump out
MV | 90 | N | LN2 dewar pressure relieving regulator isolation
MV | 91 | V | LN2 dewar vacuum readout isolation
MV | 91 | N | LN2 dewar fill line drain valve
MV | 92 | N | LN2 dewar fill line isolation
MV | 93 | N | LN2 dewar vapor vent
MV | 94 | N | LN2 dewar full trycock
MV | 95 | N | LN2 dewar pressure building loop bypass
MV | 96 | N | LN2 dewar pressure building regulator isolation
MV | 97 | N | LN2 dewar liquid withdrawal
MV | 98 | N | LN2 dewar relief valve selector
MV | 99 | N | LN2 dewar vapor vent valve
MV | 100 | N | LN2 dewar liquid use isolation
MV | 101 | N | LN2 dewar vapor vent valve
MV | 111 | N2 | 160 L LN2 dewar vent valve
MV | 112 | N2 | 160 L LN2 dewar vent valve
MV | 113 | N2 | 160 L LN2 dewar isolation valve
MV | 114 | N2 | 160 L LN2 dewar isolation valve
MV | 119 | N | LN2 liquid transfer line branch isolation
MV | 120 | N | LN2 liquid transfer line test cryostat branch isolation
MV | 121 | N | LN2 dewar pressure transmitter isolation valve
MV | 202 | Ar | Filter assembly inlet isolation |  | Swagelock | SS-4BG-V51 | --- | 1000 psig max at - 20 F
MV | 208 | Ar | Filter assembly inlet isolation |  | Swagelock | SS-4BG-V51 | --- | 1000 psig max at - 20 F
MV | 203 | Ar | LAr fill line isolation |  | Swagelock | SS-6UW-Y38-T2-TF-SE8 | --- | 2500 psig max
MV | 204 | Ar | LAr fill line vent |  | Swagelock | SS-6UW-Y38-T2-TF-SE8 | --- | 2500 psig max
MV | 211 | Ar | Isolation valve for argon purge of EP-205-Ar
MV | 212 | Ar | Isolation valve for argon purge of EP-205-Ar
MV | 213 | Ar | Isolation valve for O2 monitor
MV | 215 | Ar | Isolation valve for argon purge dewar changing
MV | 216 | Ar | Isolation valve to allow argon purge venting after dewar change
MV | 219 | Ar | Isolation valve to allow argon purge venting after dewar change
MV | 220 | Ar | Argon purge dewar vent for dewar change
MV | 221 | Ar | Argon purge dewar vent for dewar change
MV | 222 | Ar | Isolation valve for Ar purge dewar changing
MV | 223 | Ar | Isolation valve for Ar purge flowmeter
MV | 224 | Ar | Isolation valve for Ar purge flowmeter
MV | 225 | Ar | Isolation valve for Ar purge flowmeter
MV | 226 | Ar | Isolation valve for Ar purge flowmeter
MV | 227 | Ar | Isolation valve for Ar purge flowmeter
MV | 228 | Ar | Isolation valve for Ar purge flowmeter
MV | 244 | Ar | MVE dewar cryo isolation valve |  | Selfa | SUPRA8-I/K-VCR3/8-BV-Pass04-PP BWO1/4
MV | 245 | Ar | Pbar dewar cryo isolation valve |  | Selfa | SUPRA8-I/K-VCR3/8-BV-Pass04-PP BWO1/4
MV | 248 | Ar | Ar supply for filter regeneration check valve
MV | 361 | V | Pbar dewar vacuum isolation valve
MV | 362 | V | LAr transfer line insulating vacuum isolation valve
MV | 364 | V | Vacuum isolation valve
MV | 405 | H2Ar | H2Ar bottle isolation
PCV | 235 | Ar | Argon purge dewar gas supply regulator
PCV | 236 | Ar | Argon purge dewar gas supply regulator
PCV | 237 | Ar | Argon purge dewar gas supply line regulator
PCV | 406 | H2Ar | H2Ar bottle regulator
PCV | 451 | H2Ar | H2Ar line regulator
FI | 229 | Ar | Ar purge flowmeter
FI | 230 | Ar | Ar purge flowmeter
FI | 231 | Ar | Ar purge flowmeter
FI | 232 | Ar | Ar purge flowmeter
FI | 233 | Ar | Ar purge flowmeter
FI | 234 | Ar | Ar purge flowmeter
FI | 452 | H2Ar | H2Ar regeneration flowmeter
MV | 360 | V | MVE dewar LAr volume vacuum isolation
MV | 361 | V | Pbar dewar LAr volume vacuum isolation
MV | 362 | V | LAr transfer line insultating vacuum
MV | 363 | V | Vacuum isolation valve
MV | 364 | V | Pbar dewar 2 vacuum isolation
MV | 365 | V | LAr transfer line vacuum isolation
MV | 366 | V | LAr transfer line vacuum isolation
MV | 480 | H2Ar | Filter regeneration isolation valve
MV | 481 | H2Ar | Filter regeneration isolation valve
MV | 403 | H2Ar | H2Ar vent valve
MV | 402 | H2Ar | H2Ar isolation valve
PSV | 101 | N2 | LN2 transfer line trapped volume relief
PSV | 115 | N2 | 160 L LN2 dewar trapped volume relief
PSV | 116 | N2 | 160 L LN2 dewar trapped volume relief
PSV | 117 | N2 | LN2 transfer line trapped volume relief
PSV | 118 | N2 | LN2 transfer line trapped volume relief
PSV | 201 | Ar | Pbar storage dewar LAr volume pressure relief | 22 psig set point | Anderson Greenwood | 83S68-6
PSV | 203 | Ar | LAr filtration assembly trapped volume relief
PSV | 210 | Ar | MVE detector dewar LAr volume pressure relief | 22 psig set point | Anderson Greenwood | 81S88-8
PSV | 241 | Ar | Ar purge regulator failure supply relief
PSV | 242 | Ar | Ar purge regulator failure supply relief
PSV | 243 | Ar | LAr filtration assembly trapped volume relief
PSV | 246 | Ar | LAr fill trapped volume relief
PSV | 249 | Ar | LAr transfer line trapped volume relief
PSV | 250 | Ar | LAr transfer line trapped volume relief
PSV | 344 | V | LAr transfer line vacuum relief |  | Fermilab
PSV | 345 | V | MVE dewar LAr condensor vacuum relief
PSV | 346 | V | Pbar dewar LAr condensor vacuum relief
PSV | 347 | V | Pbar dewar vacuum relief
PSV | 348 | V | MVE dewar vacuum relief
PSV | 404 | H2Ar | H2Ar regulator failure relief valve
PE | 91 | V
RD | 99 | N | LN2 dewar rupture disk
RD | 100 | N | LN2 dewar rupture disk
RD | 303 | V | Pbar storage dewar LAr volume pressure relief | 55 psig set point | BS&B | JRS
RD | 301 | V | Pbar filtering dewar LAr volume pressure relief
RD | 302 | V | MVE detector dewar LAr volume pressure relief | 55 psig set point | BS&B | JRS
RV | 90 | N | LN2 dewar pressure relieving regulator
S | 91 | N
SV | 90 | N | LN2 dewar fill line trapped volume relief
SV | 90 | V | LN2 dewar vacuum jacket relief
SV | 96 | N | LN2 dewar pressure building loop trapped volume relief
SV | 97 | N | LN2 dewar pressure building loop trapped volume relief
SV | 98 | N | LN2 dewar pressure building loop trapped volume relief
SV | 99 | N | LN2 dewar relief valve
SV | 100 | N | LN2 dewar relief valve

## PLC Modules
Current
Needed
Model# | Description | Lab F Sys | On-Hand | Total Needed | Channels | Unused CH's | Buy | Cost | Total Cost
BC9000 | Processor | 1 |  | 1 |  |  | 0 |  | 0 | 304 | stock
KL3064 | 4 ch Analog In (0-10VDC) | 0 | 1 | 1 | 15 | 0 | 1 | 203 | 203 | 203 | stock
KL3042 | 2 ch Analog In (0-20mA) | 4 | 0 | 3 | 12 | 2 | 0 | 160 | 0 | 160 | stock
KL3202 | 2 ch RTD input | 0 | 4 | 2 | 2 | 2 | 1 | 193 | 193 | 193 | stock
KL4414 | 4 ch Analog Out (0-20 mA) | 0 | 3 | 1 | 6 | 3 | 0 | 158 | 0 | 158 | 2wk
KL1114 | 4 ch Discrete In (24VDC) | 1 | 6 | 1 | ? | 4 | 0 | 28.2 | 0 | 28.2 | stock
KL2602 | 2 ch Realy Out (5A) | 1 | 6 | 5 | 7 | 5 | 4 | 43.6 | 174.4 | 43.6 | stock
KL9190 | Arbitrary Power Feed | 0 | 0 | 2 |  | 0 | 3 | 15.3 | 45.9 | 15.3 | stock
KL9010 | End Terminal | 1 | 6 | 1 |  | 0 | 0 | 11.4 | 0 | 11.4 | stock
Thermocouple
KL3062 | 2 ch Analog Input (0-10VDC) | 1 | [7 empty] | 160 | stock
| OPC | 0 | 0 | 1 |  |  | 1 | 680 | 680 | 680 | stock
1296.3

## Input_Output
FLARE INSTRUMENTATION LIST
[5 empty] | Device Tag |  |  | Description | EU Range | Signal Range | Manufacturer | Model | Beckhoff Variable | iFIX VARIABLE
27 |  |  |  |  | Discrete Output
[5 empty] | EV | 103 | N2 | Spare | ON/OFF | 110 VAC | Asco | 8263G209LT (normally closed)
[5 empty] | EV | 104 | N2 | LN2 transfer line into Pbar condensor | ON/OFF | 110 VAC | Asco | 8263G209LT (normally closed)
[5 empty] | EV | 105 | N2 | LN2 transfer line into MVE condensor | ON/OFF | 110 VAC | Asco | 8263G209LT (normally closed)
[5 empty] | EV | 106 | N2 | LN2 transfer line vent | ON/OFF | 110 VAC | Asco | 8263G209LT (normally closed)
[5 empty] | EV | 110 | N2 | Spare | ON/OFF | 110 VAC | Asco | 8263G209LT (normally closed)
[5 empty] | EV | 270 | N2 | EP-205-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 271 | N2 | EP-206-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 272 | N2 | EP-251-V actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 273 | N2 | EP-252-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 274 | N2 | EP-253-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 275 | N2 | EP-254-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 276 | N2 | EP-255-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 277 | N2 | EP-256-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 278 | N2 | EP-257-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 279 | N2 | EP-258-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 280 | N2 | EP-259-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 281 | N2 | EP-260-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 282 | N2 | EP-261-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 283 | N2 | EP-262-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 284 | N2 | EP-263-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 285 | N2 | EP-266-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 286 | N2 | EP-267-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 287 | N2 | EP-265-V actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 292 | N2 | EP-290-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 293 | N2 | EP-291-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 395 | N2 | EP-396-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
[5 empty] | EV | 397 | N2 | EP-398-Ar actuation | ON/OFF | 24 VDC | Asco | 8320G132 (normally closed)
| 0 |  |  |  | Discrete Input
|  | 44 |  |  | Analog Input
[5 empty] | AE | 36 | Ar | Oxygen Analyzer | 0 - 5000 ppm | 4-20 mA | Delta F | DF-310
[5 empty] | AE | 37 | Ar | Oxygen Analyzer | 0 - 20 ppm | 4-20 mA | Delta F | DF-560
[5 empty] | AE | 52 | HAr | Filter regeneration moisture monitoring | -80 to + 20 C | 4-20 mA | Vaisala | DMT242A
[5 empty] | LT | 2 | N2 | Pbar storage dewar condensor LN2 level | 0-20.5 inches | 4-20 mA | American Magnetics | Model 286 Controller
[5 empty] | LT | 5 | Ar | Pbar storage dewar Lar level | 0-63 inches | 4-20 mA | American Magnetics | Model 286 Controller
[5 empty] | LT | 10 | N2 | MVE detector dewar condensor LN2 level | 0-20.5 inches | 4-20 mA | American Magnetics | Model 286 Controller
[5 empty] | LT | 13 | Ar | MVE detector dewar Lar level | 0-39.62 inches | 4-20 mA | American Magnetics | Model 286 Controller
[5 empty] | DPT | 100 | N | Liquid Nitrogen Dewar | 0 - 80" wc | 4-20 mA | Barton | ITI3
[5 empty] | PT | 1 | N2 | Pbar storage dewar condensor LN2 pressure | 0-50 psig | 4-20 mA | Setra | C206
[5 empty] | PT | 3 | Ar | Pbar storage dewar Ar pressure | 0-50 psia | 4-20 mA | Setra | GCT-225 (2251-050P-A-D4-11-B1)
[5 empty] | PT | 9 | N2 | MVE detector dewar condensor LN2 pressure | 0-50 psig | 4-20 mA | Setra | C206
[5 empty] | PT | 11 | Ar | MVE detector dewar Ar pressure | 0-50 psia | 4-20 mA | Setra | GCT-225 (2251-050P-A-D4-11-B1)
[5 empty] | PT | 14 | V | Rough Vacuum at pump inlet | 10-4- 760 Torr | 0 - 7 VDC, 1 V per decade log-linear | Varian (Controller Part# L8350301) | ConvecTorr gauge board (Part# L9887301)
[5 empty] | PT | 15 | V | LAr transfer line insultating vacuum | 10-4- 1Torr linear & 10-4- 1000 Torr non-linear | 0-10 VDC | Granville-Phillips | 275857-EU
[5 empty] | PT | 16 | V | MVE detector dewar insulating vacuum | 10-4- 1Torr linear & 10-4- 1000 Torr non-linear | 0-10 VDC | Granville-Phillips | 275857-EU
[5 empty] | PT | 17 | V | Pbar storage dewar insulating vacuum | 10-4- 1Torr linear & 10-4- 1000 Torr non-linear | 0-10 VDC | Granville-Phillips | 275857-EU
[5 empty] | PT | 18 | V | Pbar storage dewar Argon volume rough vacuum | 10-4- 760 Torr | 0 - 7 VDC, 1 V per decade log-linear | Varian (Controller Part# L8350301) | ConvecTorr gauge board (Part# L9887301)
[5 empty] | PT | 19 | V | MVE detector dewar Argon volume rough vacuum | 10-4- 760 Torr | 0 - 7 VDC, 1 V per decade log-linear | Varian (Controller Part# L8350301) | ConvecTorr gauge board (Part# L9887301)
[5 empty] | PT | 27 | N2 | Nitrogen transfer line pressure | 0 - 100 psig | 0 - 5 VDC | Setra
[5 empty] | PT | 30 | V | Pbar filter dewar insulating vacuum | 10-4-1Torr linear & 10-4-1000 Torr non-linear | 0-10 VDC | Granville-Phillips | 275857-EU
[5 empty] | PT | 31 | V | High Vacuum at pump inlet | 10-11 Torr to 10-3 Torr | 0-10 VDC, 1 V per decade log-linear | Varian (Controller Part# L8350301) | UHV Bayard-Alpter gauge board (Part# L8321301)
[5 empty] | PT | 32 | V | Pbar storage dewar Argon volume high vacuum | 10-11 Torr to 10-3 Torr | 0-10 VDC, 1 V per decade log-linear | Varian (Controller Part# L8350301) | UHV Bayard-Alpter gauge board (Part# L8321301)
[5 empty] | PT | 33 | V | MVE detector dewar Argon volume high vacuum | 10-11 Torr to 10-3 Torr | 0-10 VDC, 1 V per decade log-linear | Varian (Controller Part# L8350301) | UHV Bayard-Alpter gauge board (Part# L8321301)
[5 empty] | PT | 51 | N | LN2 dewar pressure transmitter | 0-100 psig | 0-5 VDC | Setra
[5 empty] | PT | 53 | V | Rough pump inlet pressure | 10-4-1Torr linear & 10-4-1000 Torr non-linear | 0-10 VDC | Granville-Phillips | 275857-EU
[5 empty] | PT | 58 | Ar | AE-36-Ar inlet pressure | 0-50 psia | 4-20 mA | Setra | 2231-050P-A-BA-11-B1-F
[5 empty] | PT | 59 | Ar | AE-37-Ar inlet pressure | 0-50 psia | 4-20 mA | Setra | 2231-050P-A-BA-11-B1-F
[5 empty] | PT | 60 | Ar | Zero gas line pressure after filter | 0-50 psia | 4-20 mA | Setra | 2231-050P-A-BA-11-B1-F
[5 empty] | PT | 61 | Ar | Argon purge / analyzer purifying line pressure | 0-50 psia | 4-20 mA | Setra | 2231-050P-A-BA-11-B1-F
[5 empty] | PT | 62 | V | AE-37-Ar gas switching manifold vacuum | 10-4-1Torr linear & 10-4-1000 Torr non-linear | 0-10 VDC | Granville-Phillips | 275857-EU
[5 empty] | PT | 63 | V | AE-36-Ar gas switching manifold vacuum | 10-4-1Torr linear & 10-4-1000 Torr non-linear | 0-10 VDC | Granville-Phillips | 275857-EU
[5 empty] | PT | 64 | Ar | Argon purge / analyzer purifying gas bottle pressure | 0-3000 psia | 4-20 mA | Setra | 2231-30CP-A-BA-11-Ba-F
[5 empty] | PT | 65 | Ar | Argon purge / analyzer purifying dewar pressure | 0-500 psia | 4-20 mA | Setra | 2231-30CP-A-BA-11-Ba-F
[5 empty] | PT | 66 | Ar | Argon span gas bottle pressure | 0-3000 psia | 4-20 mA | Setra | 2231-30CP-A-BA-11-Ba-F
[5 empty] | PT | 70 | V | Seal pump inlet vacuum | 10-4-1Torr linear & 10-4-1000 Torr non-linear | 0-10 VDC | Granville-Phillips | 275857-EU
[5 empty] | PT | 71 | V | Seal monitor vacuum | 10-4-1Torr linear & 10-4-1000 Torr non-linear | 0-10 VDC | Granville-Phillips | 275857-EU
[5 empty] | PT | 399 | N2 | Nitrogen gas bottle pressure for pneumatic valves | 0-3000 psia | 4-20 mA | Setra | 2231-30CP-A-BA-11-Ba-F
[5 empty] | TE | 6 | N2 | LN2 transfer line cooldown temperature | 70-400K | 100 ohm | Omega | Platinum RTD (PR-19-2-100-1/8-6-E)
[5 empty] | TE | 7 | Ar | Purifier internal temperature (interlock) | 70-700K | 100 ohm | Minco | 100 ohm platinum RTD (Part # S201PD)
[5 empty] | TE | 23 | Ar | HTR-21-Ar internal temperature (read out) | 70-400K | Type K | Watlow | Type K thermocouple
[5 empty] | TE | 24 | Ar | HTR-21-Ar internal temperature (interlock) | 70-400K | Type K | Watlow | Type K thermocouple
[5 empty] | TE | 25 | Ar | HTR-22-Ar internal temperature (read out) | 70-400K | Type K | Watlow | Type K thermocouple
[5 empty] | TE | 26 | Ar | HTR-22-Ar internal temperature (interlock) | 70-400K | Type K | Watlow | Type K thermocouple
[5 empty] | TE | 29 | Ar | O2 monitor outlet temperature | 70-400K | 100 ohm | Minco | 100 ohm platinum RTD (Part # S201PD)
[5 empty] | TE | 54 | Ar | Purifier internal temperature (read out) | 70-700K | 100 ohm | Minco | 100 ohm platinum RTD (Part # S201PD)
[5 empty] | TE | 56 | Ar | Regeneration pre-heater temperature (interlock) | 70-700K | 100 ohm | Minco | 100 ohm platinum RTD (Part # S201PD)
[5 empty] | TE | 57 | Ar | Regeneration pre-heater temperature (interlock) | 70-700K | 100 ohm | Minco | 100 ohm platinum RTD (Part # S201PD)
|  |  | 4 |  | Analog Output
[5 empty] | HTR | 8 | HAr | Purifier regeneration heater | 1000W | 220 VAC | Omega
[5 empty] | HTR | 21 | Ar | LAr transfer from detector | 100 W | 110 VAC
[5 empty] | HTR | 22 | Ar | LAr transfer from pbar dewar | 100 W | 110 VAC
[5 empty] | HTR | 55 | HAr | Purifier pre-heater | 150 W | 110 VAC
27 | 0 | 44 | 4
Discrete Output | Discrete Input | Analog Input | Analog Output
|  |  | i/o channels needed | i/o channels ordered
|  | Disc Out | 27 | 10
|  | 4-20 mA | 20 | 14
|  | 0 - 10 V | 17 | 24
|  | RTD | 6 | 6
|  | Type K | 4 | 12