Technology Costing Modules Applied to Model Facilities

EPA developed the following costing modules for assessing model-facility compliance costs for the Notice of Data Availability (NODA):

- Fish handling and return system (impingement only)

- Fine mesh traveling screens with fish handling and return (impingement & entrainment)

- New larger intake structure with fine mesh, handling and return (impingement & entrainment)

- Passive fine mesh screens at shoreline (impingement & entrainment)

- Fish barrier net (impingement only)

- Gunderboom (impingement & entrainment)

- Relocate intake to submerged offshore with passive fine mesh screen (impingement & entrainment)

- Velocity cap at inlet of offshore submerged (impingement only)

- Passive fine mesh screen at inlet of offshore submerged (impingement & entrainment)

- Add/modify shoreline tech for submerged offshore (impingement only or I&E)

- Add double-entry, single-exit with fine mesh and fish handling and return (impingement & entrainment)

The derivation and background for each of these technology modules is presented in public record under the item titled, “316(b) Phase II NODA Cost Modules.”

For the main NODA option, each model facility had three potential compliance actions: (1) no impingement and entrainment controls, (2) impingement controls only, or (3) impingement controls plus entrainment controls.  A facility qualifies for compliance action (1) if it has recirculating cooling systems in place.  Figures 1 and 2 at the end of this document provide a decision tree for assigning compliance actions (2) and (3) to the in-scope Phase II model facilities.  The following files included in the public record present a roadmap of technology upgrades for those facilities and intakes receiving compliance actions (2) and (3):

- 316b_Phase2_DQ_MainOpt_Estuary.xls (compliance actions for estuarine and tidal river facilities responding to the detailed questionnaire)

- 316b_Phase2_DQ_MainOpt_FreshRiver.xls (compliance actions for freshwater river and stream facilities responding to the detailed questionnaire)

- 316b_Phase2_DQ_MainOpt_Lake_Ocean_GL.xls (compliance actions for freshwater lake and reservoir, Great Lake, and ocean facilities responding to the detailed questionnaire)

- 316b_Phase2_STQ_MainOpt_Estuary.xls (compliance actions for estuarine and tidal river facilities responding to the short-technical questionnaire)

- 316b_Phase2_STQ_MainOpt_ FreshRiver.xls (compliance actions for freshwater river and stream facilities responding to the short-technical questionnaire)

- 316b_Phase2_STQ_MainOpt_Estuary.xls (compliance actions for freshwater lake and reservoir, Great Lake, and ocean facilities responding to the short-tech. questionnaire)

Of the modules listed above, numbers 1, 5, 8, and in some cases 10 are dedicated to impingement controls alone.  The Agency generally applied the remainder of the technology modules (including number 10 in some instances) for cases where the model facility received entrainment and impingement requirements.

In the cases that a facility had a functional impingement control system at baseline and was deemed to require upgrades to entrainment controls, the Agency generally assigned costs to the model facility to upgrade the existing impingement controls in addition to the entrainment upgrade.  The Agency learned through its research subsequent to the February 2002 proposal that in most cases when upgrading a technology for entrainment controls, the effort and cost of replacing the attached impingement controls generally compared with the effort and cost to retain and reuse the existing impingement controls (for more details, see the traveling screen technology module documentation).  The Agency assigned entrainment only (with no additional impingement upgrade costs) requirements to a few unique situations for the main option in the NODA.  This included the case of a low-velocity, double-entry, single-exit screening system operating in-place at baseline.  The Agency assigned only the costs associated with adding fine-mesh overlays for this system because the model facility had additional, redundant impingement technologies in-place.  In addition, those facilities with barrier net systems in-place that required entrainment upgrades received only the entrainment system costs, as the existing barrier net would be functional regardless of changes to an intake structure.

The Agency based its approach of assigning costing modules to model facilities on a combination of facility and intake-specific questionnaire data in addition to satellite photos and overhead maps, where available.  Because not all facilities received the same questionnaire, the Agency attempted to utilize data responses to questions that were asked in both the short-technical and detailed questionnaires whenever possible.  In the end, the primary difference in data analysis between short-technical and detailed questionnaire respondents was the level to which the Agency developed costs.  The short-technical questionnaire responses did not provide significant intake-level data, outside of intake identification information and velocity.  For instance, for the short-technical questionnaire, the Agency did not obtain intake-specific information on the exact technology in-place for each intake.  The Agency instead obtained technology in-place information at the facility-level for short-technical questionnaires.  Necessarily, the Agency utilized this facility-level information for the short-technical respondents and treated the facility as though it were a single intake with the characteristics reported for the facility.  For the detailed questionnaire facilities, the Agency obtained sufficient intake-level information to develop individual costing decisions for each intake.

The Agency utilized questionnaire data as the primary tool in the assessment of the types of intake technologies applied at each model-facility.  For those facilities utilizing recirculating cooling systems in-place, the Agency assigned no compliance actions as they met the standards at baseline.  For those with once-through, combination, other, or unknown cooling system types, the Agency treated the facility as though all intakes were of once-through configuration.  The Agency chose this method so as to conservatively estimate the compliance costs, as the Agency’s methodology utilizes flow as the independent variable.  The Agency then determined those intakes (facilities) that met compliance requirements with technologies in-place.  These facilities received no capital or annual operating and maintenance compliance upgrade costs (although they may receive administrative or monitoring costs).  The Agency then categorized facilities by questionnaire type (that is, short-technical questionnaire and detailed questionnaire respondents).  Following the questionnaire division, the Agency categorized facilities according to waterbody type from which they withdraw cooling water.  The Agency then sorted the intakes (facilities) within each waterbody type based on their configuration as reported in the questionnaires. (Note, as discussed above, the Agency examined short-technical questionnaire facilities on the facility-level and detailed questionnaire respondents by the intake level.)

Generally, the categories of intakes within one waterbody type are as follows: canal/channel, bay/embayment/cove, shoreline, and offshore.  Once the intake (facility) is classified to this level the Agency examines the type of technology in-place and compares that against the compliance requirements of the particular intake (facility).  For the case of entrainment requirements, the only intake technology (outside of recirculating cooling) that qualifies to meet the requirements at baseline is a fine mesh screening system.  Few intakes have fine mesh in-place at baseline.  Therefore, in the case of entrainment requirements, most facilities with the requirement would receive technology upgrades.  The methodology for choosing these entrainment technologies is explained further on in this discussion.  For the case of impingement requirements, there are a variety of intake technologies that qualify to meet the requirements at baseline.  The intake types meeting impingement requirements at baseline include the following: barrier net (the only fish diversion system which qualifies), passive intakes (of a variety of types), and fish handling and return systems.  A significant number of intakes (facilities) have impingement technologies in-place.  Therefore, some intakes (facilities) require no technology upgrades when only impingement requirements apply.

For facilities that do not pre-qualify for impingement and/or entrainment technology in-place credits, the Agency focuses next on questionnaire data relating to the intake type – canal/channel, bay/ embayment/cove, shoreline, and offshore.  Within each intake type, the Agency further classifies according to certain specific characteristics.  For the case of bays, embayments, and coves, the Agency determined if the intake is flush, protruding, or recessed from shoreline.  For the case of canals and channels, the Agency similarly focuses on whether the intake is flush, protruding, or recessed from a shoreline.  In addition, the Agency calculates an approximate approach velocity using reported information on the canal flow rate and cross-sectional area, where applicable (specific to detailed questionnaire respondents only).  The approximated approach velocity aided the Agency in verifying the reported mean intake velocity.  For the case of shoreline intakes, the Agency necessarily assessed whether the intake is flush, protruding, or recessed.  For the case of offshore intakes, the Agency examines whether or not the intake has an onshore terminus (or well) and assesses the characteristics of the onshore system.

The information the Agency gathers up to this point is sufficient to narrow down the likely technology applications for each intake (facility).  However, in order to determine the best technology application, the Agency also utilizes commercially available satellite images and maps where available.  The use of the satellite images and maps aided the Agency in determining the potential for the construction of expanded intakes in-front of existing intakes, the degree of navigational traffic in the near vicinity of the intake, the potential for an intake modification to protrude into the waterbody (such as a near-shore t-screen) and whether a protrusion might be tolerated, the possibility of installing a barrier net system, obvious signs of strong currents, the relative distance of a potentially relocated intake inlet, the possibility for fish return installations of moderate length, etcetera.  The Agency was able to collect satellite images for most intakes (facilities) for which it required the resource.  However, in some cases (especially those in the rural, mid-western US), only maps were available.  Hence, for the case of a significant number facilities located near small freshwater rivers/streams and lakes/reservoirs, the Agency utilized only the questionnaire data and the overhead maps available.

The Agency prepared a crosswalk and breakdown of the application of the technology modules.  The crosswalk provides specific factors that EPA considered in the application of each module.  The following sections provide the factors that the Agency used in determining the proper technology application and explain any exceptions to these cases.

Module 1 - Add Fish Handling and Return System:  This technology applies almost exclusively for the case of impingement only upgrades.  The Agency applied this technology generally to facilities that when requiring the impingement only upgrade had an existing traveling screen system.  The Agency applied this technology generally when the intake velocity of the intake (facility) was roughly 1 ft/sec or below.  The rationale behind applying this technology in this case is that because the intake velocity is relatively low and the existing traveling screen system is functional, the fish handling and return system could be added to the operating system and would perform under these conditions.  Vendors noted that approximately 75% of the existing screen components would require replacement when adding fish handling and return.  It would be more prudent to replace the entire screen unit.  (See Traveling Screen cost module, page 5)

Module 2 - Add Fine Mesh Travelling Screens with Fish Handling and Return: This technology generally applies for the case of impingement and entrainment upgrades.  The Agency applied this technology to intakes (facilities) with an existing traveling screen system in-place.  The Agency applied this technology when the intake velocity was roughly 1 ft/sec or below.  The rationale behind the application is similar to that of Module 1, in that the low existing velocity allowed for replacement of the existing screen overlays without expanding the size of the intake appreciably to lower the velocity.  As a general approach, the Agency applied this technology to a variety of waterbody types and intake locations (such as in canals, in coves, and along shorelines).  Note: in addition to adding fine-mesh screens that this technology also replaces the fish handling and return system of the intake.  Note: this scenario requires replacement of all screen units with units that include fish handling and return features plus additional spray water pumps and a fish return flume.  Note: for those facility with existing screens and fish handling and return and only entrainment reduction is required only fine mesh screen overlay panels is applied..  See the documentation for this particular module for more information.

Module 3 - Add New Larger Intake Structure with Fine Mesh, Handling and Return: This technology generally applies for the case of impingement and entrainment upgrades.  However, in a few select cases, the Agency applied it for the case of impingement only, more on that below.  The Agency applied this technology to intakes with a variety of onshore configurations.  The Agency applied this technology when the intake velocity was above roughly 1 ft/sec.  The rationale behind the application is that demonstrated cases of operable fine-mesh screening systems for large plants have used design velocities of roughly 1 ft/sec or below.  Because of the velocity implications, the Agency necessarily required certain intakes (facilities) to enlarge their intakes.  Therefore, these intakes would be constructed anew in front of an existing structure and tied in after construction complete.  As a general approach, the Agency applied this technology to a variety of waterbody types and intake locations (such as in canals, in coves, and along shorelines).  Note that the Agency verified (through observation of satellite images and overhead maps) that sufficient open water area in front of the existing intake, and that the new protruding intake would not hinder boat traffic.  In a select few cases, the intake velocity of a facility complying with the impingement only requirements was extremely high.  In these cases, the Agency may have applied this module to allow for proper operation.

Module 4 - Add Passive Fine Mesh Screens at Shoreline: This technology applies mostly for the case of entrainment and impingement upgrades.  The Agency applied this technology generally in a very similar fashion to Module 3 above.  The primary difference for their applications is that Module 4 is slightly more flexible in its location than Module 3 and that Module 4 has the ability to be retrofitted to unusual intake structures, such as protruding intakes, submerged shoreline intakes, etc.  In addition, the passive wedgewire t-screen system is very well suited for application where currents are present, as the system is designed to utilize currents for controlling impingement.  The Agency applied this technology generally when the intake velocity of the intake (facility) was above roughly 1 ft/sec.  However, that is not exclusively the case, as there were exceptions where even for low velocity, unusual passive screen systems, the Agency upgraded these intakes with Module 4.  This module, similarly to Module 3 above, would apply for a select few cases that had extremely high intake velocities, even though they were required to comply with impingement only.

Module 5 - Add Fish Barrier Net: The Agency applied the barrier net module to control impingement, both in the case of impingement only upgrades and the combined impingement/entrainment upgrades.  As a general rule, the Agency applied the barrier net only to cases where it could acertain that a favorable geographical condition existed, such as the case of a wide mouth canal without boat traffic and low current potential, the similar conditions in a wide mouth cove/bay, and the similar conditions for a lake/reservoir shore.  In a select number of situations, the Agency applied both the fish barrier net system and an entrainment controlling system.  Generally, this was for the case that a fish handling and return system could not reasonably be configured to deliver impinged fish safely away from the intake.  Therefore, the barrier net served the purpose of preventing the cyclical impingement/reimpingement condition in several cases.  The Agency did not examine velocities when applying barrier nets.  Instead, the Agency focused on the configuration of the intake and its adjoining shorelines.

Module 6 - Gunderboom: The Agency did not apply this module for any of the intakes/facilities for the Notice of Data Availability.

Module 7 - Relocate Intake to Submerged Offshore with Passive Screen: The Agency applied this costing module to address impingement and entrainment requirements.  The Agency applied this module, generally, to any waterbody for which there was a clear advantage to its implementation.  What the Agency defined as an advantage for this module generally related to the fact that an onshore or short canal intake provided no clear avenue for applying one of the velocity reducing modules, such as numbers 3 and 4.  As a rule the Agency applied the relocation of an intake to submerged offshore only for cases where the existing intake velocity was significantly above 1 ft/s.  Additionally, the Agency relied on this module to represent situations where there was not one module that stood out as the clear choice solution.  Contrary to intuition, the Agency learned in its research of offshore submerged intakes that a good number are used in river environments.  Hence, the Agency utilized this module in several cases for large rivers.  The relocation distance utilized for each case was that derived from the median of those within the intake's waterbody class.

Module 8 - Add Velocity Cap at Offshore Inlet: The Agency applied a velocity cap at the inlet of a submerged offshore pipe in several cases to address impingement only requirements.  The prerequisite for this module was that the intake/facility had to have a submerged offshore intake with no reported impingement controls.  This combination was rare, as most submerged offshore intakes had at least passive offshore intake inlets.  However, for the small number of cases where facilities did not have impingement controls (or at least did not report them in the questionnaire), the Agency applied this module to meet the impingement only requirments.  As a general rule, the Agency has reservations about the ability of a velocity cap system to meet the numerical requirements of the impingement standards.  However, it should be noted that in the case of offshore intakes that the "location" of an intake can be considered for the compliance action.  Therefore, an offshore intake with a velocity cap is a combination that the Agency feels reasonably represents the costs of complying with the impingement requirements.

Module 9 - Add Passive Fine Mesh Screen at Inlet of Offshore Submerged: The Agency applied a passive, fine-mesh, wedgewire, t-screen system at the inlet of a submerged offshore pipe to address impingement and entrainment requirements.  The prerequisite for this module was that the intake/facility had to have a submerged offshore intake with no reported entrainment controls.  In some cases, the intake (facility) may have reported impingement controls, but the Agency generally ignored these controls and presumed that the installation of the passive fine mesh at the offshore inlet would suffice to control both entrainment and impingement effectively.  This module obviously is one of the simplest in application, as it is clear for all intakes (facilities) through the questionnaire whether or not their intake is submerged offshore.  The primary nuance for this situation exists where the intake (facility) may have reported both offshore inlet controls and onshore screening controls.  See module 10 for more discussion of onshore screening technologies for submerged offshore intakes.  For the purposes of the discusssion of this module, it should be noted that the Agency treated the existance of an offshore inlet as the primary location for the application of a compliance technology over an onshore modification where both pre-existed.

Module 10 - Add/Modify Shoreline Tech for Submerged Offshore: The Agency did not apply this module for any of the intakes/facilities for the Notice of Data Availability.  Even though this technology would be a reasonable method for an intake (facility) to comply with the rule, the Agency chose not to use it.  The basic reason that the Agency did not use the technology was that in most cases where entrainment controls would be required this method did not allow the reconfigured intake to be enlarged in order to lower the intake velocity.  In addition, the passive screen intake at the inlet of the offshore pipe was more expensive, and therefore, likely more applicable for a wider range of applications.

Module 11 - Add Double-Entry, Single-Exit with Fine Mesh, Handling and Return: The double-entry, single-exit screen provides a way for facilities with limited ability to expand the size of their intakes to lower the intake velocity (that is, increase the cross-sectional area of the intake screens) without expanding the foot print of the intake.  This would be a useful application for facilities attempting to comply with the impingement and entrainment requirements in the narrow terminus of a canal or cove.  Additionally, in cases where the intake is recessed from shore, this technology can be applied to shoreline applications.  The Agency generally applied this technology when the intake velocity was above roughly 1 ft/sec.

The Agency compiled a breakdown of the application of each module by compliance requirement and waterbody type.  These results are presented in Tables 1 – 3.

Table 1.  Technology Module Applications for Facilities with Impingement Requirements Only

|  | Waterbody Type |
| --- | --- |
| Module | Lake/Res. | Great Lake | Ocean | Estuary | River/Stream | All Waterbodies |
| 1 | 44 | 1 | 4 | 26 | 42 | 117 |
| 2 | 0 | 0 | 0 | 1 | 3 | 4 |
| 3 | 0 | 0 | 0 | 0 | 2 | 2 |
| 4 | 0 | 0 | 0 | 1 | 6 | 7 |
| 5 | 31 | 1 | 0 | 14 | 13 | 59 |
| 6 | 0 | 0 | 0 | 0 | 0 | 0 |
| 7 | 0 | 0 | 0 | 0 | 0 | 0 |
| 8 | 8 | 0 | 0 | 1 | 0 | 9 |
| 9 | 0 | 0 | 0 | 0 | 0 | 0 |
| 10 | 0 | 0 | 0 | 0 | 0 | 0 |
| 11 | 0 | 0 | 1 | 0 | 2 | 3 |

Table 2.  Module Applications for both Entrainment & Impingement  Requirements

|  | Waterbody Type |
| --- | --- |
| Module | Lake/Res. | Great Lake | Ocean | Estuary | River/Stream | All Waterbodies |
| 1 | 0 | 0 | 0 | 0 | 1 | 1 |
| 2 | 0 | 13 | 2 | 23 | 34 | 72 |
| 3 | 0 | 7 | 0 | 10 | 4 | 21 |
| 4 | 0 | 5 | 1 | 13 | 42 | 61 |
| 5 + | 0 | 2 | 0 | 1 | 1 | 4 |
| 6 | 0 | 0 | 0 | 0 | 0 | 0 |
| 7 | 0 | 2 | 1 | 4 | 10 | 17 |
| 8 | 0 | 0 | 0 | 0 | 0 | 0 |
| 9 | 0 | 12 | 11 | 2 | 6 | 31 |
| 10 | 0 | 0 | 0 | 0 | 0 | 0 |
| 11 | 0 | 17 | 5 | 19 | 15 | 56 |

Note: Module “5+” represents the application of module 5 combined with another module.

Table 3.  Module Applications for All Requirements and All Waterbody Types

| Module | All Waterbodies |
| --- | --- |
| 1 | 118 |
| 2 | 76 |
| 3 | 23 |
| 4 | 68 |
| 5 | 63 |
| 6 | 0 |
| 7 | 17 |
| 8 | 9 |
| 9 | 31 |
| 10 | 0 |
| 11 | 59 |

Examples of the Application of Technology Modules to Model Facilities

Because the determination of the best technology application depends on a variety of factors and there is a large population of intakes to which these multiple factors apply, the Agency views a series of examples as the best means for demonstrating the logical progression that it applied to the decisions.  Based on the classification system described above, the Agency presents examples of each major intake type – canal/channel, bay/ embayment/cove, shoreline, and offshore– to aid the understanding of the Agency’s costing assignment process.

Example 1: Canal or Channel Intake

In this example, an intake withdraws cooling water through a canal branching off a tidal river.  The intake is a shoreline intake, flush with the shore and built at the terminus of the canal.    Based on its characteristics, the facility is subject to impingement and entrainment requirements.  The Agency determined that the intake is at the terminus of the canal by examining the satellite imagery and overhead maps, using the reported latitude and longitude of the intake.  The detailed questionnaire reports that the existing intake is a coarse-mesh traveling screen with a fish diversion system in-place.  The Agency determined that the reported fish diversion technology in-place was a fish-bypass technology using the satellite imagery.  The reported mean intake velocity is 1.5 ft/s, and the Agency calculated the approximate canal approach velocity as 1.4 ft/s based on the canal cross-sectional area and flow rate reported in the questionnaire.  Therefore, the Agency concludes that the reported intake velocity is accurate.  The canal length is reported at 100 ft.  Both the overhead map and satellite photo demonstrate that the intake is close to this estimated length.  In addition, the Agency observes that the intake location at the terminus of the canal is less than 100 feet from the bank of the tidal river.  The Agency determines that the mouth of the canal is not significantly wider than the canal itself and that the apparent route of boat navigation is to utilize a portion of the canal for barge docking and traffic.

Based on the above factors, the Agency determines that the best technology for this model intake application is a double-entry, single-exit traveling screen with fine-mesh overlay and a fish handling and return system.  The reason that the Agency utilized a double-entry, single-exit system in this case is that the velocity of the intake is significantly above 1 ft/s.  The double-entry, single-exit systems provide increased surface area (compared to a single-entry, single-exit system) without significantly enlarging the horizontal footprint of the intake.  Therefore, for the case of a canal terminus, where enlarging an intake’s width cam be impractical, the double-entry, single-exit system allows the intake velocity to be lowered to level that is in keeping with current practice for fine-mesh, entrainment controlling systems.  The Agency studied existing cases of retrofit fine-mesh screen applications and found the 1 ft/s threshold a reliable design criterion for large intake systems where surface area can be constricted.  The fish handling and return system in this case addresses the impingement control requirements.  Because the canal is not long and the return branch would be of reasonable length, the Agency considered the fish handling and return system to be appropriate.  The existing fish by-pass system is not considered to be adequate (in and of itself) for meeting the impingement requirements of the national rule.  In addition, the navigational use of the canal and the canal’s limited throat width necessarily prevents the use of a barrier net system.

In this case, the Agency determines that the debris loading potential near the intake is high.  This is due to the clear evidence of boat/barge traffic and the known nature of the particular tidal river from which this facility withdraws water.

Example 2: Bay/Embayment/Cove

In this example, an intake withdraws cooling water from a Great Lake.  The intake is a shoreline intake, flush with shore and built at the terminus of the cove.  Based on its characteristics, the facility is subject to impingement and entrainment requirements.  The Agency determined that the intake is at the terminus of the cove by examining the satellite imagery and overhead maps, using the reported latitude and longitude of the intake.  The detailed questionnaire reports that the existing intake is a coarse-mesh traveling screen with no impingement reducing technologies in-place.  The reported mean intake velocity is 2.0 ft/s.  Both the overhead map and satellite photo demonstrate that the cove recedes approximately 500 ft from the main water body.  The Agency determines that the mouth of the cove is approximately 250 feet in width.  Based on the overhead map and satellite image, there is no evidence of boat traffic in the cove.  The railroad access and highway access of the plant apparently meet the fuel delivery needs of the plant.

Based on the above factors, the Agency determined that the best technology for this model intake application is construction of a new, larger intake directly in front of the existing structure.  In addition, the Agency determined that a barrier net system would address the impingement requirements imposed on the intake.  The reason that the Agency utilized a new, larger intake system in this case is that the velocity of the intake is significantly above 1 ft/s and the there is ample room directly in front of the existing intake to allow for the larger intake.  Another alternative would be to use the double-entry, single-exit screen as in the above canal example.  The larger intake system provides increased surface area (compared to the existing single-entry, single-exit system), thereby reducing the intake velocity to a level that would facilitate use of the fine-mesh system.

A fish handling and return system in this case would be difficult to implement due to the orientation of the deep cove.  The Agency would be concerned about the creation of a cyclical impingement condition, which would exacerbate the strain on the organisms.  A 500-foot return system could be built, but the alternative system of a barrier net is favorable for this particular situation, in the Agency’s view.  The lack of navigational use of the cove and the cove’s wide throat provides a good environment for barrier net deployment.

In this case, the Agency determines that the debris loading potential near the intake is low.  This is due to the lack of boat/barge traffic evidence and the known nature of the particular Great Lake from which this facility withdraws water.

Example 3: Shoreline

In this example, an intake withdraws cooling water from a freshwater river.  The facility withdraws more than 5 percent of the mean annual flow of this river.  Hence, it is subject to impingement and entrainment requirements.  The intake is a shoreline intake, protruding from shore.  The Agency determined that the intake extends 10 feet into the waterbody by examining the satellite imagery and overhead maps, using the reported latitude and longitude of the intake.  The Agency also observes that the apparent river width at the intake location is well over 100 feet.  The intake is located on a straight section of river, and an approximately 15 foot protruding diversion wall protects the intake from river debris and traffic.  The detailed questionnaire reports that the existing intake is a coarse-mesh traveling screen with a fish handling and return system.  The reported mean intake velocity is 3.0 ft/s.  Based on the satellite images, there is evidence of coal barge traffic near the intake, but significantly far away to allow for the protruding intake.

Based on the above factors, the Agency determines that the best technology for this model intake application is construction of a fine-mesh, cylindrical, wedge wire t-screen system.  This passive intake would be constructed to branch from the original protruding intake.  In the Agency’s view, the wedge wire t-screen system will address the impingement and entrainment requirements imposed on the intake.  The reason that the Agency utilized a new intake system in this case is that the velocity of the intake is significantly above 1 ft/s and there is already precedence to allow for a protruding intake.  With the construction of a properly sized replacement intake, the velocity can be lowered for entrainment and impingement controls, and the current of the river can be utilized to aid the operation of the intake.  Another alternative would be to use a new, larger intake protruding into the waterbody as in the cove example above.  Both of the larger intake system provides increased surface area (compared to the existing single-entry, single-exit system), thereby reducing the intake velocity to a level that would facilitate use of the fine-mesh system.  However, the wedgewire screen system would provide additional advantages in the form of inherent impingement controls.  A fish handling and return system with a traditional traveling system could be an option.

In this case, the Agency determines that the debris loading potential near the intake is high.  This is due to the clear evidence of boat/barge traffic and the known nature of the particular river from which this facility withdraws water.

Example 4: Offshore

In this example, an intake withdraws cooling water from a submerged offshore intake in an Ocean.  At the offshore inlet of the intake is a velocity cap crib built approximately 500 feet from shore.  The facility is a short-technical questionnaire facility, and the Agency has no information as to whether or not the intake delivers water to an onshore well.  Based on observations of the satellite imagery, the Agency was also unable to identify an onshore well.  Based on its characteristics, the facility requires an entrainment technology upgrade.  The existing intake – a velocity cap system – is insufficient to meet the entrainment requirements.  The facility reports no other impingement or entrainment technologies in-place.  The reported mean intake velocity is 1.0 ft/s.

The Agency is unable to verify or disprove the length of the submerged offshore intake with overhead maps and satellite photos, as it did for the cases of canal and cove distances.  However, the distance of the intake offshore may not be relevant for certain costing modules.

Based on the above factors, the Agency determines that the best technology for this model intake application is construction of a fine-mesh, cylindrical, wedge wire t-screen system constructed at the inlet of the offshore, submerged intake piping.  The reason that the Agency utilized an inlet t-screen system in this case is that, to the best of its knowledge, the Agency determined there is no onshore technology in use.  Had an onshore technology been reported or observed for the facility, the Agency could have considered upgrades to that technology system (such as replacing coarse-mesh screen overlays with fine-mesh, etc.).  However, the Agency opted to utilize a technology that would work for the description of the facility in its possession.  With the construction of a properly sized replacement intake, the velocity can be maintained at a low level (1 ft/s) for entrainment and impingement controls, and the natural currents of the Ocean can be utilized to aid the operation of the intake.

In this case, the Agency determines that the debris loading potential near the intake is high.  This is due to the fact that this intake is in a coastal Ocean setting.

Figure 1.  Impingement Controls Flowchart for Model Facility Compliance Costs

Figure 2.  Entrainment Controls Flowchart for Model Facility Compliance Costs

Figure 2 (cont.).  Entrainment Controls Flowchart for Model Facility Compliance Costs

# Text boxes

Impingement:

Non-Recirculating Facilities

Facility will incur costs for impingement controls upgrade.

No

Yes

Does the facility have impingement controls in-place?

No costs for impingement controls.

Continue to Next Page…

No

Yes

Does the facility withdraw from an estuary, tidal river, or Great Lake?

No costs for entrainment controls.

Yes

Does the facility withdraw from a Lake or Reservoir?

Entrainment: Non-Recirc. Facilities

No

Yes

Does the facility have entrainment controls in-place?

No costs for entrainment controls.

No

Facility will incur costs for entrainment controls.

No costs for entrainment controls.

No

Yes

Is the intake flow greater than 5 % of the freshwater river/stream flow?

Entrainment: Continued from Previous Page

Facility will incur costs for entrainment controls upgrade.

No

Yes

Does the Facility withdraw > 500 MGD from an Ocean?

Facility will incur costs for entrainment controls