Mercury Emissions Monitoring Program for Coal-Fired Boilers

under the Clean Air Mercury Rule

Status Report

August 2006

Introduction

The Clean Air Mercury Rule (CAMR) requires affected electric utility units to continuously monitor mercury (Hg) mass emissions, using technically-feasible, compliance-capable technologies.  To ensure that the Hg emission reduction goals of CAMR are met, these monitoring technologies will be subject to rigorous certification and quality assurance/quality control (QA/QC) requirements under 40 CFR Part 75.  The U.S. Environmental Protection Agency (EPA) continues to work with the regulated community, the monitoring equipment and software vendors, academia, and other organizations to ensure timely implementation of a technically sound, effective CAMR mercury monitoring program.

This paper updates the February 2006 status report on the mercury emissions monitoring program under the CAMR.  The paper discusses the results of the mercury emission monitoring demonstration and method validation tests to date and the remaining challenges to be overcome.  The paper also discusses capacity issues associated with the availability and installation of the required monitoring systems within the required CAMR deadlines.

Background

Over the past two years, EPA, the Electric Power Research Institute (EPRI), industry and monitoring equipment vendors have conducted field demonstration and validation tests of continuous mercury emission monitoring systems (CEMS) and sorbent trap monitoring systems at a number of coal-fired utility boilers.  EPA and the National Institute of Standards and Technology (NIST) have also been working together to develop NIST-traceable mercury calibration gas standards and protocols necessary to ensure the accuracy of the mercury monitoring systems.  As a result of these tests, system design changes have been made to improve the performance and reliability of the monitoring systems.  Most notably, design changes have been made to reduce probe plugging and calibration drift, particularly under wet stack environments.  Additionally, the precision between different CEM systems has improved dramatically.

Working with EPRI, NIST, and industry, most of the major issues have been successfully addressed, and now the focus of future field tests and laboratory analyses is on resolving the remaining issues.  These include: (1) developing a viable instrumental reference method (IRM) for mercury; (2) finalizing NIST traceability protocols for Hg calibration gas cylinders and gas generators; and (3) improving CEMS performance in daily calibration error tests and system integrity checks (especially in low temperature, low concentration, high moisture stack environments).

EPA is also working with industry and other groups to develop an alternative reference method using sorbent trap technology.  However, the Agency still considers a workable instrumental reference method for mercury to be the best alternative to the currently-required Ontario Hydro wet-chemistry reference method.

Hg CEMS and Sorbent Trap Hardware

Mercury monitoring technologies continue to advance at a rapid pace and are on-track to meet the QA/QC requirements required under CAMR.  However, continued commitment from all parties is essential to maintain this pace and ensure that CAMR requirements are met.

Approximately, twelve Hg CEMS and sorbent trap vendors are currently developing new and improved monitoring systems.  EPA, EPRI and monitoring system vendors will continue to conduct tests demonstrating these improvements at various coal-fired power plants in the United States.  Hg CEMS manufactured by Tekran, Horiba, Durag, Opsis, Thermo, Ohio Lumex, Forney/Genesis, and GE/PS Analytical are currently being field tested.  Most manufacturers have made significant improvements to or refinements of their monitors as a direct result of EPA and EPRI’s field demonstration tests.  For example, several new CEMS probe designs have been developed, some of which reduce plugging and may reduce system calibration drift in low concentration, high moisture stack environments.  Other more streamlined probe designs are being developed by  equipment vendors to facilitate sample traversingduring IRM testing.  Vendors are also working to integrate Hg calibration gas generating systems into their CEMS.

Mercury sorbent trap monitoring systems continue to perform well at the EPA and EPRI field test sites.  Remaining developmental efforts for these systems will include: (1) testing of a variety of sorbent materials and sample conditioning systems; and (2) development of alternatives to the lengthy process of sending Hg samples to a laboratory for analysis.  Promising alternatives that allow for rapid, on-site sample analysis include thermal desorption and direct combustion methods, both of which are based on sample heating/combustion to release mercury.  Industry is also working to improve the Hg detection capabilities of sorbent trap systems in low-concentration stack environments.

Instrumental Reference Method Evaluation and Validation

EPA has drafted a conceptual mercury IRM to provide an alternative to the lengthy and complex Ontario Hydro reference method currently required by CAMR.  EPRI and industry will continue to provide IRM development assistance to EPA through the assessment of its feasibility and challenges.  Issues associated with the implementation and validation of the conceptual IRM are currently being addressed at the EPA North Carolina and the EPRI Kentucky test sites.  Also, IRM development was one of the primary areas of focus at the recent Pennsylvania/Lehigh University field test, and is currently a primary area of focus at a Texas lignite field test site.  The principal objective of these field tests is to demonstrate the practicality and effectiveness of the draft IRM procedures in a variety of stack environments.  EPA and EPRI are examining the length of time required to perform the procedures and the efficacy of pre- and post-test dynamic spiking, as well as the possibility of using SO2 stratification test results as an indicator of Hg stratification in the stack.  Equipment manufacturers are also exploring equipment design modifications to improve sample conditioning, reference method probe mobility, and the integrity of the instruments during transport.

Field Demonstrations

Field demonstration tests currently in progress include a continuation of EPA’s work at a coal-fired power plant in North Carolina and EPRI’s work at a field test site in Kentucky. Substantial improvements in Hg CEMS and sorbent trap operation and performance have been achieved at these two test sites.  Testing was recently completed at a coal-fired power plant in Pennsylvania in collaboration with Lehigh University, and additional testing has commenced at a lignite coal-fired facility in Texas.  The following paragraphs describe these tests in more detail.

North Carolina Site Testing:  At this dry stack location, EPA ORD has installed and operated a Tekran CEMS since December 2004.  In addition to the Tekran system, the test team has evaluated Hg CEMS manufactured by Thermo, Horiba, GE/PS Analytical, Forney/Genesis, Durag and Ohio Lumex.  These evaluations include multiple certification and relative accuracy tests as well as long-term daily calibration error tests and weekly system integrity checks.  Results of the testing effort include improvements in instrument reliability as evidenced through increased data availability.  More recently, the North Carolina site has been used to demonstrate and optimize tools and approaches for implementing the conceptual IRM, including the refinement of approaches for dynamic spiking.  The North Carolina test site is also being used to evaluate new and innovative probes that can be used to meet the traversing requirements of the IRM.

Kentucky Site Testing:  As mentioned in the February 2006 status report, the Kentucky test site is now serving as an equipment and software development location for Hg CEMS vendors and is considered to be representative of the most challenging measurement environment found among well-controlled boilers (i.e., it represents low temperature, low Hg concentration, and high moisture flue gas conditions).  EPRI has evaluated the performance and reliability of CEMS manufactured by GE, Thermo, and Tekran at this site, as well as sorbent trap systems made by Frontier Geosciences.  Remaining CEMS and sorbent trap performance issues continue to be addressed.

Participating equipment vendors are also developing and testing suitable probes for the wet stack conditions encountered at the Kentucky site.  One manufacturer is testing two probe types simultaneously.  Each of these new probes has shown promise, and has significantly reduced the occurrence of plugging.  On-going efforts are being made to continue to improve probe reliability and reduce the amount of required maintenance and repair.  The Agency expects that industry and vendors will have reliable probes within the next few months.

Other outstanding CEMS issues that have been identified at the Kentucky test site include: (1) the need to reduce calibration drift; (2) the need for front-end humidification to allow for dynamic spiking and daily calibration at the probe; and (3) the need to optimize the position of the Hg converter in the sampling system (i.e., nearer to or farther away from the probe).  EPRI and industry experts are addressing these issues, however, the same high level of commitment and support provided up to this point needs to be maintained by all parties to ensure that these issues are satisfactorily resolved.

Lehigh Field Study:  With support from EPA, EPRI, the Italian government, several utility companies and others, the Lehigh University Energy Research Center (ERC) organized a field test where reference methods for mercury, heavy metals and particulate, which have been developed in the U.S. and the European Union (EU), were compared.  The field testing was begun in late June 2006 and was completed in July 2006.  Testing was conducted by a joint U.S. and European Union team at a power plant in Pennsylvania.  Western Kentucky University (WKU) provided a mobile mercury test laboratory for the project.

As part of the Lehigh field study, EPA was able to satisfactorily perform many of the procedures in EPA’s draft conceptual IRM, including dynamic spiking, calibration error, and system integrity tests.  The test team performed IRM test procedures on Hg CEMS manufactured by Thermo Electron, Tekran, GE/PS Analytical and Ohio Lumex.  In addition, Frontier Geosciences and CONSOL/Clean Air performed Appendix K sorbent trap monitoring.  The Lehigh study provided a valuable opportunity to assess the amount of time required to perform the IRM pretest activities and sample runs, and to develop and optimize the dynamic spiking procedures.  Due to time and resource constraints, only limited traverse and stratification tests (using SO2  as a surrogate) were undertaken.  These issues will be addressed more fully in future field tests. The results of the conceptual IRM testing from the Lehigh study will be compared to those obtained with paired Ontario Hydro trains.

We Energies Michigan Field Study:

We Energies has been working with the Department of Energy on a mercury control technology demonstration project at a Michigan test site, involving a ®TOXECON baghouse and activated carbon injection to control mercury emissions from three electric generating units.  Hg CEMS manufactured by Thermo have been installed on the inlet and outlet of the baghouse and have been operating without any significant problems for several months.  Baseline stack tests were conducted in February using the Ontario Hydro reference method and the Appendix K sorbent trap method.  In addition, CEMS relative accuracy and IRM evaluation testing are scheduled to be performed later this summer or in the fall.

Texas Lignite Field Study:

WKU, in conjunction with EPRI, is conducting three field tests on Tekran and Thermo CEMS at a lignite-fired utility plant in Texas.  The tests are scheduled to be completed later this summer.  Both relative accuracy and IRM evaluation testing will be conducted.  Stratification tests, using SO2 as a surrogate for Hg, will also be performed during one of the field tests.

Additional Field Tests:

EPRI and the U.S. Department of Energy performed relative accuracy tests of a Hg CEMS and a sorbent trap monitoring system at another field site in Pennsylvania.   IRM evaluation tests were also performed.  The IRM tests were conducted using batch-type dynamic spiking.

Field tests of Thermo and Tekran CEMS and two sorbent trap monitoring systems have also been performed at an Indiana power plant.  These tests are part of EPA’s Environmental Technology Verification (ETV) program.  The verification testing included two relative accuracy tests, the first of which was conducted in mid-June 2006 and the second in mid-July 2006.  IRM evaluation testing was not done at this site.

Availability of Mercury Monitoring Systems

Approximately 1100 electric generating units (EGUs) are affected by CAMR.  EPA estimates that between 800 and 1000 mercury monitoring systems (i.e., Hg CEMS and sorbent trap systems) must become commercially available between now and 2008, to ensure that the affected EGUs will be able to meet the continuous emission monitoring requirements of CAMR.  The exact number of Hg monitoring systems that will be needed to implement CAMR is somewhat uncertain, because: (1) some of the affected units are in common stack configurations; and (2) at least 100 to 200 of the affected units are expected to qualify as low mass emission (LME) units under Part 75 (§75.81(b)), and the owners of these units may elect to perform periodic Hg emission testing rather than installing mercury monitoring systems.

The manufacturers of Hg CEMS have indicated that beginning in 2007 they will, collectively, be able to produce well over 1000 CEMS per year. One vendor plans to produce 600 Hg CEMS per year, and a second vendor plans to produce 60 CEMS per month.  A number of other monitoring equipment manufacturers also plan to increase their production capabilities to meet the monitoring demands of CAMR.  Based on these projections, there will be more than enough Hg CEMS and sorbent trap systems available to meet the requirements of CAMR, and there should be sufficient time for facilities to install and certify the monitoring systems before the January 1, 2009 compliance deadline.

Thus, EPA is confident that the CAMR monitor certification deadline will be met.  The Agency will continue to work with industry and with the equipment vendors to ensure that the CAMR emissions monitoring program is implemented on schedule.

NIST- Traceable Hg Calibration Standards

NIST continues to provide assistance in developing Hg reference standards for elemental and oxidized mercury.  The existence of such reference standards is the first step in developing the NIST-traceable Hg standards for use under Part 75.  EPA ORD and NIST are collaborating to develop calibration procedures for mercury gas generators and cylinders.  Gas generators calibrated by these procedures are expected to be available for field tests during the fall of this year.  These calibration procedures will serve as the basis for drafting traceability protocols for elemental and oxidized mercury.  The Agency also expects that NIST-traceable gas standards and protocols will be available in fiscal year 2007 for use in certifying CEMS and sorbent trap monitoring systems.

Rulemaking Changes to Hg Monitoring Provisions in Part 75

EPA has proposed minor technical and procedural changes to the Hg monitoring provisions of Part 75.  The proposed changes were published in the Federal Register on 22 August 2006 and are expected to be finalized by early summer 2007.  These changes include adding EPA Method 29 (with additional QA provisions consistent with the Ontario Hydro method) as an alternative reference method.  Method 29 is similar to Ontario Hydro, but is more familiar to stack testers.  The method would be an option for relative accuracy and LME tests.

The rule change proposal also addresses the testing and reporting requirements of mercury LME units and provides changes to the common stack provisions.  EPA will also solicit comment on how to equitably apply the LME provision to units which, in addition to coal, burn fuels that have very low Hg content.  The rule currently assumes that only coal is burned in these units.

# Footnotes

In order to make measurements of its concentration in the stack, sampling at multiple points is generally required.  “Traversing” is the act of moving the probe to reach the individual sampling points.