July 22, 1994

Contract #TW0592

SPECIAL SPECIFICATION

SECTION 16631

CENTRAL BATTERY INVERTER SYSTEMS

PART 1 - GENERAL                                           						  Page

1.01 Related Documents 	2

1.02 Summary	2

1.03 Submittals	2

1.04 Quality Assurance	3

1.05 Warranty 	3

PART 2 - PRODUCTS

2.01 Manufacturers	4

2.02 Central Battery Inverter System 	4

2.03 Finish 	5

2.04 Concrete Bases	5

PART 3 - EXECUTION

3.01 Concrete Bases	6

3.02 Installation	6

3.03 Identification	6

3.04 Field Quality Control	6

3.05 Cleaning	7

3.06 Demonstration	7

SPECIAL SPECIFICATION

SECTION 16631

CENTRAL BATTERY INVERTER SYSTEMS

PART 1 - GENERAL

1.01 RELATED DOCUMENTS

A.  	Drawings and general provisions of Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

B.  	Requirements of the following Division 16 Sections apply to this Section:

1.  	"Basic Electrical Requirements."

2.  	"Basic Electrical Materials and Methods."

1.02 SUMMARY

A.  	This Section includes a battery source packaged with battery charger, inverter, transfer switch, and automatic control and protective devices to provide an integrated system.

1.03 SUBMITTALS

A.  	General:  Submit the following in accordance with Conditions of Contract and Division 1 Specification Sections.

B.  	Product data for products specified in this Section.  Include dimensions and data on features and components.  Include wiring diagrams and elevation view of front panel showing control and indicating devices.  Include data on ratings.

C.  	Maintenance data for products for inclusion in "Operating and Maintenance Manual" specified in Division 1 and in Division 16 Section "Basic Electrical Requirements."

D.  	Record of Field Tests:  Covering tests required by Article 700 of the National Electrical Code and Part 3 of this Section.

E.  	Special Project warranties specified in this Section.

1.04 QUALITY ASSURANCE

A.  	Components and Installation:  Comply with NFPA 70, National Electrical Code.

B.  	Listing and Labeling:  Provide products specified in this Section that are listed and labeled.

1.  	The Terms "Listed" and "Labeled":  As defined in the National Electrical Code, Article 100.

2.  	Listing and Labeling Agency Qualifications:  A "Nationally Recognized Testing Laboratory" (NRTL) as defined in OSHA Regulation 1910.7.

C.  	Comply with UL 924, Standard for Emergency Lighting and Power Equipment.

1.05 WARRANTY

A.  	Special Project Warranty:  A written warranty, mutually executed by the manufacturer and the Installer, agreeing to replace central battery inverter systems that fail in materials or workmanship within the special project warranty period specified below.  This warranty shall be in addition to, and not a limitation of, other rights and remedies the Owner may have under the Contract Documents.

B.  	Special Project Warranty Period:  10 years beginning on the date of Substantial Completion.  A full warranty shall apply for the first year of the period, and a pro rata warranty for the last 9 years.

PART 2 - PRODUCTS

2.01 MANUFACTURERS

A.  	Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated in the Work include, but are not limited to, the following:

B.  	Manufacturers:  Subject to compliance with requirements, provide products by the following:

1.  	Exide Electronics, Inc.

2.02 CENTRAL BATTERY INVERTER SYSTEM

A.  	Description:  Powerware System 50 Model 40. A factory-fabricated unit that uses an integral battery source, input filter, an inverter with a maintenance bypass switch, and automatic control and switching to provide both normal and emergency or standby electrical supply for alternating current branch circuit loads.

B.  	Operation:  System normally supplies power to output circuits from a single external normal supply source for the system.  When the normal power source fails, the system automatically transfers from the normal source to the internal battery source and reenergizes and feeds output circuits through the inverter.  When normal power is restored, the load automatically retransfers to the normal supply, and the battery is recharged.

C.  	Multiple Output Voltages:  System shall supply branch circuits at 480/277V voltage levels as indicated.  Voltages shall be transformed internally from 480V 3 phase 3 wire as required to produce indicated output voltages.

D.  	Provide capacity and voltage ratings as indicated.  Indicated capacity ratings applyboth to 100-percent tungsten lamp load and 100-percent low-power-factorfluorescent lamp ballast load.

E.  	Enclosure:  NEMA Type 1 steel cabinet.  Provide access to components through hinged doors with flush tumbler lock and catch.

F.  	Inverter:  Solid-state type with features including:

1.  	Output voltage automatically regulated to within plus or minus 2 percent, and output frequency regulated to within plus or minus 1 Hz, from no load to full load at unity power factor over the operating range of the battery voltage.

2.  	Total Conversion Efficiency:  75 percent, minimum.

3.  	Output Wave Form:  Sine wave with maximum 10-percent total harmonic distortion throughout the battery operating voltage range, at unity power factor, from 50-percent capacity load to full load.

G.  	Protection:  Automatic, 130-percent current-limiting, short-circuit protection and fail-safe start-up protection for inverter.  Automatic low-battery-voltage shutdown, reverse input polarity protection, and separate overload and short-circuit protection for input power circuit and control circuit.

H.  	Battery Charger:  Solid-state, automatic, three-charging-rate type with minimum charger efficiency of 85 percent.  Include controls that automatically apply an equalizing charge to the battery every 90 days.

I.  	Battery:  Sealed lead-calcium type designed for maintenance-free operation, including no addition of water for the service life of the battery.

J.  	Instrumentation and Controls:  Include ready-normal power "on" light, "charge" light, "inverter supply load" light, battery voltmeter, a.c. output voltmeter, load ammeter, and test switch to simulate a.c. failure.  Provide meters with 2-percent accuracy.

K.  	Batteries shall provide a minimum of 15 minutes of back-up power at 100%  load.

L.  	Provide input circuit Breaker rated at 125% of maximum AC output current.

2.03 FINISH

A.  	Cabinet:  Manufacturer's standard baked-enamel finish over corrosion-resistant prime treatment.

2.04 CONCRETE BASES

A.  	Concrete:  Portland cement, mix to a 4000-psi, 28-day compressive strength.

1.  	Cement:  ASTM C 150, Type I.

2.  	Fine Aggregate:  ASTM C 33, sand.

3.  	Coarse Aggregate:  ASTM C 33, crushed gravel.

B.  	Reinforcement Fabric:  ASTM A 185, welded-wire fabric, plain.

C.  	Reinforcement Bars:  ASTM A 615, Grade 60, deformed.

PART 3 - EXECUTION

3.01 CONCRETE BASES

A.  	Construct concrete equipment bases of dimensions indicated.

B.  	Form concrete bases having permanent steel frame, using steel channels conforming to ASTM A 36, size and location as indicated.  Miter and weld corners and provide cross bracing.  Anchor or key to floor slab.

C.  	Install reinforcing bars, tied to frame, and place anchor bolts and sleeves using manufacturer's installation template.

D.  	Form concrete bases using framing lumber with form-release compounds.  Chamfer top edges and corners.

E.  	Install reinforcing bars and place anchor bolts and sleeves using manufacturer's installation template.

F.  	Place concrete and allow to cure before installation of equipment.

G.  	Clean exposed steel frames and apply 2 coats of rust-preventative metal primer and 2 coats of exterior, gloss, alkyd enamel in color selected by the Architect.

3.02 INSTALLATION

A.  	Manufacturer's Field Services:  Arrange and pay for the services of a factory-authorized service representative to supervise the installing, connecting, testing, and adjusting of the unit.

B.  	Clearance:  Minimum 36 inches in front of unit and additional side and rear clearance if required by manufacturer's installation instructions.

3.03 IDENTIFICATION

A.  	Identify system and components in accordance with Division 16 Section "Electrical Identification."

3.04 FIELD QUALITY CONTROL

A.  	Tests:  Under supervision of factory-authorized service representative, test all system functions, operations, and protective features.  Adjust to ensure operation is in accordance with specifications.  Perform tests required by the National Electrical Code, Article 700.  Perform the following tests upon completion of installation of system and after building circuits have been energized from normal power source.

1.  	Simulation of malfunctions to verify protective device operation.

2.  	Provision of instruments as required to make positive observation of test results.

3.  	Tests of duration of supply on emergency, demonstrations of low-battery-voltage shutdown, and transfers due to normal source failure and restoration.

B.  	Retest:  Correct deficiencies identified by tests and observations and retest until specified requirements are met.

3.05 CLEANING

A.  	Upon completion of installation, inspect system components.  Remove paint splatters and other spots, dirt, and debris.  Touch up scratches and mars of finish to match original finish.  Clean unit internally using methods and materials recommended by manufacturer.

3.06 DEMONSTRATION

A.  	Training:  Arrange and pay for the services of a factory-authorized service representative to demonstrate adjustment, operation, and maintenance of the system and to train Owner's personnel, for a minimum of 5 working days.

B.  	Conduct a minimum of 2 hours of training as specified under "Instructions to Owner's Employees" in the "Project Closeout" Section of these specifications.

C.  	Schedule training with at least seven working days advance notification.

END OF SECTION