## Path 15 vs Borah West
Path 15 vs Borah West |  |  |  |  | Put in this one for 5/15 tp 9/15
for temp >55 F and <90 F | [5 empty] | For temp >90 F
| Y = Path 15 flow |  |  | X = Borah West flow |  | Y = Path 15 flow |  |  | X = Borah West flow
| 3409 |  |  | 2065 |  | 3250 |  |  | 2065
| 1775 |  |  | 2307 |  | 1910 |  |  | 2307
| -1634 |  |  | 242 |  | -1340 |  |  | 242
|  | m = | -6.7521 |  |  |  | m = | -5.5372
| mX+k=Y |  |  |  |  | mX+k=Y
| or mX -Y=K thus |  | -6.752 X - Y = -17352 |  |  | or mX -Y=K thus |  | -5.537 X - Y = -14684
|  |  | where |  |  |  |  | where
Solving the | -17352.0165 |  | Y = Path 15 flow |  | k= | -14684.2975 |  | Y = Path 15 flow
constant | -17352.0165 |  | X = Borah West flow |  | k= | -14684.2975 |  | X = Borah West flow
[7 empty] | I divided by 10 for | -0.554 X - 0.1 Y = -1468

## 4a vs 4b
| Y = Tot 4a flow |  |  | X = Tot 4b flow
| 400 |  |  | 628
| 800 |  |  | 200
| 400 |  |  | -428
|  | m = | -0.93458
-1.07
mX+k=Y
| or mX-Y=K |  | -0.935 X - Y = -987 |  | or | X + 1.07Y = 987
where
Solving the | -986.9159 |  | Y = Tot 4a flow
constant | -986.9159 |  | X = Tot 4b flow

## Others
Total flow on Tot 2a, Tot 2b, and Tot 2c
South to North |  | 1600
North to South |  | 1570
Total Flow on Tot 2b1 and 2b2
South to North |  | 850
North to South |  | 780
Combined Maximum on PACI and PDCI
North to South |  | 7300
Combined Maximum on PACI and Alturas Project
North to South |  | 4800
North of John Day
Total | 8600

## Lines
ID | Name | LowLimit | HighLimit | FromBus_ID | CI_Bus_1.BusName | CI_Bus_1.Voltage | ToBus_ID | CI_Bus.BusName | CI_Bus.Voltage | Resistance | Reactance | RatingA | Coefficient
1 | ALBERTA - BRITISH COLUMBIA | -1200 | 1000 | 54150 | LANGDON2 | 500 | 50791 | CBK500 | 500 | 0.0029 | 0.0403 | 1000 | 1
1 | ALBERTA - BRITISH COLUMBIA | -1200 | 1000 | 50830 | FRO T274 | 138 | 54329 | POCATER7 | 138 | 0.03577 | 0.14577 | 190 | -1
1 | ALBERTA - BRITISH COLUMBIA | -1200 | 1000 | 54232 | COLEMAN7 | 138 | 50776 | NTL138 | 138 | 0.03477 | 0.0795 | 131.9 | 1
2 | ALBERTA - SASKATCHEWAN | -150 | 150 | 54700 | MCNEILL | 138 | 54233 | DOME EM7 | 138 | 0.00568 | 0.02168 | 167 | -1
3 | NORTHWEST - CANADA | -3150 | 2000 | 50822 | NLYPHS | 230 | 40145 | BOUNDARY | 230 | 0.00043 | 0.0036 | 505.9 | -1
3 | NORTHWEST - CANADA | -3150 | 2000 | 50194 | ING500 | 500 | 40323 | CUSTER W | 500 | 0.00033 | 0.0048 | 2664.8 | -1
3 | NORTHWEST - CANADA | -3150 | 2000 | 50194 | ING500 | 500 | 40323 | CUSTER W | 500 | 0.00034 | 0.00488 | 2599.8 | -1
4 | WEST OF CASCADES - NORTH | -10500 | 10500 | 40261 | COLUMBIA | 230 | 40303 | COVINGTN | 230 | 0.01705 | 0.16386 | 255 | 1
4 | WEST OF CASCADES - NORTH | -10500 | 10500 | 42312 | CASCADEP | 230 | 46831 | ROCKYRH1 | 230 | 0.00908 | 0.08346 | 419.1 | -1
4 | WEST OF CASCADES - NORTH | -10500 | 10500 | 40869 | RAVER | 500 | 40957 | SCHULTZ | 500 | 0.00103 | 0.02004 | 2061.1 | -1
4 | WEST OF CASCADES - NORTH | -10500 | 10500 | 40869 | RAVER | 500 | 40957 | SCHULTZ | 500 | 0.00119 | 0.0232 | 2243 | -1
4 | WEST OF CASCADES - NORTH | -10500 | 10500 | 40869 | RAVER | 500 | 40957 | SCHULTZ | 500 | 0.00063 | 0.00916 | 2728 | -1
4 | WEST OF CASCADES - NORTH | -10500 | 10500 | 40691 | MAPLE VL | 345 | 40891 | ROCKY RH | 345 | 0.0066 | 0.08617 | 627.4 | -1
4 | WEST OF CASCADES - NORTH | -10500 | 10500 | 40285 | COULEE | 300 | 40795 | OLYMPIA | 300 | 0.0207 | 0.20022 | 332.6 | 1
4 | WEST OF CASCADES - NORTH | -10500 | 10500 | 40233 | CHIEF JO | 500 | 40749 | MONROE | 500 | 0.00148 | 0.02882 | 2511.5 | 1
4 | WEST OF CASCADES - NORTH | -10500 | 10500 | 40225 | CHIEF J4 | 345 | 40994 | SNOHOMS4 | 345 | 0.00681 | 0.08826 | 627.4 | 1
4 | WEST OF CASCADES - NORTH | -10500 | 10500 | 40223 | CHIEF J3 | 345 | 40993 | SNOHOMS3 | 345 | 0.00681 | 0.08826 | 627.4 | 1
4 | WEST OF CASCADES - NORTH | -10500 | 10500 | 40381 | ECHOLAKE | 500 | 40957 | SCHULTZ | 500 | 0.00068 | 0.01057 | 2728 | -1
5 | WEST OF CASCADES - SOUTH | -7000 | 7000 | 40585 | JOHN DAY | 500 | 40699 | MARION | 500 | 0.00155 | 0.03054 | 2788.6 | 1
5 | WEST OF CASCADES - SOUTH | -7000 | 7000 | 41342 | BIGEDDY2 | 230 | 40213 | CHEMAWA | 230 | 0.02018 | 0.17463 | 346.6 | 1
5 | WEST OF CASCADES - SOUTH | -7000 | 7000 | 41343 | BIGEDDY3 | 230 | 43313 | MCLOUGLN | 230 | 0.00718 | 0.09369 | 416.3 | 1
5 | WEST OF CASCADES - SOUTH | -7000 | 7000 | 41341 | BIGEDDY1 | 230 | 40813 | PARKDALE | 230 | 0.0036 | 0.03518 | 255 | 1
5 | WEST OF CASCADES - SOUTH | -7000 | 7000 | 40809 | OSTRNDER | 500 | 41138 | WAUTOMA | 500 | 0.00195 | 0.03805 | 3031.1 | -1
5 | WEST OF CASCADES - SOUTH | -7000 | 7000 | 40155 | BUCKLEY | 500 | 40699 | MARION | 500 | 0.00083 | 0.02101 | 4182.9 | 1
5 | WEST OF CASCADES - SOUTH | -7000 | 7000 | 40039 | ALFALFA | 230 | 40141 | BONNVILE | 230 | 0.02455 | 0.16126 | 426.3 | 1
5 | WEST OF CASCADES - SOUTH | -7000 | 7000 | 40123 | BOARD T2 | 230 | 41352 | MCNRY S2 | 230 | 0.00275 | 0.02676 | 525.9 | -1
5 | WEST OF CASCADES - SOUTH | -7000 | 7000 | 40111 | BIG EDDY | 500 | 40809 | OSTRNDER | 500 | 0.0011 | 0.02143 | 909.3 | 1
5 | WEST OF CASCADES - SOUTH | -7000 | 7000 | 40061 | ASHE | 500 | 40699 | MARION | 500 | 0.00183 | 0.04705 | 3767.2 | 1
5 | WEST OF CASCADES - SOUTH | -7000 | 7000 | 40721 | MCNARY | 345 | 40901 | ROSS | 345 | 0.00893 | 0.11789 | 454.1 | 1
6 | WEST OF HATWAI | -9999 | 4000 | 40521 | HATWAI | 500 | 40679 | LOW GRAN | 500 | 0.00039 | 0.00736 | 2182.4 | 1
6 | WEST OF HATWAI | -9999 | 4000 | 40091 | BELL BPA | 500 | 40287 | COULEE | 500 | 0.00082 | 0.01747 | 3949.1 | 1
6 | WEST OF HATWAI | -9999 | 4000 | 48197 | LOLO | 230 | 48195 | LOLO | 115 | 0.00144 | 0.05592 | 144 | -1
6 | WEST OF HATWAI | -9999 | 4000 | 48197 | LOLO | 230 | 48195 | LOLO | 115 | 0.00195 | 0.0568 | 144 | -1
6 | WEST OF HATWAI | -9999 | 4000 | 45097 | DRYGULCH | 69 | 48113 | DRYGULCH | 115 | 0.0347 | 0.796 | 20 | -1
6 | WEST OF HATWAI | -9999 | 4000 | 48255 | N LEWIST | 230 | 48451 | WALA AVA | 230 | 0.00567 | 0.05175 | 365.7 | 1
6 | WEST OF HATWAI | -9999 | 4000 | 48187 | LIND | 115 | 48375 | ROXBORO | 115 | 0.04507 | 0.06947 | 53 | 1
6 | WEST OF HATWAI | -9999 | 4000 | 48463 | WEST | 230 | 41276 | WESTBPA2 | 230 | 0.00032 | 0.00285 | 480 | 1
6 | WEST OF HATWAI | -9999 | 4000 | 40519 | HATWAI | 230 | 48197 | LOLO | 230 | 0.00132 | 0.01207 | 429 | 1
6 | WEST OF HATWAI | -9999 | 4000 | 40239 | CLARKSTN | 115 | 48253 | N LEWIST | 115 | 0.00703 | 0.02202 | 131.5 | -1
6 | WEST OF HATWAI | -9999 | 4000 | 40090 | BELL SO | 230 | 41356 | COULEES1 | 230 | 0.01296 | 0.12104 | 557.7 | 1
6 | WEST OF HATWAI | -9999 | 4000 | 40088 | BELL MI | 230 | 41358 | COULEES3 | 230 | 0.0129 | 0.12576 | 569.7 | 1
6 | WEST OF HATWAI | -9999 | 4000 | 40087 | BELL BPA | 115 | 41015 | SPRNGHIL | 115 | 0.01384 | 0.0597 | 138.6 | 1
6 | WEST OF HATWAI | -9999 | 4000 | 48147 | HARRNGTN | 115 | 48295 | ODESSA | 115 | 0.0993 | 0.153 | 53 | 1
8 | MONTANA - NORTHWEST | -1350 | 2200 | 62004 | ANACOND | 230 | 40457 | GARRISON | 230 | 0.00472 | 0.04327 | 478 | 1
8 | MONTANA - NORTHWEST | -1350 | 2200 | 40457 | GARRISON | 230 | 62072 | OVANDO | 230 | 0.00506 | 0.0464 | 478 | -1
8 | MONTANA - NORTHWEST | -1350 | 2200 | 62009 | RATTLE S | 161 | 40867 | RATTLE S | 230 | 0 | 0.0403 | 200 | 1
8 | MONTANA - NORTHWEST | -1350 | 2200 | 48051 | BURKE | 115 | 48055 | BURKAVAB | 115 | 0.00546 | 0.02201 | 73.9 | -1
8 | MONTANA - NORTHWEST | -1350 | 2200 | 48051 | BURKE | 115 | 48053 | BURKAVAA | 115 | 0.00545 | 0.02196 | 73.9 | -1
8 | MONTANA - NORTHWEST | -1350 | 2200 | 40391 | ELMO | 115 | 62066 | KERR | 115 | 0.05449 | 0.08542 | 83.7 | -1
8 | MONTANA - NORTHWEST | -1350 | 2200 | 62004 | ANACOND | 230 | 40457 | GARRISON | 230 | 0.00723 | 0.04655 | 358.5 | 1
8 | MONTANA - NORTHWEST | -1350 | 2200 | 40453 | GAR2EAST | 500 | 40459 | GARRISON | 500 | 0 | -0.0158 | 1732.1 | 1
8 | MONTANA - NORTHWEST | -1350 | 2200 | 40451 | GAR1EAST | 500 | 40459 | GARRISON | 500 | 0 | -0.0158 | 1732.1 | 1
8 | MONTANA - NORTHWEST | -1350 | 2200 | 40551 | HOT SPR | 230 | 62072 | OVANDO | 230 | 0.01392 | 0.12768 | 478 | -1
9 | WEST OF BROADVIEW | -9999 | 2573 | 62046 | BROADVU | 500 | 62012 | TOWN2 | 500 | 0.00151 | 0.02547 | 3152.3 | 1
9 | WEST OF BROADVIEW | -9999 | 2573 | 62046 | BROADVU | 500 | 62013 | TOWN1 | 500 | 0.00151 | 0.02547 | 3152.3 | 1
9 | WEST OF BROADVIEW | -9999 | 2573 | 62058 | SHOREYRD | 230 | 62019 | WILSALL | 230 | 0.01496 | 0.13737 | 478 | 1
9 | WEST OF BROADVIEW | -9999 | 2573 | 62223 | BROADVU | 230 | 62036 | JUDITHGP | 230 | 0.01134 | 0.10259 | 478 | 1
9 | WEST OF BROADVIEW | -9999 | 2573 | 62205 | COLRPLJE | 161 | 62109 | ALKALI | 161 | 0.02343 | 0.09739 | 203.6 | -1
9 | WEST OF BROADVIEW | -9999 | 2573 | 62089 | BROADVU | 100 | 62223 | BROADVU | 230 | 0 | 0.08267 | 100 | -1
9 | WEST OF BROADVIEW | -9999 | 2573 | 62223 | BROADVU | 230 | 62089 | BROADVU | 100 | 0 | 0.0845 | 100 | 1
10 | WEST OF COLSTRIP | -9999 | 2598 | 62060 | COLSTRP | 230 | 62051 | HARDIN | 230 | 0.0078 | 0.07161 | 478 | 1
10 | WEST OF COLSTRIP | -9999 | 2598 | 62081 | COLSTRP | 115 | 62210 | ARMELLCR | 115 | 0.00809 | 0.02026 | 106 | 1
10 | WEST OF COLSTRIP | -9999 | 2598 | 62057 | COLSTRP | 500 | 62053 | BROADV&2 | 500 | 0.00132 | 0.02306 | 3152.3 | 1
10 | WEST OF COLSTRIP | -9999 | 2598 | 62057 | COLSTRP | 500 | 62054 | BROADV&1 | 500 | 0.00128 | 0.02244 | 3152.3 | 1
11 | WEST OF CROSSOVER | -9999 | 2598 | 62057 | COLSTRP | 500 | 62053 | BROADV&2 | 500 | 0.00132 | 0.02306 | 3152.3 | 1
11 | WEST OF CROSSOVER | -9999 | 2598 | 62057 | COLSTRP | 500 | 62054 | BROADV&1 | 500 | 0.00128 | 0.02244 | 3152.3 | 1
11 | WEST OF CROSSOVER | -9999 | 2598 | 62056 | HUNTLEY | 230 | 63002 | CRSOVRUM | 230 | 0.00365 | 0.03355 | 478 | -1
14 | IDAHO - NORTHWEST | -1200 | 2400 | 61826 | HINES | 115 | 40507 | HARNEY | 115 | 0.00642 | 0.02025 | 117.5 | 1
14 | IDAHO - NORTHWEST | -1200 | 2400 | 45029 | BURNS | 500 | 60240 | MIDPOINT | 500 | 0.00264 | 0.02689 | 1500 | -1
14 | IDAHO - NORTHWEST | -1200 | 2400 | 60150 | HELLSCYN | 230 | 45103 | ENTERPRS | 230 | 0.0058 | 0.0545 | 478 | 1
14 | IDAHO - NORTHWEST | -1200 | 2400 | 48197 | LOLO | 230 | 60278 | IMNAHA | 230 | 0.01012 | 0.09253 | 366.5 | -1
14 | IDAHO - NORTHWEST | -1200 | 2400 | 60192 | LADD | 230 | 40621 | LAGRANDE | 230 | 0.00082 | 0.0353 | 300 | 1
15 | MIDWAY - LOS BANOS | -9999 | 3900 | 30790 | PANOCHE | 230 | 30900 | GATES | 230 | 0.01084 | 0.06186 | 296 | -1
15 | MIDWAY - LOS BANOS | -9999 | 3900 | 30880 | HENTAP2 | 230 | 30900 | GATES | 230 | 0.00261 | 0.02028 | 637.4 | -1
15 | MIDWAY - LOS BANOS | -9999 | 3900 | 30879 | HENTAP1 | 230 | 30900 | GATES | 230 | 0.00261 | 0.02028 | 637.4 | -1
15 | MIDWAY - LOS BANOS | -9999 | 3900 | 30050 | LOSBANOS | 500 | 30055 | GATES | 500 | 0.0008 | 0.00896 | 2146 | -1
15 | MIDWAY - LOS BANOS | -9999 | 3900 | 30790 | PANOCHE | 230 | 30900 | GATES | 230 | 0.01084 | 0.06186 | 296 | -1
15 | MIDWAY - LOS BANOS | -9999 | 3900 | 30050 | LOSBANOS | 500 | 30060 | MIDWAY | 500 | 0.0015 | 0.01446 | 2146 | -1
16 | IDAHO - SIERRA | -360 | 500 | 60235 | MIDPOINT | 345 | 64061 | IDAHO-NV | 345 | 0.0037 | 0.0385 | 1075.6 | 1
17 | BORAH WEST | -9999 | 2307 | 60060 | BORAH | 345 | 60005 | ADEL TAP | 345 | 0.0025 | 0.02 | 1015.9 | 1
17 | BORAH WEST | -9999 | 2307 | 60060 | BORAH | 345 | 60006 | ADELAIDE | 345 | 0.0022 | 0.0185 | 1015.9 | 1
17 | BORAH WEST | -9999 | 2307 | 60020 | AMFLS | 138 | 60295 | PLST VLY | 138 | 0.00682 | 0.04056 | 203.4 | 1
17 | BORAH WEST | -9999 | 2307 | 60020 | AMFLS | 138 | 61900 | RAFT RVR | 138 | 0.0149 | 0.0778 | 203.2 | 1
17 | BORAH WEST | -9999 | 2307 | 60235 | MIDPOINT | 345 | 60190 | KINPORT | 345 | 0.0026 | 0.03668 | 1075.6 | -1
18 | IDAHO - MONTANA | -337 | 337 | 62084 | DILLON S | 161 | 65155 | BIGGRASS | 161 | 0.0964 | 0.2914 | 164.5 | -1
18 | IDAHO - MONTANA | -337 | 337 | 62030 | PTRSNFLT | 230 | 65025 | AMPS | 230 | 0.01174 | 0.10827 | 478 | -1
19 | BRIDGER WEST | -9999 | 2200 | 60085 | BRIDGER | 345 | 65665 | GOSHEN | 345 | 0.0068 | 0.0574 | 892.2 | 1
19 | BRIDGER WEST | -9999 | 2200 | 60085 | BRIDGER | 345 | 60060 | BORAH | 345 | 0.0079 | 0.0647 | 892.2 | 1
19 | BRIDGER WEST | -9999 | 2200 | 60085 | BRIDGER | 345 | 60190 | KINPORT | 345 | 0.0077 | 0.0624 | 892.2 | 1
20 | PATH C | -1000 | 1000 | 65920 | MALAD | 138 | 60020 | AMFLS | 138 | 0.0755 | 0.2422 | 129.1 | 1
20 | PATH C | -1000 | 1000 | 65135 | BENLOMND | 345 | 60060 | BORAH | 345 | 0.0062 | 0.0679 | 1165.2 | 1
20 | PATH C | -1000 | 1000 | 66565 | TREASTON | 230 | 60073 | BRADY | 230 | 0.0163 | 0.1012 | 362.5 | 1
20 | PATH C | -1000 | 1000 | 65560 | FISHCREK | 161 | 65670 | GOSHEN | 161 | 0.0428 | 0.1312 | 148.1 | 1
21 | ARIZONA - CALIFORNIA | -9999 | 5700 | 15021 | PALOVRDE | 500 | 24801 | DEVERS | 500 | 0.0022 | 0.0303 | 1645.5 | 1
21 | ARIZONA - CALIFORNIA | -9999 | 5700 | 19053 | LIBERTY | 345 | 19315 | PEACOCK | 345 | 0.00563 | 0.03589 | 508 | 1
21 | ARIZONA - CALIFORNIA | -9999 | 5700 | 19042 | PARKER | 230 | 19204 | HARCUVAR | 230 | 0.0062 | 0.0659 | 239 | -1
21 | ARIZONA - CALIFORNIA | -9999 | 5700 | 15090 | HASSYAMP | 500 | 22536 | N.GILA | 500 | 0.00115 | 0.01354 | 1212.4 | 1
21 | ARIZONA - CALIFORNIA | -9999 | 5700 | 19042 | PARKER | 230 | 14209 | EAGLEYE | 230 | 0.0083 | 0.0879 | 239 | -1
21 | ARIZONA - CALIFORNIA | -9999 | 5700 | 14003 | NAVAJO | 500 | 26123 | CRYSTAL | 500 | 0.0019 | 0.01302 | 1411.6 | 1
21 | ARIZONA - CALIFORNIA | -9999 | 5700 | 14002 | MOENKOPI | 500 | 24042 | ELDORDO | 500 | 0.002 | 0.0153 | 1645.4 | 1
21 | ARIZONA - CALIFORNIA | -9999 | 5700 | 19056 | MCCONICO | 230 | 19022 | DAVIS | 230 | 0.0062 | 0.0429 | 450 | 1
22 | SOUTHWEST OF FOUR CORNERS | -9999 | 2325 | 14001 | FOURCORN | 500 | 14002 | MOENKOPI | 500 | 0.00177 | 0.04169 | 1645 | 1
22 | SOUTHWEST OF FOUR CORNERS | -9999 | 2325 | 14101 | FOURCORN | 345 | 14100 | CHOLLA | 345 | 0.00855 | 0.06146 | 687 | 1
22 | SOUTHWEST OF FOUR CORNERS | -9999 | 2325 | 14101 | FOURCORN | 345 | 14100 | CHOLLA | 345 | 0.0086 | 0.06198 | 687 | 1
23 | FOUR CORNERS 345_500 | -840 | 840 | 14101 | FOURCORN | 345 | 14525 | FOURC1AA | 100 | 3.5e-05 | -0.003755 | 840 | 1
24 | PG&E - SPP | -150 | 160 | 30993 | SUMMIT | 60 | 64109 | SUMMIT 3 | 60 | 0 | 0.0006 | 123 | 1
24 | PG&E - SPP | -150 | 160 | 64228 | SUMMIT 1 | 115 | 32218 | DRUM | 115 | 0.035 | 0.1189 | 123 | -1
24 | PG&E - SPP | -150 | 160 | 64229 | SUMMIT 2 | 115 | 32218 | DRUM | 115 | 0.0347 | 0.1179 | 123 | -1
25 | PACIFICORP_PG&E 115 KV INTERCON. | -30 | 80 | 10026 | BACA | 46 | 10000 | 12ST_TAP | 46 | 0.0216 | 0.0316 | 27.1 | 1
25 | PACIFICORP_PG&E 115 KV INTERCON. | -30 | 80 | 10356 | VALENCIA | 46 | 10000 | 12ST_TAP | 46 | 0.0239 | 0.0375 | 23.9 | -1
25 | PACIFICORP_PG&E 115 KV INTERCON. | -30 | 80 | 45087 | DELTA | 115 | 31468 | CASCADE | 115 | 0.0416 | 0.1311 | 83 | 1
26 | NORTHERN - SOUTHERN CALIFORNIA | -3000 | 3400 | 30060 | MIDWAY | 500 | 24156 | VINCENT | 500 | 0.0011 | 0.0081 | 1848.1 | 1
26 | NORTHERN - SOUTHERN CALIFORNIA | -3000 | 3400 | 30060 | MIDWAY | 500 | 24156 | VINCENT | 500 | 0.00112 | 0.00662 | 1848.1 | 1
26 | NORTHERN - SOUTHERN CALIFORNIA | -3000 | 3400 | 30060 | MIDWAY | 500 | 24156 | VINCENT | 500 | 0.0011 | 0.0082 | 1848.1 | 1
27 | IPP DC LINE | -1400 | 1920 | 26043 | INTERMT | 345 | 26114 | INTERMTX | 345 | 0 | 0.0003 | 2500 | 1
28 | INTERMOUNTAIN - MONA 345 KV | -1200 | 1400 | 26043 | INTERMT | 345 | 65995 | MONA | 345 | 0.0018 | 0.0245 | 600 | 1
28 | INTERMOUNTAIN - MONA 345 KV | -1200 | 1400 | 26043 | INTERMT | 345 | 65995 | MONA | 345 | 0.0018 | 0.0245 | 600 | 1
29 | INTERMOUNTAIN - GONDER 230 KV | -9999 | 250 | 26041 | INTERMT | 230 | 64056 | GONDER | 230 | 0.02929 | 0.20832 | 402 | 1
30 | TOT 1A | -9999 | 650 | 79005 | BEARS | 345 | 65193 | BONANZA | 345 | 0.0036 | 0.0541 | 650 | 1
30 | TOT 1A | -9999 | 650 | 79046 | MEEKER | 138 | 66278 | RANGELY | 138 | 0.06061 | 0.22103 | 115 | 1
30 | TOT 1A | -9999 | 650 | 79001 | ARTESIA | 138 | 79038 | HAYDEN | 138 | 0.1015 | 0.4303 | 90 | -1
31 | TOT 2A | -9999 | 690 | 79061 | SHIP PS | 230 | 79063 | SHIPROCK | 230 | 0 | 0.044 | 400 | 1
31 | TOT 2A | -9999 | 690 | 79060 | SANJN PS | 345 | 79072 | HESPERUS | 345 | 0.00149 | 0.02338 | 1619 | -1
31 | TOT 2A | -9999 | 690 | 79105 | GLADETAP | 115 | 79260 | ELPASOTP | 115 | 0.01502 | 0.04577 | 85 | -1
32 | PAVANT, INTRMTN - GONDER 230 KV | -235 | 440 | 26041 | INTERMT | 230 | 64056 | GONDER | 230 | 0.02929 | 0.20832 | 402 | 1
32 | PAVANT, INTRMTN - GONDER 230 KV | -235 | 440 | 64056 | GONDER | 230 | 64124 | UTAH-NEV | 230 | 0.01304 | 0.07896 | 215 | -1
33 | BONANZA WEST | -9999 | 785 | 65193 | BONANZA | 345 | 65995 | MONA | 345 | 0.0048 | 0.0821 | 650 | 1
33 | BONANZA WEST | -9999 | 785 | 65280 | CARBON | 138 | 66183 | PANTHER | 138 | 0.00132 | 0.00397 | 136 | -1
34 | TOT 2B | -850 | 780 | 66235 | PINTO PS | 345 | 14101 | FOURCORN | 345 | 0.0056 | 0.0511 | 1026 | 1
34 | TOT 2B | -850 | 780 | 66355 | SIGURDPS | 230 | 79031 | GLENCANY | 230 | 0.033 | 0.2427 | 386.8 | 1
35 | TOT 2C | -300 | 300 | 18002 | HA PS | 345 | 66280 | REDBUTTE | 345 | 0.00492 | 0.05033 | 300 | -1
36 | TOT 3 | -9999 | 1424 | 73150 | PEETZ | 115 | 73179 | SIDNEY | 115 | 0.0325 | 0.0963 | 109 | -1
36 | TOT 3 | -9999 | 1424 | 73009 | ARCHER | 230 | 73011 | AULT | 230 | 0.009 | 0.0653 | 462 | 1
36 | TOT 3 | -9999 | 1424 | 73012 | AULT | 345 | 73108 | LAR.RIVR | 345 | 0.00388 | 0.05428 | 896 | -1
36 | TOT 3 | -9999 | 1424 | 73043 | CHEYENNE | 115 | 73504 | PONNEQUI | 115 | 0.01545 | 0.04714 | 110 | 1
36 | TOT 3 | -9999 | 1424 | 73108 | LAR.RIVR | 345 | 73193 | STORY | 345 | 0.00543 | 0.08428 | 956.1 | 1
36 | TOT 3 | -9999 | 1424 | 73143 | N.YUMA | 230 | 73180 | SIDNEY | 230 | 0.0154 | 0.1175 | 566 | -1
37 | TOT 4A | -9999 | 810 | 66305 | RIVERTON | 230 | 66740 | WYOPO | 230 | 0.0032 | 0.0288 | 423.9 | 1
37 | TOT 4A | -9999 | 810 | 65420 | DAVEJOHN | 230 | 65460 | DIFICULT | 230 | 0.0071 | 0.0637 | 423.9 | 1
37 | TOT 4A | -9999 | 810 | 66020 | MUSTANG | 230 | 66410 | SPENCE | 230 | 0.0122 | 0.1117 | 423.9 | -1
38 | TOT 4B | -9999 | 680 | 65095 | BADWATER | 230 | 66410 | SPENCE | 230 | 0.0102 | 0.1125 | 478.1 | -1
38 | TOT 4B | -9999 | 680 | 65293 | CARR DRA | 230 | 66725 | WYODAK | 230 | 0.00545 | 0.04885 | 423.9 | -1
38 | TOT 4B | -9999 | 680 | 65300 | CASPERPP | 230 | 65955 | MIDWEST | 230 | 0.01 | 0.0575 | 327.1 | 1
38 | TOT 4B | -9999 | 680 | 66305 | RIVERTON | 230 | 66535 | THERMOPL | 230 | 0.0091 | 0.0733 | 358.9 | 1
38 | TOT 4B | -9999 | 680 | 73004 | ALCOVA | 115 | 73162 | RADERVIL | 115 | 0.093 | 0.2658 | 80 | 1
38 | TOT 4B | -9999 | 680 | 73170 | RIVERTON | 115 | 66305 | RIVERTON | 230 | 0.0031 | 0.0948 | 100 | -1
39 | TOT 5 | -9999 | 1675 | 73009 | ARCHER | 230 | 79039 | HAYDEN | 230 | 0.0219 | 0.2367 | 320 | -1
39 | TOT 5 | -9999 | 1675 | 79033 | GOREPASS | 230 | 73072 | GOREPASS | 138 | 0.0012 | 0.0595 | 150 | 1
39 | TOT 5 | -9999 | 1675 | 79021 | CURECANT | 230 | 79054 | PONCHABR | 230 | 0.01179 | 0.1255 | 442 | 1
39 | TOT 5 | -9999 | 1675 | 73072 | GOREPASS | 138 | 79038 | HAYDEN | 138 | 0.0823 | 0.2446 | 96 | -1
39 | TOT 5 | -9999 | 1675 | 73012 | AULT | 345 | 79014 | CRAIG | 345 | 0.0061 | 0.0927 | 956 | -1
39 | TOT 5 | -9999 | 1675 | 70274 | MALTA | 230 | 79004 | BASALT | 230 | 0.00407 | 0.05 | 989.6 | -1
39 | TOT 5 | -9999 | 1675 | 70358 | RIFLE PS | 230 | 70232 | HOPKINS | 230 | 0.0057 | 0.041 | 373.3 | 1
39 | TOT 5 | -9999 | 1675 | 70053 | BLUERIVR | 230 | 79033 | GOREPASS | 230 | 0.0022 | 0.0343 | 859.7 | -1
39 | TOT 5 | -9999 | 1675 | 70231 | HOPKINS | 115 | 79003 | BASALT | 115 | 0.05031 | 0.07266 | 66.9 | -1
39 | TOT 5 | -9999 | 1675 | 70327 | PONCHA | 115 | 79037 | GUNNISON | 115 | 0.1037 | 0.3212 | 113 | -1
40 | TOT 7 | -9999 | 890 | 70471 | WELD PS | 230 | 70410 | ST.VRAIN | 230 | 0.00297 | 0.02356 | 500 | 1
40 | TOT 7 | -9999 | 890 | 70410 | ST.VRAIN | 230 | 73116 | LONGPEAK | 230 | 0.0018 | 0.0142 | 377.7 | -1
40 | TOT 7 | -9999 | 890 | 73011 | AULT | 230 | 70474 | WINDSOR | 230 | 0.0018 | 0.0167 | 495 | 1
41 | SYLMAR - SCE | -1200 | 1200 | 26094 | SYLMARLA | 230 | 24147 | SYLMAR S | 230 | 0 | 0.0138 | 600 | 1
41 | SYLMAR - SCE | -1200 | 1200 | 26094 | SYLMARLA | 230 | 24147 | SYLMAR S | 230 | 0 | 0.0134 | 600 | 1
42 | IID - SCE | -9999 | 600 | 21007 | COACHELV | 230 | 24804 | DEVERS | 230 | 0.0064 | 0.0493 | 392.8 | 1
42 | IID - SCE | -9999 | 600 | 21076 | RAMON | 230 | 24806 | MIRAGE | 230 | 3e-05 | 0.00032 | 392.8 | 1
43 | NORTH OF SAN ONOFRE | -9999 | 2440 | 24131 | S.ONOFRE | 230 | 24134 | SANTIAGO | 230 | 0.00163 | 0.02947 | 1195 | 1
43 | NORTH OF SAN ONOFRE | -9999 | 2440 | 24131 | S.ONOFRE | 230 | 24137 | SERRANO | 230 | 0.00228 | 0.04132 | 1195 | 1
43 | NORTH OF SAN ONOFRE | -9999 | 2440 | 25654 | VIEJOSC | 230 | 24131 | S.ONOFRE | 230 | 0.00114 | 0.02066 | 1287 | -1
43 | NORTH OF SAN ONOFRE | -9999 | 2440 | 24131 | S.ONOFRE | 230 | 24134 | SANTIAGO | 230 | 0.00163 | 0.02947 | 1195 | 1
44 | SOUTH OF SAN ONOFRE | -200 | 1900 | 22716 | SANLUSRY | 230 | 24131 | S.ONOFRE | 230 | 0.00145 | 0.0131 | 796.7 | -1
44 | SOUTH OF SAN ONOFRE | -200 | 1900 | 22716 | SANLUSRY | 230 | 24131 | S.ONOFRE | 230 | 0.00155 | 0.0181 | 796.7 | -1
44 | SOUTH OF SAN ONOFRE | -200 | 1900 | 22716 | SANLUSRY | 230 | 24131 | S.ONOFRE | 230 | 0.0016 | 0.0187 | 796.7 | -1
44 | SOUTH OF SAN ONOFRE | -200 | 1900 | 22844 | TALEGA | 230 | 24131 | S.ONOFRE | 230 | 0.0007 | 0.0072 | 796.7 | -1
44 | SOUTH OF SAN ONOFRE | -200 | 1900 | 22844 | TALEGA | 230 | 24131 | S.ONOFRE | 230 | 0.0007 | 0.0072 | 796.7 | -1
45 | CA INDEPENDENT - MEXICO (CFE) | -800 | 408 | 22356 | IMPRLVLY | 230 | 20118 | ROA-230 | 230 | 0.001 | 0.00991 | 796.7 | 1
45 | CA INDEPENDENT - MEXICO (CFE) | -800 | 408 | 22609 | OTAYMESA | 230 | 20149 | TJI-230 | 230 | 0.0005 | 0.0052 | 796.7 | 1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 25406 | J.HINDS | 230 | 24806 | MIRAGE | 230 | 0.0136 | 0.0731 | 357 | 1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 26051 | MEAD | 287 | 26104 | VICTORVL | 287 | 0.02443 | 0.17602 | 419.1 | 1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 26048 | MCCULLGH | 500 | 26105 | VICTORVL | 500 | 0.00157 | 0.0252 | 1385.6 | 1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 15021 | PALOVRDE | 500 | 24801 | DEVERS | 500 | 0.0022 | 0.0303 | 1645.5 | 1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 26044 | MARKETPL | 500 | 26003 | ADELANTO | 500 | 0.00115 | 0.02256 | 1636 | 1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 24086 | LUGO | 500 | 24097 | MOHAVE | 500 | 0.0017 | 0.01253 | 1386 | -1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 24042 | ELDORDO | 500 | 24086 | LUGO | 500 | 0.0017 | 0.0128 | 1386 | 1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 24627 | CIMA | 230 | 24041 | ELDORDO | 230 | 0.014 | 0.0764 | 288.8 | -1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 24219 | PISGAH | 230 | 24041 | ELDORDO | 230 | 0.031 | 0.1689 | 289 | -1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 22536 | N.GILA | 500 | 22360 | IMPRLVLY | 500 | 0.00075 | 0.00933 | 1212.4 | 1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 21076 | RAMON | 230 | 24806 | MIRAGE | 230 | 3e-05 | 0.00032 | 392.8 | 1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 22356 | IMPRLVLY | 230 | 21025 | ELCENTRO | 230 | 0.00379 | 0.025 | 370.1 | -1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 21007 | COACHELV | 230 | 24804 | DEVERS | 230 | 0.0064 | 0.0493 | 392.8 | 1
46 | WEST OF COLORADO RIVER (WOR) | -10118 | 10118 | 26048 | MCCULLGH | 500 | 26105 | VICTORVL | 500 | 0.00157 | 0.0252 | 1385.6 | 1
47 | SOUTHERN NEW MEXICO (NM1) | -1048 | 1048 | 10369 | WESTMESA | 345 | 11014 | ARR___PS | 345 | 0.0102 | 0.0999 | 717 | 1
47 | SOUTHERN NEW MEXICO (NM1) | -1048 | 1048 | 11080 | HIDALGO | 345 | 16101 | GREENLEE | 345 | 0.00332 | 0.03036 | 717.1 | -1
47 | SOUTHERN NEW MEXICO (NM1) | -1048 | 1048 | 16104 | SPRINGR | 345 | 11093 | LUNA | 345 | 0.0104 | 0.0809 | 657 | 1
47 | SOUTHERN NEW MEXICO (NM1) | -1048 | 1048 | 12007 | BELEN_PG | 115 | 12086 | WESTMS_P | 115 | 0.0703 | 0.2086 | 78.1 | -1
48 | NORTHERN NEW MEXICO (NM2) | -1450 | 1665 | 14101 | FOURCORN | 345 | 10390 | RIOPUERC | 345 | 0.0068 | 0.0419 | 1195.1 | 1
48 | NORTHERN NEW MEXICO (NM2) | -1450 | 1665 | 10011 | AMBROSIA | 230 | 10041 | BISTI | 230 | 0.0132 | 0.1035 | 318.7 | -1
48 | NORTHERN NEW MEXICO (NM2) | -1450 | 1665 | 10292 | SAN_JUAN | 345 | 10390 | RIOPUERC | 345 | 0.0068 | 0.04175 | 1195.1 | 1
48 | NORTHERN NEW MEXICO (NM2) | -1450 | 1665 | 10369 | WESTMESA | 345 | 11014 | ARR___PS | 345 | 0.0102 | 0.0999 | 717 | -1
48 | NORTHERN NEW MEXICO (NM2) | -1450 | 1665 | 12008 | BERNARDO | 115 | 12007 | BELEN_PG | 115 | 0.0253 | 0.075 | 78.1 | 1
48 | NORTHERN NEW MEXICO (NM2) | -1450 | 1665 | 16102 | MCKINLEY | 345 | 10382 | YAHTAHEY | 115 | 0.0012 | 0.054 | 200 | 1
48 | NORTHERN NEW MEXICO (NM2) | -1450 | 1665 | 10292 | SAN_JUAN | 345 | 10392 | OJO_EAST | 345 | 0.0042 | 0.0422 | 1195.1 | 1
49 | EAST OF COLORADO RIVER (EOR) | -9999 | 7550 | 14002 | MOENKOPI | 500 | 24042 | ELDORDO | 500 | 0.002 | 0.0153 | 1645.4 | 1
49 | EAST OF COLORADO RIVER (EOR) | -9999 | 7550 | 14003 | NAVAJO | 500 | 26123 | CRYSTAL | 500 | 0.0019 | 0.01302 | 1411.6 | 1
49 | EAST OF COLORADO RIVER (EOR) | -9999 | 7550 | 15021 | PALOVRDE | 500 | 24801 | DEVERS | 500 | 0.0022 | 0.0303 | 1645.5 | 1
49 | EAST OF COLORADO RIVER (EOR) | -9999 | 7550 | 19107 | BIGSANDY | 500 | 15034 | PERKINS | 500 | 0.00081 | 0.00507 | 1270.8 | -1
49 | EAST OF COLORADO RIVER (EOR) | -9999 | 7550 | 15090 | HASSYAMP | 500 | 22536 | N.GILA | 500 | 0.00115 | 0.01354 | 1212.4 | 1
49 | EAST OF COLORADO RIVER (EOR) | -9999 | 7550 | 19053 | LIBERTY | 345 | 19315 | PEACOCK | 345 | 0.00563 | 0.03589 | 508 | 1
50 | CHOLLA - PINNACLE PEAK | -9999 | 1200 | 14100 | CHOLLA | 345 | 14102 | PNPKAPS | 345 | 0.00361 | 0.06746 | 600 | 1
50 | CHOLLA - PINNACLE PEAK | -9999 | 1200 | 14100 | CHOLLA | 345 | 14103 | PRECHCYN | 345 | 0.00364 | 0.03474 | 600 | 1
51 | SOUTHERN NAVAJO | -9999 | 2264 | 14003 | NAVAJO | 500 | 14011 | TABLMESA | 500 | 0.00274 | 0.03208 | 984.7 | 1
51 | SOUTHERN NAVAJO | -9999 | 2264 | 14002 | MOENKOPI | 500 | 14006 | YAVAPAI | 500 | 0.00098 | 0.01659 | 1385 | 1
52 | SILVER PEAK - CONTROL 55 KV | -17 | 17 | 64096 | SLVR PS | 60 | 64230 | NEVBD501 | 60 | 0.54379 | 0.77872 | 25 | 1
52 | SILVER PEAK - CONTROL 55 KV | -17 | 17 | 64096 | SLVR PS | 60 | 64231 | NEVBD502 | 60 | 0.61847 | 0.92984 | 25 | 1
53 | BILLINGS - YELLOWTAIL | -400 | 400 | 66750 | YELOWTLP | 230 | 62045 | BLGS PHA | 230 | 0.0072 | 0.0655 | 478 | -1
53 | BILLINGS - YELLOWTAIL | -400 | 400 | 62062 | RIMROCK | 161 | 62061 | RMRK PHA | 161 | 0 | 0.0667 | 100 | 1
54 | CORONADO - SILVER KING - KYRENE | -9999 | 1100 | 15001 | CORONADO | 500 | 14000 | CHOLLA | 500 | 0.00074 | 0.01743 | 1732.1 | 1
54 | CORONADO - SILVER KING - KYRENE | -9999 | 1100 | 15001 | CORONADO | 500 | 15041 | SILVERKG | 500 | 0.00176 | 0.04189 | 1732 | 1
55 | BROWNLEE EAST | -9999 | 1750 | 60270 | OXBOW | 138 | 60220 | MCCALL | 138 | 0.05276 | 0.17032 | 141 | 1
55 | BROWNLEE EAST | -9999 | 1750 | 60045 | BOISEBCH | 230 | 60095 | BROWNLEE | 230 | 0.0202 | 0.0617 | 394.4 | -1
55 | BROWNLEE EAST | -9999 | 1750 | 60305 | QUARTZ | 138 | 61055 | NELSN TP | 138 | 0.03236 | 0.09807 | 141 | 1
55 | BROWNLEE EAST | -9999 | 1750 | 60045 | BOISEBCH | 230 | 60095 | BROWNLEE | 230 | 0.0197 | 0.064 | 394.4 | -1
55 | BROWNLEE EAST | -9999 | 1750 | 60095 | BROWNLEE | 230 | 60265 | ONTARIO | 230 | 0.00749 | 0.02192 | 569.7 | 1
55 | BROWNLEE EAST | -9999 | 1750 | 60045 | BOISEBCH | 230 | 60095 | BROWNLEE | 230 | 0.0197 | 0.064 | 394.4 | -1
55 | BROWNLEE EAST | -9999 | 1750 | 60045 | BOISEBCH | 230 | 60095 | BROWNLEE | 230 | 0.0202 | 0.0617 | 394.4 | -1
58 | ELDORADO - MEAD 230 KV LINES | -1140 | 1140 | 19012 | MEAD S | 230 | 24041 | ELDORDO | 230 | 0.0013 | 0.0165 | 988 | -1
58 | ELDORADO - MEAD 230 KV LINES | -1140 | 1140 | 19012 | MEAD S | 230 | 24041 | ELDORDO | 230 | 0.0013 | 0.0168 | 988 | -1
59 | EAGLE MTN 230_161 KV - BLYTHE 16 | -168 | 72 | 24017 | BLYTHESC | 161 | 24035 | EAGLEMTN | 161 | 0.0499 | 0.189 | 168.7 | -1
60 | INYO - CONTROL 115 KV TIE | -56 | 56 | 24723 | CONTROL | 115 | 24728 | INYO | 115 | 0.006 | 0.0196 | 194.2 | -1
61 | LUGO - VICTORVILLE 500 KV LINE | -900 | 2400 | 24086 | LUGO | 500 | 26105 | VICTORVL | 500 | 0.0001 | 0.0036 | 2400 | -1
62 | ELDORADO - MCCULLOUGH 500 KV | -2598 | 2598 | 24042 | ELDORDO | 500 | 26048 | MCCULLGH | 500 | 0 | 0.00055 | 2598 | 1
63 | PERKINS - MEAD - MARKETPLACE 500 | -9999 | 1300 | 19107 | BIGSANDY | 500 | 15034 | PERKINS | 500 | 0.00081 | 0.00507 | 1270.8 | -1
64 | MARKETPLACE - ADELANTO | -1200 | 1200 | 26044 | MARKETPL | 500 | 26003 | ADELANTO | 500 | 0.00115 | 0.02256 | 1636 | 1
65 | PACIFIC DC INTERTIE (PDCI) | -3100 | 3100 | 26099 | SYLMAR2 | 230 | 24147 | SYLMAR S | 230 | 0 | 0.0003 | 1100 | -1
65 | PACIFIC DC INTERTIE (PDCI) | -3100 | 3100 | 26098 | SYLMAR3 | 230 | 26094 | SYLMARLA | 230 | 0 | 0.0003 | 1600 | -1
65 | PACIFIC DC INTERTIE (PDCI) | -3100 | 3100 | 26100 | SYLMAR4 | 230 | 26094 | SYLMARLA | 230 | 0 | 0.0003 | 1600 | -1
65 | PACIFIC DC INTERTIE (PDCI) | -3100 | 3100 | 26097 | SYLMAR1 | 230 | 24147 | SYLMAR S | 230 | 0 | 0.0003 | 1100 | -1
66 | COI | -3675 | 4800 | 40687 | MALIN | 500 | 30005 | ROUND MT | 500 | 0.00103 | 0.00902 | 2338 | 1
66 | COI | -3675 | 4800 | 40687 | MALIN | 500 | 30005 | ROUND MT | 500 | 0.00107 | 0.00886 | 1559 | 1
66 | COI | -3675 | 4800 | 45035 | CAPTJACK | 500 | 30020 | OLINDA | 500 | 0.0011 | 0.0123 | 2310 | 1
66 | COI | -3675 | 4800 | 40537 | HIL TOP | 230 | 64058 | HIL TOP | 345 | 0.00196 | 0.0392 | 300 | 1
73 | NORTH OF JOHN DAY | -8600 | 8600 | 40499 | HANFORD | 500 | 41138 | WAUTOMA | 500 | 0.00022 | 0.00432 | 3031.1 | 1
73 | NORTH OF JOHN DAY | -8600 | 8600 | 40723 | MCNARY | 500 | 40990 | SMITHSHJ | 500 | 0.0003 | 0.00639 | 3949.1 | -1
73 | NORTH OF JOHN DAY | -8600 | 8600 | 40821 | PAUL | 500 | 40869 | RAVER | 500 | 0.00084 | 0.0159 | 2511.5 | -1
73 | NORTH OF JOHN DAY | -8600 | 8600 | 40061 | ASHE | 500 | 40699 | MARION | 500 | 0.00183 | 0.04705 | 3767.2 | 1
73 | NORTH OF JOHN DAY | -8600 | 8600 | 40499 | HANFORD | 500 | 41138 | WAUTOMA | 500 | 0.00022 | 0.00431 | 3031.1 | 1
73 | NORTH OF JOHN DAY | -8600 | 8600 | 40061 | ASHE | 500 | 40989 | SLATT | 500 | 0.00059 | 0.01516 | 3767.2 | 1
73 | NORTH OF JOHN DAY | -8600 | 8600 | 40723 | MCNARY | 500 | 40990 | SMITHSHJ | 500 | 0.00037 | 0.00707 | 3031.1 | -1
75 | MIDPOINT - SUMMER LAKE | -400 | 1500 | 45029 | BURNS | 500 | 60240 | MIDPOINT | 500 | 0.00264 | 0.02689 | 1500 | -1
76 | ALTURAS PROJECT | -300 | 300 | 40537 | HIL TOP | 230 | 64058 | HIL TOP | 345 | 0.00196 | 0.0392 | 300 | 1
77 | CRYSTAL - ALLEN | -9999 | 950 | 26123 | CRYSTAL | 500 | 18013 | CRSTL3PS | 230 | 0.00031 | 0.02083 | 672 | 1
77 | CRYSTAL - ALLEN | -9999 | 950 | 26123 | CRYSTAL | 500 | 18012 | CRSTL2PS | 230 | 0.00031 | 0.02083 | 672 | 1
78 | TOT 2B1 | -600 | 560 | 66235 | PINTO PS | 345 | 14101 | FOURCORN | 345 | 0.0056 | 0.0511 | 1026 | 1
79 | TOT 2B2 | -300 | 265 | 66355 | SIGURDPS | 230 | 79031 | GLENCANY | 230 | 0.033 | 0.2427 | 386.8 | 1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10265 | REEVES_1 | 115 | 10261 | REEVE_G1 | 13.8 | 0 | 0.13816 | 55 | -1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10368 | WESTMESA | 230 | 10370 | WESTMS_1 | 115 | 0.0007 | 0.0373 | 200 | 1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10368 | WESTMESA | 230 | 10371 | WESTMS_2 | 115 | 0.001 | 0.0368 | 200 | 1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10369 | WESTMESA | 345 | 10371 | WESTMS_2 | 115 | 0.0012 | 0.0265 | 400 | 1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10294 | SANDIA | 345 | 10296 | SANDIA_2 | 115 | 0.0005 | 0.0279 | 400 | 1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10266 | REEVES_2 | 115 | 10263 | REEVE_G3 | 13.8 | 0 | 0.10513 | 85 | -1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10265 | REEVES_1 | 115 | 10262 | REEVE_G2 | 13.8 | 0 | 0.13751 | 55 | -1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10245 | PERSON | 115 | 10246 | PERSONG1 | 18 | 0 | 0.0581 | 162 | -1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10370 | WESTMS_1 | 115 | 12086 | WESTMS_P | 115 | 0 | 0.0006 | 133.5 | -1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10198 | MARQUEZT | 115 | 10371 | WESTMS_2 | 115 | 0.0521 | 0.2076 | 120 | 1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10044 | BLCKRA_T | 115 | 10370 | WESTMS_1 | 115 | 0.01484 | 0.05915 | 119.5 | 1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10440 | ENCHNTED | 115 | 10024 | B-A | 115 | 0.0033 | 0.0243 | 156 | -1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10024 | B-A | 115 | 10315 | SIGNET_T | 115 | 0.0306 | 0.1222 | 127.5 | 1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10024 | B-A | 115 | 10221 | NO_BERN | 115 | 0.0053 | 0.0211 | 127 | 1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10369 | WESTMESA | 345 | 10370 | WESTMS_1 | 115 | 0.0012 | 0.0265 | 400 | 1
179 | Albuquerque Sum with caps | -9999 | 9999 | 10245 | PERSON | 115 | 10247 | PERSONG2 | 18 | 0 | 0.0581 | 162 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10371 | WESTMS_2 | 115 | 10284 | S.JOSEPH | 115 | 0.0006 | 0.007 | 322 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10245 | PERSON | 115 | 10246 | PERSONG1 | 18 | 0 | 0.0581 | 162 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10227 | NORTHPNM | 115 | 10228 | NORTH | 12.5 | 0 | 0.34167 | 44.8 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10370 | WESTMS_1 | 115 | 10282 | S._COORS | 115 | 0.0058 | 0.023 | 156 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10371 | WESTMS_2 | 115 | 10455 | VOLCANOT | 115 | 0.0047 | 0.0186 | 156 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10369 | WESTMESA | 345 | 10371 | WESTMS_2 | 115 | 0.0012 | 0.0265 | 400 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10245 | PERSON | 115 | 10247 | PERSONG2 | 18 | 0 | 0.0581 | 162 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10295 | SANDIA_1 | 115 | 10296 | SANDIA_2 | 115 | 0 | 0.0006 | 358.5 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10266 | REEVES_2 | 115 | 10264 | REEVES | 12.5 | 0 | 0.6233 | 20 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10370 | WESTMS_1 | 115 | 10374 | WESTMS_T | 115 | 0.00194 | 0.00769 | 156 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10254 | PRAGER | 46 | 10255 | PRAGER | 115 | 0.0044 | 0.1027 | 60 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10255 | PRAGER | 115 | 10256 | PRAGER | 12.5 | 0 | 0.6542 | 20 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10265 | REEVES_1 | 115 | 10261 | REEVE_G1 | 13.8 | 0 | 0.13816 | 55 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10266 | REEVES_2 | 115 | 10263 | REEVE_G3 | 13.8 | 0 | 0.10513 | 85 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10294 | SANDIA | 345 | 10296 | SANDIA_2 | 115 | 0.0005 | 0.0279 | 400 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10295 | SANDIA_1 | 115 | 10293 | SANDIA | 46 | 0.0068 | 0.17803 | 44 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10368 | WESTMESA | 230 | 10370 | WESTMS_1 | 115 | 0.0007 | 0.0373 | 200 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10368 | WESTMESA | 230 | 10371 | WESTMS_2 | 115 | 0.001 | 0.0368 | 200 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10369 | WESTMESA | 345 | 10370 | WESTMS_1 | 115 | 0.0012 | 0.0265 | 400 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10370 | WESTMS_1 | 115 | 12086 | WESTMS_P | 115 | 0 | 0.0006 | 133.5 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10265 | REEVES_1 | 115 | 10262 | REEVE_G2 | 13.8 | 0 | 0.13751 | 55 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10024 | B-A | 115 | 10315 | SIGNET_T | 115 | 0.0306 | 0.1222 | 127.5 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10266 | REEVES_2 | 115 | 10463 | ROY | 115 | 0.00074 | 0.00296 | 133 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10226 | NORTH | 46 | 10227 | NORTHPNM | 115 | 0.007 | 0.56615 | 9.4 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10024 | B-A | 115 | 10221 | NO_BERN | 115 | 0.0053 | 0.0211 | 127 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10440 | ENCHNTED | 115 | 10024 | B-A | 115 | 0.0033 | 0.0243 | 156 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10044 | BLCKRA_T | 115 | 10370 | WESTMS_1 | 115 | 0.01484 | 0.05915 | 119.5 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10265 | REEVES_1 | 115 | 10121 | HAWKINS# | 115 | 0.0011 | 0.0044 | 127 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10151 | JEFFRSNT | 115 | 10265 | REEVES_1 | 115 | 0.0005 | 0.002 | 131 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10295 | SANDIA_1 | 115 | 10154 | KAFB | 115 | 0.00221 | 0.00801 | 156 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10295 | SANDIA_1 | 115 | 10170 | LENKURT | 115 | 0.0031 | 0.0111 | 127 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10179 | LOSANGEL | 115 | 10265 | REEVES_1 | 115 | 0.00074 | 0.00291 | 156 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10255 | PRAGER | 115 | 10251 | PN-PL | 115 | 0.0003 | 0.0035 | 179 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10198 | MARQUEZT | 115 | 10371 | WESTMS_2 | 115 | 0.0521 | 0.2076 | 120 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10227 | NORTHPNM | 115 | 10212 | MPLAZA_T | 115 | 0.0032 | 0.0118 | 143 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10250 | PN-CG | 115 | 10227 | NORTHPNM | 115 | 0.00089 | 0.01042 | 156 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10265 | REEVES_1 | 115 | 10227 | NORTHPNM | 115 | 0.0033 | 0.013 | 143 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10266 | REEVES_2 | 115 | 10227 | NORTHPNM | 115 | 0.0031 | 0.013 | 156 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10245 | PERSON | 115 | 10295 | SANDIA_1 | 115 | 0.0167 | 0.0666 | 156 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10363 | WAYNE__# | 115 | 10266 | REEVES_2 | 115 | 0.00243 | 0.0095 | 156 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10266 | REEVES_2 | 115 | 10380 | WYOMING | 115 | 0.0046 | 0.0182 | 127 | 1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10019 | ASPEN | 115 | 10255 | PRAGER | 115 | 0.0003 | 0.003 | 322 | -1
180 | Albuquerque Sum without caps | -9999 | 9999 | 10371 | WESTMS_2 | 115 | 10194 | MARIPOSA | 115 | 0.0049 | 0.0195 | 156 | 1
500 | Southern CA Imports | -15200 | 15200 | 26003 | ADELANTO | 500 | 26105 | VICTORVL | 500 | 0 | 0.00159 | 2598 | 1
500 | Southern CA Imports | -15200 | 15200 | 26003 | ADELANTO | 500 | 26105 | VICTORVL | 500 | 0 | 0.00159 | 2598 | 1
500 | Southern CA Imports | -15200 | 15200 | 26003 | ADELANTO | 500 | 26079 | TOLUCA | 500 | 0.00082 | 0.01668 | 2598 | 1
500 | Southern CA Imports | -15200 | 15200 | 26003 | ADELANTO | 500 | 26115 | RINALDI2 | 500 | 0.00074 | 0.01861 | 1593 | 1
500 | Southern CA Imports | -15200 | 15200 | 26044 | MARKETPL | 500 | 26003 | ADELANTO | 500 | 0.00115 | 0.02256 | 1636 | -1
500 | Southern CA Imports | -15200 | 15200 | 25406 | J.HINDS | 230 | 24806 | MIRAGE | 230 | 0.0136 | 0.0731 | 357 | 1
500 | Southern CA Imports | -15200 | 15200 | 26044 | MARKETPL | 500 | 26003 | ADELANTO | 500 | 0.00115 | 0.02256 | 1636 | 1
500 | Southern CA Imports | -15200 | 15200 | 26119 | ADELSVC | 500 | 26003 | ADELANTO | 500 | 0 | 0.0001 | 387.5 | -1
500 | Southern CA Imports | -15200 | 15200 | 26048 | MCCULLGH | 500 | 26105 | VICTORVL | 500 | 0.00157 | 0.0252 | 1385.6 | 1
500 | Southern CA Imports | -15200 | 15200 | 26048 | MCCULLGH | 500 | 26105 | VICTORVL | 500 | 0.00157 | 0.0252 | 1385.6 | 1
500 | Southern CA Imports | -15200 | 15200 | 10000 | 12ST_TAP | 46 | 10001 | 12STREET | 46 | 0.0027 | 0.0042 | 23.9 | 1
500 | Southern CA Imports | -15200 | 15200 | 10026 | BACA | 46 | 10000 | 12ST_TAP | 46 | 0.0216 | 0.0316 | 27.1 | 1
500 | Southern CA Imports | -15200 | 15200 | 10356 | VALENCIA | 46 | 10000 | 12ST_TAP | 46 | 0.0239 | 0.0375 | 23.9 | 1
500 | Southern CA Imports | -15200 | 15200 | 30060 | MIDWAY | 500 | 24156 | VINCENT | 500 | 0.00112 | 0.00662 | 1848.1 | 1
500 | Southern CA Imports | -15200 | 15200 | 26051 | MEAD | 287 | 26104 | VICTORVL | 287 | 0.02443 | 0.17602 | 419.1 | 1
500 | Southern CA Imports | -15200 | 15200 | 26098 | SYLMAR3 | 230 | 26094 | SYLMARLA | 230 | 0 | 0.0003 | 1600 | 1
500 | Southern CA Imports | -15200 | 15200 | 24042 | ELDORDO | 500 | 24086 | LUGO | 500 | 0.0017 | 0.0128 | 1386 | 1
500 | Southern CA Imports | -15200 | 15200 | 30060 | MIDWAY | 500 | 24156 | VINCENT | 500 | 0.0011 | 0.0081 | 1848.1 | 1
500 | Southern CA Imports | -15200 | 15200 | 26100 | SYLMAR4 | 230 | 26094 | SYLMARLA | 230 | 0 | 0.0003 | 1600 | 1
500 | Southern CA Imports | -15200 | 15200 | 15021 | PALOVRDE | 500 | 24801 | DEVERS | 500 | 0.0022 | 0.0303 | 1645.5 | 1
500 | Southern CA Imports | -15200 | 15200 | 21007 | COACHELV | 230 | 24804 | DEVERS | 230 | 0.0064 | 0.0493 | 392.8 | 1
500 | Southern CA Imports | -15200 | 15200 | 22356 | IMPRLVLY | 230 | 21025 | ELCENTRO | 230 | 0.00379 | 0.025 | 370.1 | -1
500 | Southern CA Imports | -15200 | 15200 | 21076 | RAMON | 230 | 24806 | MIRAGE | 230 | 3e-05 | 0.00032 | 392.8 | 1
500 | Southern CA Imports | -15200 | 15200 | 22536 | N.GILA | 500 | 22360 | IMPRLVLY | 500 | 0.00075 | 0.00933 | 1212.4 | 1
500 | Southern CA Imports | -15200 | 15200 | 24627 | CIMA | 230 | 24041 | ELDORDO | 230 | 0.014 | 0.0764 | 288.8 | -1
500 | Southern CA Imports | -15200 | 15200 | 24601 | VICTOR | 230 | 24085 | LUGO | 230 | 0.00186 | 0.01548 | 494 | 1
500 | Southern CA Imports | -15200 | 15200 | 24601 | VICTOR | 230 | 24085 | LUGO | 230 | 0.00186 | 0.01548 | 494 | 1
500 | Southern CA Imports | -15200 | 15200 | 24701 | KRAMER | 230 | 24085 | LUGO | 230 | 0.00822 | 0.06849 | 478 | 1
500 | Southern CA Imports | -15200 | 15200 | 24701 | KRAMER | 230 | 24085 | LUGO | 230 | 0.00822 | 0.06849 | 478 | 1
500 | Southern CA Imports | -15200 | 15200 | 24086 | LUGO | 500 | 24097 | MOHAVE | 500 | 0.0017 | 0.01253 | 1386 | -1
500 | Southern CA Imports | -15200 | 15200 | 26097 | SYLMAR1 | 230 | 24147 | SYLMAR S | 230 | 0 | 0.0003 | 1100 | 1
500 | Southern CA Imports | -15200 | 15200 | 26099 | SYLMAR2 | 230 | 24147 | SYLMAR S | 230 | 0 | 0.0003 | 1100 | 1
500 | Southern CA Imports | -15200 | 15200 | 30060 | MIDWAY | 500 | 24156 | VINCENT | 500 | 0.0011 | 0.0082 | 1848.1 | 1
500 | Southern CA Imports | -15200 | 15200 | 24219 | PISGAH | 230 | 24041 | ELDORDO | 230 | 0.031 | 0.1689 | 289 | -1
501 | WOR - PV to Devers | -9999 | 1550 | 15021 | PALOVRDE | 500 | 24801 | DEVERS | 500 | 0.0022 | 0.0303 | 1645.5 | 1
502 | WOR - N.Gila | -9999 | 1331 | 22536 | N.GILA | 500 | 22360 | IMPRLVLY | 500 | 0.00075 | 0.00933 | 1212.4 | 1
502 | WOR - N.Gila | -9999 | 1331 | 22356 | IMPRLVLY | 230 | 21025 | ELCENTRO | 230 | 0.00379 | 0.025 | 370.1 | -1
503 | WOR - IID230 | -600 | 600 | 21076 | RAMON | 230 | 24806 | MIRAGE | 230 | 3e-05 | 0.00032 | 392.8 | 1
503 | WOR - IID230 | -600 | 600 | 21007 | COACHELV | 230 | 24804 | DEVERS | 230 | 0.0064 | 0.0493 | 392.8 | 1
504 | WOR -n- Mc-Vic | -9999 | 2592 | 26048 | MCCULLGH | 500 | 26105 | VICTORVL | 500 | 0.00157 | 0.0252 | 1385.6 | 1
504 | WOR -n- Mc-Vic | -9999 | 2592 | 26048 | MCCULLGH | 500 | 26105 | VICTORVL | 500 | 0.00157 | 0.0252 | 1385.6 | 1
504 | WOR -n- Mc-Vic | -9999 | 2592 | 26051 | MEAD | 287 | 26104 | VICTORVL | 287 | 0.02443 | 0.17602 | 419.1 | 1
505 | WOR -n- El Dor to Lugo | -9999 | 2754 | 24627 | CIMA | 230 | 24041 | ELDORDO | 230 | 0.014 | 0.0764 | 288.8 | -1
505 | WOR -n- El Dor to Lugo | -9999 | 2754 | 25406 | J.HINDS | 230 | 24806 | MIRAGE | 230 | 0.0136 | 0.0731 | 357 | 1
505 | WOR -n- El Dor to Lugo | -9999 | 2754 | 24219 | PISGAH | 230 | 24041 | ELDORDO | 230 | 0.031 | 0.1689 | 289 | -1
505 | WOR -n- El Dor to Lugo | -9999 | 2754 | 24042 | ELDORDO | 500 | 24086 | LUGO | 500 | 0.0017 | 0.0128 | 1386 | 1
505 | WOR -n- El Dor to Lugo | -9999 | 2754 | 24086 | LUGO | 500 | 24097 | MOHAVE | 500 | 0.0017 | 0.01253 | 1386 | -1
506 | Path 15 Borah W Summer | -9999 | 9999 | 30790 | PANOCHE | 230 | 30900 | GATES | 230 | 0.01084 | 0.06186 | 296 | -0.1
506 | Path 15 Borah W Summer | -9999 | 9999 | 30050 | LOSBANOS | 500 | 30060 | MIDWAY | 500 | 0.0015 | 0.01446 | 2146 | -0.1
506 | Path 15 Borah W Summer | -9999 | 9999 | 30880 | HENTAP2 | 230 | 30900 | GATES | 230 | 0.00261 | 0.02028 | 637.4 | -0.1
506 | Path 15 Borah W Summer | -9999 | 9999 | 60060 | BORAH | 345 | 60005 | ADEL TAP | 345 | 0.0025 | 0.02 | 1015.9 | 0.555
506 | Path 15 Borah W Summer | -9999 | 9999 | 30879 | HENTAP1 | 230 | 30900 | GATES | 230 | 0.00261 | 0.02028 | 637.4 | -0.1
506 | Path 15 Borah W Summer | -9999 | 9999 | 30790 | PANOCHE | 230 | 30900 | GATES | 230 | 0.01084 | 0.06186 | 296 | -0.1
506 | Path 15 Borah W Summer | -9999 | 9999 | 60020 | AMFLS | 138 | 61900 | RAFT RVR | 138 | 0.0149 | 0.0778 | 203.2 | 0.555
506 | Path 15 Borah W Summer | -9999 | 9999 | 60020 | AMFLS | 138 | 60295 | PLST VLY | 138 | 0.00682 | 0.04056 | 203.4 | 0.555
506 | Path 15 Borah W Summer | -9999 | 9999 | 60060 | BORAH | 345 | 60006 | ADELAIDE | 345 | 0.0022 | 0.0185 | 1015.9 | 0.555
506 | Path 15 Borah W Summer | -9999 | 9999 | 30050 | LOSBANOS | 500 | 30055 | GATES | 500 | 0.0008 | 0.00896 | 2146 | -0.1
506 | Path 15 Borah W Summer | -9999 | 9999 | 60235 | MIDPOINT | 345 | 60190 | KINPORT | 345 | 0.0026 | 0.03668 | 1075.6 | -0.555
507 | Combined 4a, 4b | -9999 | 1096 | 66305 | RIVERTON | 230 | 66740 | WYOPO | 230 | 0.0032 | 0.0288 | 423.9 | 1.07
507 | Combined 4a, 4b | -9999 | 1096 | 73004 | ALCOVA | 115 | 73162 | RADERVIL | 115 | 0.093 | 0.2658 | 80 | 1
507 | Combined 4a, 4b | -9999 | 1096 | 66305 | RIVERTON | 230 | 66535 | THERMOPL | 230 | 0.0091 | 0.0733 | 358.9 | 1
507 | Combined 4a, 4b | -9999 | 1096 | 65300 | CASPERPP | 230 | 65955 | MIDWEST | 230 | 0.01 | 0.0575 | 327.1 | 1
507 | Combined 4a, 4b | -9999 | 1096 | 65095 | BADWATER | 230 | 66410 | SPENCE | 230 | 0.0102 | 0.1125 | 478.1 | -1
507 | Combined 4a, 4b | -9999 | 1096 | 73170 | RIVERTON | 115 | 66305 | RIVERTON | 230 | 0.0031 | 0.0948 | 100 | -1
507 | Combined 4a, 4b | -9999 | 1096 | 66020 | MUSTANG | 230 | 66410 | SPENCE | 230 | 0.0122 | 0.1117 | 423.9 | -1.07
507 | Combined 4a, 4b | -9999 | 1096 | 65420 | DAVEJOHN | 230 | 65460 | DIFICULT | 230 | 0.0071 | 0.0637 | 423.9 | 1.07
507 | Combined 4a, 4b | -9999 | 1096 | 65293 | CARR DRA | 230 | 66725 | WYODAK | 230 | 0.00545 | 0.04885 | 423.9 | -1
508 | PACI vs PDCI | -9999 | 7300 | 45035 | CAPTJACK | 500 | 30020 | OLINDA | 500 | 0.0011 | 0.0123 | 2310 | 1
508 | PACI vs PDCI | -9999 | 7300 | 40687 | MALIN | 500 | 30005 | ROUND MT | 500 | 0.00107 | 0.00886 | 1559 | 1
508 | PACI vs PDCI | -9999 | 7300 | 40687 | MALIN | 500 | 30005 | ROUND MT | 500 | 0.00103 | 0.00902 | 2338 | 1
508 | PACI vs PDCI | -9999 | 7300 | 10026 | BACA | 46 | 10000 | 12ST_TAP | 46 | 0.0216 | 0.0316 | 27.1 | 1
508 | PACI vs PDCI | -9999 | 7300 | 10356 | VALENCIA | 46 | 10000 | 12ST_TAP | 46 | 0.0239 | 0.0375 | 23.9 | 1
509 | Tot 2a, 2b, 2c Nomogram | -1600 | 1570 | 18002 | HA PS | 345 | 66280 | REDBUTTE | 345 | 0.00492 | 0.05033 | 300 | -1
509 | Tot 2a, 2b, 2c Nomogram | -1600 | 1570 | 66235 | PINTO PS | 345 | 14101 | FOURCORN | 345 | 0.0056 | 0.0511 | 1026 | 1
509 | Tot 2a, 2b, 2c Nomogram | -1600 | 1570 | 66355 | SIGURDPS | 230 | 79031 | GLENCANY | 230 | 0.033 | 0.2427 | 386.8 | 1
509 | Tot 2a, 2b, 2c Nomogram | -1600 | 1570 | 79060 | SANJN PS | 345 | 79072 | HESPERUS | 345 | 0.00149 | 0.02338 | 1619 | -1
509 | Tot 2a, 2b, 2c Nomogram | -1600 | 1570 | 79105 | GLADETAP | 115 | 79260 | ELPASOTP | 115 | 0.01502 | 0.04577 | 85 | -1
509 | Tot 2a, 2b, 2c Nomogram | -1600 | 1570 | 79061 | SHIP PS | 230 | 79063 | SHIPROCK | 230 | 0 | 0.044 | 400 | 1
510 | EOR - HASSYAMP- N.GILA | -9999 | 1273 | 15090 | HASSYAMP | 500 | 22536 | N.GILA | 500 | 0.00115 | 0.01354 | 1212.4 | 1
511 | WOR - N.GILA - IMPRLVLY | -9999 | 1273 | 22536 | N.GILA | 500 | 22360 | IMPRLVLY | 500 | 0.00075 | 0.00933 | 1212.4 | 1
512 | Imp.Valley to Miguel | -9999 | 1120 | 22360 | IMPRLVLY | 500 | 22468 | MIGUEL | 500 | 0.00077 | 0.00992 | 1212.4 | 1