July 22, 1994

Contract #TW0592

SPECIAL STANDARD SPECIFICATION

SECTION 13943-S

CONTROLS

LIST OF ARTICLES TITLES

Page

PART I - GENERAL

1.01	Scope	2

1.02	Responsibility	2

1.03	Submittals	2

PART 2 - PRODUCTS

2.01	General	3

2.02	FID (Field Interface Device)	3

2.03	Sensor, Switch, And Control Device	3

2.04	Control Damper	3

2.05	Control Valve	4

2.06	Instrument Air Source	4

2.07	Instrument Air Piping	5

2.08	Wiring	5

2.09	Control Panel	65

PART 3 - INSTALLATION

3.01	General	6

3.02	FID (Field Interface Device)	6

3.03	Sensor, Switch, And Control Device	6

3.04	Control Damper	7

3.05	Control Valve	7

3.06	Instrument Air Piping	7

3.07	Wiring	8

3.08	Control Panel	8

3.09	Labels	98

SPECIAL STANDARD SPECIFICATION

SECTION 13943-S

CONTROLS

PART 1 - GENERAL

1.01	SCOPE

Instrumentation and control systems required for HVAC systems and Sandia National Laboratories' Energy Management and Control System (EMCS).

(Note that the EMCS is referred to as the Plant Control Center [PCC].  Remote control units, called Field Interface Devices [FID], located in individual buildings provide local monitoring and control functions.  Each FID communicates with an existing PCC Host Computer in Building 887 or Building 858 for remote monitoring and control purposes.)

1.02	RESPONSIBILITY

A.	The contractor shall furnish, install, adjust, calibrate, and make ready for use all sensors, switches, relays, controllers, control dampers and valves, wiring, instrument air piping, and accessories indicated on the drawings and required for a complete and totally functioning HVAC control system and EMCS.

B.	All required PCC programming will be provided by Sandia National Laboratories (SNL).

C.	All contractor furnished products and labor shall have a one-year warranty.

D.	During warranty, all defective products shall be repaired or replaced, and all readjustments necessary to accomplish the specified sequences of operation shall be at no cost to SNL.

E.	Provide labor, material, equipment, etc., required to facilitate the commissioning process.  Perform form tests and verification procedures required by the commissioning process when requested by the Commissioning Authority and directed by the General Contractor.  See Section 15995.

1.03	SUBMITTALS

A.	Provide submittals in accordance with Section 01300 of these specifications.

B.	Provide calibration data and procedures for all sensors, switches, and controllers as part of submittals.

C.	Provide control diagrams in the form of shop drawings for each system or sub-system.  Use the control diagrams included in the contract drawings for this purpose.  Each diagram shall be altered to show all proposed controls and controlled devices, together with name, catalog number, set point, and action at each end of the throttling range.

D.	The contractor will be furnished reproducible copies of all contract drawings for use in preparing his shop drawings.

PART 2 - PRODUCTS

2.01	GENERAL

A.	All materials and components used shall be standard components, regularly manufactured for this type application and not custom designed especially for this project.

B.	All products shall be as specified on the drawings and in these specifications or approved equals.

2.02	FID

FIDS will be provided by SNL.

2.03	SENSOR, SWITCH, AND CONTROL DEVICE

A.	Room, duct, and immersion sensors shall provide an output signal that varies continuously with the sensed media within a fixed range specified on the drawings.  Output shall be linear with negligible hysteresis.

B.	Sensor accuracy shall be as indicated on the drawings and, when part of a control loop, shall be sufficient to maintain the controlled variable within limits indicated on the drawings.

C.	Controllers shall have variable set point and adjustable proportional band unless indicated otherwise on the drawings.

D.	Pneumatic room thermostats shall be a two pipe non-bleed relay type with visible temperature scale and adjustable set point scale with a permanently affixed external adjustment suitable for occupant control of room temperature without the use of tools.

E.	Pneumatic zone thermostats shall be similar to room thermostats except the adjustable set point scale shall be concealed with an internal means of set point adjustment.

2.04	CONTROL DAMPER

A.	Damper shall be low leakage type, Ruskin CD-50 series airfoil unless indicated otherwise on the drawings.

B.	Damper shall be a standard louver type of heavy duty construction with each leaf reinforced.  Damper shall be provided with non-ferrous self lubricating bearings and trunions.

C.	Damper shall be of aluminum unless indicated otherwise on the drawings.

D.	Damper frame, blades, shafts, linkage, bearings, and trunions shall be non-corrosive.

E.	Damper blade edge seals shall be replaceable and of vinyl, silicone rubber, neoprene, or other synthetic elastomer.

F.	Damper shall have a published leak rate not exceeding 5 scfm per square foot at 1.5 inches W.C. differential pressure unless indicated otherwise on the drawings.

G.	Modulating dampers shall have opposed acting blades, and two-position dampers shall have parallel acting blades unless indicated otherwise on the drawings.

H.	Each damper section shall have an individual motor, derated so there is 10 percent over-capacity available over published rating for dust and corrosion buildup and shall be additionally sized to operate against the static pressure of the systems.

2.05	CONTROL VALVE

A.	Control valves 2 inches or smaller shall be screwed pattern with bronze body unless indicated otherwise on the drawings.

B.	Control valves larger than 2 inches shall be flanged with cast iron body unless indicated otherwise on the drawings.

C.	Valve pressure-temperature ratings and materials of construction shall be suitable for the intended service.  Valves intended for steam service shall be rated for 350oF.

D.	All 2-way control valves shall be capable of tight shut-off against total system differential pressure.

E.	Modulating control valves shall be fitted with equal percentage or linear characteristic modulating plugs as the service requires.

F.	Valve sizing data, including capacity index, shall be indicated on the control submittal diagrams.

G.	Visible position indicators shall be provided on all automatic valves.

2.06	INSTRUMENT AIR SOURCE

A.	A 1/2-inch valved tap is provided in the basement mechanical room to supply 90 psig Nitrogen for pneumatic actuators.  See Drawing 104530 M19.  The Contractor shall field route Nitrogen to each valve utilizing pneumatic actuators.Furnish and install as indicated on the drawings, a self-contained air compressor which will supply compressed air for the operation of the pneumatic controls.

B.	The compressor shall be a complete unit designed to compress air to 80 psi.

C.	Compressor and motor shall be adequately sized so that the free air delivery at the receiver cut-in pressure equals or exceeds all present and indicated future instrument air demands while operating not more than 33% of the time.

D.	Compressor shall be provided with controls including starter, control panel, gauges, and controllers for full automatic operation.

E.	The compressor shall be factory assembled with a suitable receiver, ASME Code constructed for pressure of 125 psi.  Receiver shall be National Board Certified and so stamped.  The certification papers shall be submitted.  Receiver shall be provided with a manual valve drain, automatic drain, and ASME safety relief valves.

F.	A suitable pressure reducing valve designed for 125 psi to the controls operating pressure shall be provided for system supply.

G.	Compressor shall be provided with an OSHA approved belt guard.

H.	When specified on the drawings, a properly sized, completely automatic refrigerative type air dryer shall be furnished and installed in the supply line to the system to assure dry control air.  Dryer shall be equal to Hankison Series 80.

I.	The FID main control air filter shall be for compressed air service with manual drain and metal guard, 1/4" NPT inlet and outlet; Quincy Model No. 8527.

2.07	INSTRUMENT AIR PIPING

A.	Instrument air piping shall be copper, plastic, or stainless steel.  Aluminum tubing may be used only if approved prior to the start of any work.

B.	Copper tubing shall be hard drawn with sweated fittings or soft drawn-stretched and straightened.

C.	Plastic tubing shall be flame retardant polyethylene.  Plastic tube bundles shall be provided with a factory installed PVC vinyl jacket.

D.	All instrument air piping shall be 1/4" O.D. unless approved prior to the start of any work.

2.08	WIRING

A.	All wiring shall comply with the electrical sections of these specifications.

B.	Plant Control Center Wiring

1.	Field wiring for each analog sensor shall be two conductor No. 18, twisted AWG, copper, 300 volt, thermoplastic.

2.	Field wiring for each digital input device shall be #16 type THHN.  Wiring shall be blue.

3.	Field wiring for each digital output device shall be #14 type THHN.  Wiring shall be black.

4.	All wiring shall be installed in electrical-metallic tubing (EMT) with watertight compression-type threadless fittings or rigid galvanized steel conduit (RC) or Intermediate Metal Conduit (IMC).

2.09	CONTROL PANEL

A.	Panels shall be totally enclosed, 16 gage (min.) steel, with hinged locking door and door stiffeners.

B.	Panels shall have electrical connections prewired to terminal strips using same numbers shown on the drawings.

C.	Each panel shall contain flushmounted on the cover all 3 1/2-inch dial thermometers and other devices as indicated on the drawings.

PART 3 - INSTALLATION

3.01	GENERAL

Install all FIDS, sensors, switches, control devices, conduit and wire, and instrument air piping indicated on the drawings and required for a complete and operational temperature control system.

3.02	FID

FIDS shall be in dry interior areas of buildings and as indicated on drawings.  Do not install FIDS near heat generating devices.

3.03	SENSOR, SWITCH, AND CONTROL DEVICE

A.	All sensor assemblies shall be readily accessible and adaptable to each type of application in such a manner as to allow for quick, easy replacement and servicing without special tools or skills.

B.	All sensors and switches installed outdoors shall be installed in NEMA 3R enclosures.

C.	Install sensors in locations which will provide a correct measurement of the sensed media.  Do not locate sensors in dead air spaces or positions obstructed by ducts, equipment, etc.  The location shall be within the vibration and velocity limits of the sensing element.  Use an extended surface element when required to properly sense the average temperature or pressure, etc., securely mounted and positioned to measure the best average temperature, etc.  Thermally isolate elements from brackets and supports.  Securely seal ducts where elements or connections penetrate ducts.

D.	Provide all sensors measuring temperatures in pipes with thermometer wells.  Where piping is smaller than the length of the well, install the well in the piping at elbows to affect proper flow across the entire area of the well.  Install wells either looking upstream or downstream.  Provide suitable thermal transmission material within the well to speed the response of temperature measurement.  Provide wells with sealing nuts to contain the thermal transmission material and allow for easy replacement.  Well shall not restrict flow area to less than 70 percent of the line-size-pipe normal flow area.

E.	All pressure sensors and switches, including differential pressure sensors and switches, installed on steam lines shall be protected by pigtail siphons installed between the sensor element and the steam line.

F.	Pressure sensors and switches, including differential pressure sensors and switches, installed on steam or liquid lines shall have an isolation valve installed between each sensor and its pressure source.

G.	Duct thermometers with a minimum 3-inch dial shall be installed upstream and downstream of each duct heat exchange device and adjacent to each duct mounted temperature sensor.  Range shall match application.

H.	Room thermostats and temperature sensors shall be wall mounted 5'-6" above the floor.

I.	All thermostats or sensors located on exterior building walls shall be insulated from the wall surface on a 1-1/2 inch thick block of rigid insulation and shrouded by a cover that is closed on the top, sides, and front but open at the bottom for free air circulation.

J.	Mount all controllers in control panels so that all control adjustments can be made at a control panel.

3.04	CONTROL DAMPER

A.	Control dampers shall be installed per the ductwork sections of these specifications.

B.	Damper motors in plenums shall be mounted on damper frames.

C.	Motors shall be accessible for servicing.

D.	Motors located outside shall be mounted in a position to allow for condensation drainage.

E.	When two or more dampers are intended for inter-related operation, they shall be connected wherever possible through mechanical connections operating on easily movable swivel joints and shall not depend upon parallel operation of separate damper motors.

3.05	CONTROL VALVE

Control valves shall be installed per the piping sections of these specifications.

3.06	INSTRUMENT AIR PIPING

A.	Piping in the equipment rooms shall be installed exposed, securely attached to the structure or to the equipment and run parallel or at right angles to the structure.

B.	Piping on new construction to all equipment outside of the equipment rooms shall be concealed.

C.	Piping in old construction may be run exposed except where easy access permits concealment.

D.	All piping shall be securely supported by the structure or equipment using hangers of the clamp type.

E.	Piping shall be offset around all beams, girders, etc.

F.	Piping SHALL NOT be installed through the sheet metal ducts or in fresh air intakes.

G.	Piping installed outside shall be pitched toward the building, with suitable drip legs inside, for condensation drainage.

H.	Unsheathed plastic tubing shall be installed in an enclosed raceway system such as Wire-mold, National Electric Product, or EMT, except final connections can be made with a maximum of 18" of exposed plastic tubing.

I.	Plastic tubing for enclosed control panel piping shall be installed parallel or at right angles to the panel configuration.

J.	All piping shall be provided with pressure gages at the final control element and at the controller.

K.	Air pressure gages, size 1-1/2" shall be installed on all connections to pneumatic controlled valves, damper motors, thermostats, control devices, etc., so that the operation of each device can be checked.  The range of each gage shall match the application.  Gages are not required where room thermostats are flush mounted with concealed connecting tubing.

L.	Do not install piping in same conduit with electrical wires.

3.07	WIRING

A.	All wiring shall comply with the electrical sections of these specifications.

B.	Plant Control Center Wiring

1.	Wiring from sensors and control devices shall be to terminal strips within the FID, control panel, or Motor Control Center, as shown on the drawings.

2.	All wiring runs shall be continuous.  Splices will not be acceptable.

3.	Each wire shall be labeled at both ends per the drawings.

4.	Shielded cable shall be grounded at sensor only.

5.	All conduit shall be painted to match surroundings.  One-inch purple vinyl tape shall be installed on conduits within six inches of all J-boxes, sensors, and panels to identify PCC conduits.

6.	Wiring shall not be installed in the same conduit with instrument air piping.

3.08	CONTROL PANEL

Install control panels where indicated on drawings.  Enclosures shall be securely mounted to the floor, wall, or equipment with unistrut supports.

3.09	LABELS

A.	Each control device shall be provided with an engraved laminated phenolic resin label, black background with white letters.

B.	Nomenclature shall correspond to that shown on the contract drawings.

END OF SECTION

EXCEPT FOR ATTACHMENTS