## PS Reqs
Table 7: NuMI POWER SUPPLY REQUIREMENTS | [31 empty] | Current Regulation
Ramp Cycle Time: |  | 1.9 | seconds | 2002-04-17 | [25 empty] | Est. I Ripple (720hz) |  | "+/-" % of peak PS current, no extra reg. | "+/-" % of peak running current | Holec, FNAL elect. "+/-" % Max | "+/-" % of peak running current
CIRCUIT(ACNET if different then CKT Name) |  |  | MAG. | MAG. | MAG. | CABLE |  |  |  |  | Passive Filter |  | Total | Total | PEAK | Min. |  | PEAK | RMS | Power | PEAK | Power Supply |  |  |  | Total RMS | Fdr | Peak | Estimated | NO FILTER
| MAGNET | # | IND. | RES. | Max. Pwr. | TYPE | # | R/kFt | L | RES. | R | L | Res. | Ind. | CURR. | Curr. | dI/dT | VOLT. | CURR. | per Mag. | PWR | TYPE | Volt | Curr. | PS Loses | PWR | Load | Fdr | PS Cost | P-P | P-P
| TYPE | MAGs | (henry) | (ohms) | (kW) | kcmil | 1 way | ohms | (ft) | ohms | ohms | henry | ohms | henry | (amps) | (amps) | (A/s) | (volts) | (amps) | (kW) | (kW) | #, Man./Pwr | (volts) | (amps) | (kW) | (kW) | kVA | kVA | ($k) | amps | %
[29 empty] | 0 (on hand) | $10K/loop Filters (refurbished) |  |  |  | Cost:
MI60 Power Supplies | [33 empty] | $10K/loop
Kicker (I:KPS6N)) | kicker | 3
LAMB (I:LAM601) | Lamb. | 1 | 0.017 | 0.013 |  | 500 | 2 | 0.026 | 132.3 | 0.0034398 | 0.002 | 0.001 | 0.01844 | 0.018 | 765.85 | 0 | note 7 | 200 | 400 | 2.08 | 153.17 | 1, Xrex/500kW | 200 | 2500 | 4 | 6.9504 | 112 | 214.438 | 0 (on hand) | 1.2287 | 0.16043 | 0.1% | 0.3264% | 0.01% | 0.03264%
LAMB (I:LAM6023) | Lamb. | 2 | 0.017 | 0.013 |  | 500 | 3 | 0.026 | 153.6603 | 0.0026634 | 0.002 | 0.001 | 0.030663 | 0.035 | 1806.25 | 0 | note 8 | 200 | 794 | 8.1957 | 361.25 | 1, Xrex/500kW | 200 | 2500 | 7.94 | 27.2713 | 222.32 | 505.75 | 1 (on hand) | 0.63189 | 0.034983 | 0.1% | 0.1384% | 0.01% | 0.01384%
CMAG (E:V100) | Cmagnet | 1 | 0.002 | 0.007 |  | 500 | 5 | 0.026 | 165.2447 | 0.0017185 | 0.002 | 0.001 | 0.010719 | 0.003 | 3482.5 | 0 | note 7 | 50 | 1560 | 17.0352 | 174.125 | 1, Xrex/500kW | 50 | 5000 | 3.9 | 29.9847 | 109.2 | 243.775 | 0 (on hand) | 1.843 | 0.052922 | 0.1% | 0.1436% | 0.01% | 0.01436%
E:Q101 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 97.9114 | 0.024478 | 0 | 0 | 2.2745 | 1.5 | 64.64 | 64.64 | 0 | 147.0222 | 64.64 | 9.4012 | 9.5035 | 1, PEI/20kW | 200 | 100 | 0.6464 | 10.1499 | 18.0992 | 18.0992 | 0 (on hand) |  |  | 0.05% | 0.07735%
BND1(E:HV101) | EPB | 6 | 0.03 | 0.0175 | 50 | 500 | 3 | 0.026 | 243.5752 | 0.004222 | 0.002 | 0.001 | 0.11122 | 0.181 | 1645.67 | 0 | note 7 | 600 | 914 | 14.6194 | 987.402 | 3, Xrex/500kW | 600 | 2500 | 27.42 | 120.3344 | 767.76 | 1382.3628 | 0 (on hand) | 0.36656 | 0.022274 | 0.1% | 0.1519% | 0.01% | 0.01519%
E:HT102 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 196.6324 | 0.47192 | 0 | 0 | 4.8719 | 0.95 | 25 | 0 | 26.3158 | 146.7979 | 14.4338 | 0.91667 | 3.6699 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.1232 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:Q102 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 148.4917 | 0.037123 | 0 | 0 | 2.2871 | 1.5 | 64.64 | 64.64 | 0 | 147.8396 | 64.64 | 9.4012 | 9.5564 | 1, PEI/20kW | 200 | 100 | 0.6464 | 10.2028 | 18.0992 | 18.0992 | 0 (on hand) |  |  | 0.05% | 0.07735%
E:Q103 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 205.7002 | 0.051425 | 0 | 0 | 2.3014 | 1.5 | 72.36 | 72.36 | 0 | 166.5311 | 72.36 | 11.7809 | 12.0502 | 1, PEI/20kW | 200 | 100 | 0.7236 | 12.7738 | 20.2608 | 20.2608 | 0 (on hand) |  |  | 0.05% | 0.0691%
E:VT103 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 266.5596 | 0.63974 | 0 | 0 | 5.0397 | 0.95 | 25 | 0 | 26.3158 | 150.9936 | 14.4338 | 0.91667 | 3.7748 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.1582 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:Q104 | 3Q60 | 1 | 1.1 | 1.6 | 17 | 1/0 | 1 | 0.125 | 224.703 | 0.056176 | 0 | 0 | 1.6562 | 1.1 | 33.68 | 33.68 | 0 | 55.78 | 33.68 | 1.8149 | 1.8787 | 1, PEI/20kW | 100 | 200 | 0.1684 | 2.0471 | 4.7152 | 4.7152 | 0 (on hand) |  |  | 0.05% | 0.2969%
E:H104 | 200 Turn SY Trims | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 250 | 0.0625 | 0 | 0 | 2.3125 | 1.5 | 80 | 80 |  | 185 | 80 | 14.4 | 14.8 | 1, PEI/20kW | 200 | 100 | 0.8 | 15.6 | 22.4 | 22.4 | 0 (on hand) | 0.013638 | 0.017048 | 0.05% | 0.0625%
E:HT105 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 301.1178 | 0.72268 | 0 | 0 | 5.1227 | 0.95 | 25 | 0 | 26.3158 | 153.0671 | 14.4338 | 0.91667 | 3.8267 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.1755 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:Q105 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 252.9772 | 0.063244 | 0 | 0 | 2.3132 | 1.5 | 60.04 | 60.04 | 0 | 138.8872 | 60.04 | 8.1108 | 8.3388 | 1, PEI/20kW | 200 | 100 | 0.6004 | 8.9392 | 16.8112 | 16.8112 | 0 (on hand) |  |  | 0.05% | 0.08328%
E:VT106 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 357.6662 | 0.8584 | 0 | 0 | 5.2584 | 0.95 | 25 | 0 | 26.3158 | 156.46 | 14.4338 | 0.91667 | 3.9115 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.2038 | 3.0311 | 5.25 |  |  |  | 0.1% | 0.06%
E:Q106 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 309.5256 | 0.077381 | 0 | 0 | 2.3274 | 1.5 | 60.04 | 60.04 | 0 | 139.736 | 60.04 | 8.1108 | 8.3897 | 1, PEI/20kW | 200 | 100 | 0.6004 | 8.9901 | 16.8112 | 16.8112 | 0 (on hand) |  |  | 0.05% | 0.08328%
E:HT107 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 414.2146 | 0.99411 | 0 | 0 | 5.3941 | 0.95 | 25 | 0 | 26.3158 | 159.8529 | 14.4338 | 0.91667 | 3.9963 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.232 | 3.0311 | 5.25 |  |  |  | 0.1% | 0.06%
E:VT108 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 470.7629 | 1.1298 | 0 | 0 | 5.5298 | 0.95 | 25 | 0 | 26.3158 | 163.2458 | 14.4338 | 0.91667 | 4.0811 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.2603 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:HT109 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 527.3124 | 1.2655 | 0 | 0 | 5.6655 | 0.95 | 25 | 0 | 26.3158 | 166.6387 | 14.4338 | 0.91667 | 4.166 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.2886 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:VT110 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 583.0322 | 1.3993 | 0 | 0 | 5.7993 | 0.95 | 25 | 0 | 26.3158 | 169.9819 | 14.4338 | 0.91667 | 4.2495 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.3164 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:VT111 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 645.9603 | 1.5503 | 0 | 0 | 5.9503 | 0.95 | 25 | 0 | 26.3158 | 173.7576 | 14.4338 | 0.91667 | 4.3439 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.3479 | 3.0311 | 5.25 |  |  |  | 0.1% | 0.06%
E:HT112 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 661.8505 | 1.5884 | 0 | 0 | 5.9884 | 0.95 | 25 | 0 | 26.3158 | 174.711 | 14.4338 | 0.91667 | 4.3678 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.3558 | 3.0311 | 5.25 |  |  |  | 0.1% | 0.06%
[24 empty] | MI60N Power Totals: | 48.5281 | 265.7054 | 1358.7877 | 2516.0226
MI62 Power Supplies
E:Q107 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 662 | 0.1655 | 0 | 0 | 2.4155 | 1.5 | 60.04 | 60.04 | 0 | 145.0266 | 60.04 | 8.1108 | 8.7074 | 1, PEI/20kW | 200 | 100 | 0.6004 | 9.3078 | 16.8112 | 16.8112 | 0 (on hand) |  |  | 0.05% | 0.08328%
E:Q108 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 637.3777 | 0.15934 | 0 | 0 | 2.4093 | 1.5 | 60.04 | 60.04 | 0 | 144.657 | 60.04 | 8.1108 | 8.6852 | 1, PEI/20kW | 200 | 100 | 0.6004 | 9.2856 | 16.8112 | 16.8112 | 0 (on hand) |  |  | 0.05% | 0.08328%
BND2 (E:V109) | B2 | 6 | 0.008 | 0.00718 | 162 | 500 | 8 | 0.026 | 624.298 | 0.0040579 | 0.002 | 0.001 | 0.049138 | 0.049 | 4446.98 | 0 | note 7 | 400 | 2360 | 39.9897 | 1778.792 | MR - type | 470 | 5000 | 6.6552 | 280.3339 | 1552.88 | 2926.1128 | 0 (on hand) | 0.9027 | 0.020299 | 0.1% | 0.1124% | 0.01% | 0.01124%
E:Q109 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 580.8282 | 0.14521 | 0 | 0 | 2.3952 | 1.5 | 60.04 | 60.04 | 0 | 143.8082 | 60.04 | 8.1108 | 8.6342 | 1, PEI/20kW | 200 | 100 | 0.6004 | 9.2346 | 16.8112 | 16.8112 | 0 (on hand) |  |  | 0.05% | 0.08328%
E:Q110 | 3Q60 | 1 | 1.1 | 1.6 | 17 | 1/0 | 1 | 0.125 | 525.1084 | 0.13128 | 0 | 0 | 1.7313 | 1.1 | 24.69 | 24.69 | 0 | 42.7452 | 24.69 | 0.97535 | 1.0554 | 1, PEI/20kW | 100 | 200 | 0.12345 | 1.1788 | 3.4566 | 3.4566 | 0 (on hand) |  |  | 0.05% | 0.405%
E:Q111 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 520.1009 | 0.13003 | 0 | 0 | 2.38 | 1.5 | 55.99 | 55.99 | 0 | 133.2576 | 55.99 | 7.0535 | 7.4611 | 1, PEI/20kW | 200 | 100 | 0.5599 | 8.021 | 15.6772 | 15.6772 | 0 (on hand) |  |  | 0.05% | 0.0893%
E:Q112 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 541.8505 | 0.13546 | 0 | 0 | 2.3855 | 1.5 | 59.03 | 59.03 | 0 | 140.8139 | 59.03 | 7.8402 | 8.3122 | 1, PEI/20kW | 200 | 100 | 0.5903 | 8.9025 | 16.5284 | 16.5284 | 0 (on hand) |  |  | 0.05% | 0.0847%
[24 empty] | MI62 Power Totals: | 9.1296 | 316.9565 | 1622.1646 | 2995.3974
minus MR PS/Xformer
Upstream Service Building and Horn Power Supplies | [28 empty] | 0 (on hand)
E:Q113 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 732.0667 | 0.18302 | 0 | 0 | 2.433 | 1.5 | 59.03 | 59.03 | 0 | 143.621 | 59.03 | 7.8402 | 8.4779 | 1, PEI/20kW | 200 | 100 | 0.5903 | 9.0682 | 16.5284 | 16.5284 | 0 (on hand) |  |  | 0.05% | 0.0847%
E:VT113 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 701.2073 | 1.6829 | 0 | 0 | 6.0829 | 0.95 | 25 | 0 | 26.3158 | 177.0724 | 14.4338 | 0.91667 | 4.4268 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.3755 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:HT114 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 692.1764 | 1.6612 | 0 | 0 | 6.0612 | 0.95 | 25 | 0 | 26.3158 | 176.5306 | 14.4338 | 0.91667 | 4.4133 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.371 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:Q114 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 710.3171 | 0.17758 | 0 | 0 | 2.4276 | 1.5 | 55.99 | 55.99 |  | 135.9202 | 55.99 | 7.0535 | 7.6102 | 1, PEI/20kW | 200 | 100 | 0.5599 | 8.1701 | 15.6772 | 15.6772 | 0 (on hand) |  |  | 0.05% | 0.0893%
E:HT115 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 636.9682 | 1.5287 | 0 | 0 | 5.9287 | 0.95 | 25 | 0 | 26.3158 | 173.2181 | 14.4338 | 0.91667 | 4.3305 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.3434 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:Q115 | 3Q60 | 1 | 1.1 | 1.6 | 17 | 1/0 | 1 | 0.125 | 655.1089 | 0.16378 | 0 | 0 | 1.7638 | 1.1 | 24.69 | 24.69 | 0 | 43.5477 | 24.69 | 0.97535 | 1.0752 | 1, PEI/20kW | 100 | 200 | 0.12345 | 1.1986 | 3.4566 | 3.4566 | 0 (on hand) |  |  | 0.05% | 0.405%
E:VT116 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 590.3506 | 1.4168 | 0 | 0 | 5.8168 | 0.95 | 25 | 0 | 26.3158 | 170.421 | 14.4338 | 0.91667 | 4.2605 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.3201 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:Q116 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 608.4913 | 0.15212 | 0 | 0 | 2.4021 | 1.5 | 80.98 | 80.98 |  | 194.5239 | 80.98 | 14.755 | 15.7525 | 1, PEI/20kW | 200 | 100 | 0.8098 | 16.5623 | 22.6744 | 22.6744 | 0 (on hand) |  |  | 0.05% | 0.06174%
E:HT117 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 518.4475 | 1.2443 | 0 | 0 | 5.6443 | 0.95 | 25 | 0 | 26.3158 | 166.1068 | 14.4338 | 0.91667 | 4.1527 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.2841 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:H117 | 200 Turn SY Trims | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 518.4475 | 0.12961 | 0 | 0 | 2.3796 | 1.5 | 80 | 80 |  | 190.3689 | 80 | 14.4 | 15.2295 | 1, PEI/20kW | 200 | 100 | 0.8 | 16.0295 | 22.4 | 22.4 | 0 (on hand) | 0.014034 | 0.017543 | 0.05% | 0.0625%
E:Q117 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 536.5882 | 0.13415 | 0 | 0 | 2.3841 | 1.5 | 64.14 | 64.14 |  | 152.9192 | 64.14 | 9.2564 | 9.8082 | 1, PEI/20kW | 200 | 100 | 0.6414 | 10.4496 | 17.9592 | 17.9592 | 0 (on hand) |  |  | 0.05% | 0.07795%
E:VT118 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 496.9991 | 1.1928 | 0 | 0 | 5.5928 | 0.95 | 25 | 0 | 26.3158 | 164.8199 | 14.4338 | 0.91667 | 4.1205 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.2734 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:Q118 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 515.1398 | 0.12878 | 0 | 0 | 2.3788 | 1.5 | 71.22 | 71.22 | 0 | 169.4171 | 71.22 | 11.4126 | 12.0659 | 1, PEI/20kW | 200 | 100 | 0.7122 | 12.7781 | 19.9416 | 19.9416 | 0 (on hand) |  |  | 0.05% | 0.0702%
BND3 (E:V119) | B2 | 4 | 0.008 | 0.00718 | 162 | 500 | 7 | 0.026 | 482.8898 | 0.0035872 | 0.002 | 0.001 | 0.034307 | 0.033 | 4142.08 | 0 | note 7 | 400 | 1945 | 27.1621 | 1656.832 | 4, Xrex/500kW | 400 | 5000 | 4.668 | 134.4529 | 1089.2 | 2319.5648 | 0 (on hand) | 1.3404 | 0.03236 | 0.1% | 0.1207% | 0.01% | 0.01207%
E:HT119 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 441.2795 | 1.0591 | 0 | 0 | 5.4591 | 0.95 | 25 | 0 | 26.3158 | 161.4768 | 14.4338 | 0.91667 | 4.0369 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.2456 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:Q119 | 3Q60 | 1 | 1.1 | 1.6 | 17 | 1/0 | 1 | 0.125 | 459.4201 | 0.11486 | 0 | 0 | 1.7149 | 1.1 | 48.09 | 48.09 | 0 | 82.4674 | 48.09 | 3.7002 | 3.9659 | 1, PEI/20kW | 200 | 100 | 0.4809 | 4.4468 | 13.4652 | 13.4652 | 0 (on hand) |  |  | 0.05% | 0.104%
E:Q120 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 398.7531 | 0.099688 | 0 | 0 | 2.3497 | 1.5 | 73.63 | 73.63 | 0 | 173.0075 | 73.63 | 12.1981 | 12.7385 | 1, PEI/20kW | 200 | 100 | 0.7363 | 13.4748 | 20.6164 | 20.6164 | 0 (on hand) |  |  | 0.05% | 0.06791%
E:Q121 | 3Q120 | 1 | 1.5 | 2.25 | 24.1 | 1/0 | 1 | 0.125 | 405.2531 | 0.10131 | 0 | 0 | 2.3513 | 1.5 | 73.44 | 73.44 | 0 | 172.6804 | 73.44 | 12.1352 | 12.6817 | 1, PEI/20kW | 200 | 100 | 0.7344 | 13.4161 | 20.5632 | 20.5632 | 0 (on hand) |  |  | 0.05% | 0.06808%
E:HT121 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 346.9766 | 0.83274 | 0 | 0 | 5.2327 | 0.95 | 25 | 0 | 26.3158 | 155.8186 | 14.4338 | 0.91667 | 3.8955 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.1984 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
E:VT121 | MI Corr. | 1 | 0.95 | 4.4 |  | 10ga | 1 | 1.2 | 345.4766 | 0.82914 | 0 | 0 | 5.2291 | 0.95 | 25 | 0 | 26.3158 | 155.7286 | 14.4338 | 0.91667 | 3.8932 | MI DipoleTrim | 150 | 15 | 0.10825 | 1.1977 | 3.0311 | 5.25 | 0 (on hand) |  |  | 0.1% | 0.06%
HORN PS | Horn | 2 | 3.655 | 0.932 |  | stripline | 1 |  |  |  | 0 | 0 | 0.000932 | 3.655 | 300 | 0 | 315.7895 | 700 | 300 | 83.88 | 210 | 2, PEI/240kW | 1000 | 300 | 15 | 210 | 420 | 420
[24 empty] | Upstream Service Building Power Totals: | 26.8309 | 461.6563 | 1709.762 | 2960.097
Upgrade with Most Addtional Magnets: Narrow Band Beam (very rough guess at NBR,NBN parameters)
NBB1 | EPB | 2 | 0.03 | 0.0175 |  | 500 | 2 | 0.026 | 400 | 0.0104 |  |  | 0.0454 | 0.06 | 1000 | 0 | 1052.6316 | 108.5579 | 577.3503 | 5.8333 | 108.5579 | 1, Xrex/500kW | 200 | 2500 | 5.7735 | 20.9068 | 161.6581 | 280
NBR | NBR | 1 | 0.03 | 0.0175 |  | 500 | 2 | 0.026 | 400 | 0.0104 | - | - | 0.0279 | 0.03 | 1000 | 0 | 1052.6316 | 100 | 577.3503 | 148 | 100 | 1, Xrex/500kW | 200 | 2500 | 5.7735 | 15.0735 | 161.6581 | 280
NBN | NBB | 1 | 0.03 | 0.0175 |  | 500 | 2 | 0.026 | 400 | 0.0104 | - | - | 0.0279 | 0.03 | 1000 | 0 | 1052.6316 | 100 | 577.3503 | 78 | 100 | 1, Xrex/500kW | 200 | 2500 | 5.7735 | 15.0735 | 161.6581 | 280
Notes: | [23 empty] | Additional NBB Upstream Service Building Power Totals: | 17.3205 | 51.0538 | 484.9742 | 840
1. Assumptions for transrex-type power supplies: |  |  |  |  | Regulation: +/- .05% | [18 empty] | Upstream Service Building Power Totals (w/NBB): | 44.1514 | 512.7102 | 2194.7362 | 3800.097
Water Flow: 5gpm
PS losses: 5% of load (80% of which is in water, remainder in air)
2. PEI 20kW power supplies are air-cooled
3. BND1, BND2, BND3, B2A, and B3A dipoles increased 5%, Q1 through Q9 quads increased 20%, and Q10 quad increased 100% from Transport values as safety margin.
4. As of 1/5/00 the septa for NuMI have been eliminated and replaced by a kicker located in the PS room of MI60S.
5. The MINOS magnet coils have not been designed and the NBB NBR and NBN magnets are not well known. Estimates were put in the above table as to their resistance and inductance.
6. 9/10/99: Added 2 columns to include the inductance and resistance of a passive filter for LAMB, CMAG, BND1, BND2, & BND3.
7. 9/10/99: Used optimized ramp (mathcad calculated) for rms current values for LAMB, CMAG, BND1, BND2, & BND3. | [12 empty] | Ramp Description: 1.9s cycle time, 100ms flattop, Irest= 5% of Imax, and Ireset (hysteresis) = 2% of Imax.
Mathcad generates a ramp that uses the maximum power supply voltage to ensure good power factor.
8. 1/5/00: Used optimized ramp (mathcad calculated) for rms current values for two additional bend circuits: BND2A and BND3A. | [13 empty] | Ramp Description: 1.9s cycle time, 100ms flattop, Irest= 200 amps (voltage limited).
Mathcad generates a ramp that uses the maximum power supply voltage to ensure good power factor.
9. 1/24/00: P. Lucas states that we will need similar regulation to the Left Bends, they do not have filter chokes for filtering, thus it is thought that we will not need them (this is being double-checked).
10. 2/21/00: Critical devices will be LAMB and BND1.
11. 4/25/00 Updated PS cable numbers to current beamsheet locations.
12. 7/20/00 Updated PS data, moved BND2A to MI62, and changed BND2 from 4 Xrex PS's to one MR-type. The water requirement for one main ring supply at 4,500amps peak is 24gal/min for SCR cooling. SH says PS losses should be 6 kW not 54 kW
8. 3/1/02: Used optimized ramp (mathcad calculated) for rms current values for two lam circuits and BND2 and BND3. | [13 empty] | Ramp Description: 1.9s cycle time, 100ms flattop, Irest= 5% of Imax, and Ireset (hysteresis) = 2% of Imax.
Mathcad generates a ramp that uses the maximum power supply voltage to ensure good power factor.