November 21, 1997

Contract # TW-0928

SPECIAL SPECIFICATION

SECTION 16466-S

BUSWAYS

Page

PART 1 - GENERAL

1.01 	Related Documents	2

1.02	Summary	2

1.03	Submittals	2

1.04	Quality Assurance	3

1.05	Delivery, Storage, and Handling	3

1.06 	Project Conditions	4

PART 2 - PRODUCTS

2.01	Manufacturers	4

2.02 	Busway	4

2.03 	Plug-In Units	5

PART 3 - EXECUTION

3.01 	Installation	5

3.02 	Adjusting	6

3.03 	Cleaning	6

3.04 	Testing	6

3.05 	Demonstration	7

3.06 	Protection	7

SPECIAL SPECIFICATION

SECTION 16466 - S

BUSWAYS

PART 1 - GENERAL

1.01	RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.02	SUMMARY

A.	This Section includes the following:

1.	Busways and fittings.

2.	Plug-in units.

1.03	SUBMITTALS

A.	General:  Submit the following according to the provisions of Specification Section 1300-S.

B.	Product data for each component.  Include electrical ratings, dimensions, mounting position, mounting method, vertical supports, materials, fire stops, and weather stops.

C.	Shop drawings detailing fabrication and installation of busways, including plans, elevations, sections, details of components, and attachments to other construction elements.  Detail supports and connections to building.

D.	Coordination drawings, including floor plans and sections drawn to accurate scale.  Submit with shop drawings.  Show busway layout and relationships between components and adjacent structural and mechanical elements.  Show support locations, type of support, and weight on each support.  Indicate and certify field measurements.

E.	Qualification data for firms and persons specified in the "Quality Assurance" Article to demonstrate their capabilities and experience.  Include a list of completed projects with project names, addresses, names of Architects and Owners, and other information specified.

F.	Field test reports indicating and interpreting test results relative to compliance with specified requirements.

1.04	QUALITY ASSURANCE

A.	Testing Agency Qualifications:  In addition to the requirements specified in Division 1 Section "Quality Control Services," an independent testing agency shall meet OSHA criteria for accreditation of testing laboratories, Title 29, Part 1907, or shall be a Full Member company of the International Electrical Testing Association.

1.	Testing Agency's Field Supervision:  Person currently certified by the International Electrical Testing Association or National Institute for Certification in Engineering Technologies to supervise the on-site testing specified in Part 3.

B.	Comply with NFPA 70 "National Electrical Code" for components and installation.

C.	Listing and Labeling:  Provide products specified in this Section that are listed and labeled.

1.	The Terms "Listed" and "Labeled":  As defined in the "National Electrical Code," Article 100.

2.	Listing and Labeling Agency Qualifications:  A "Nationally Recognized Testing Laboratory" (NRTL) as defined in OSHA Regulation 1910.7.

D.	Single-Source Responsibility:  All busway components shall be the product of a single manufacturer.

1.05	DELIVERY, STORAGE, AND HANDLING

A.	Deliver, store, and handle according to NEMA BU 1.1.

1.06	PROJECT CONDITIONS

A.	Field Measurements:  Verify existing dimensions by field measurements.  Verify clearances and locate obstructions within manufacturing and installation tolerances of busway.

PART 2 - PRODUCTS

2.01	MANUFACTURERS

A.	Available Manufacturers:  Subject to compliance with requirements, manufacturers offering busways that may be incorporated in the Work are the following:

1.	The Calvert Co., Inc.

2.	Cutler-Hammer Products; Eaton Corp.

3.	Electric Busway, Inc.

4.	Electrical Distribution & Control; General Electric Co.

5.	Siemens Energy & Automation, Inc.

6.	Square D Co.

B.	Substitutions: only under provisions of Section 1600-S.

2.02	BUSWAY

A.	Plug-In Busway:  NEMA BU 1, indoor application, low-impedance busway in nonventilated housing, single-bolt joints, ratings as indicated and specified.

1.	Voltage:  120/208 volts, 3 phase, 100 percent neutral capacity and 277/480 volts, 3 phase, 100 percent neutral capacity.

2.	Short-Circuit Withstand:  200,000 symmetrical rms amperes.

3.	Temperature Rise:  55 deg C above 40 deg C ambient maximum.

4.	Bus Materials:  Current-carrying copper conductors, fully insulated with Class 130C insulation except at stabs and joints; plated surface at stabs and joints.

5.	Ground Bus:  Copper.

6.	Enclosure:  Aluminum, plug-in openings at 24 inches (610 mm) on center, hinged covers over unused openings.  The enclosure shall be designed and manufactured to exclude water from entering a joint.  The test for compliance shall be water applied in a stream from a 1 inch nozzle delivering a minimum of 5 gallons per minute from 10 feet directly above the busway and contacting the busway not more than 18 inches from the joint.  Any leakage that may occur shall drain out of bottom weep holes which sshall be located in tdhe bus enclosure to eliminate the possibility of water accumulation or condensation build-up in any part of the busway system.

7.	Fittings and Accessories:  Manufacturer's standard elbows, equipment terminations, firestops, expansion fittings, spring-mounted vertical riser supports, rigid floor supports, horizontal hangers, tap fittings, and flange fittings.

2.03	PLUG-IN UNITS

A.	Molded-Case Circuit Breakers:  NEMA AB 1; hookstick-operated handle, lockable with 2 padlocks, interlocked with cover in CLOSED position; frame size, trip rating, number of poles, and auxiliary devices as indicated; interrupting capacity rating to meet available fault current, 14,000 symmetrical rms amperes minimum on 208V system, 25,000 symetrical rms amperes minimum on 480V system.

PART 3 - EXECUTION

3.01	INSTALLATION

A.	Install busway level and plumb, according to manufacturer's written instructions, shop drawings, and referenced standards.

B.	Support busway:

1.	Design each fastener and support to carry 200 pounds (90 kg) or 4 times the supported weight of the busway, whichever is greater.

2.	Support busway with not less than 3/8-inch (10-mm) steel rods.  Install side bracing to prevent swaying or movement of busway.  Modify supports after completion to eliminate strains and stresses on bus bars and housings.

3.	Fasten supports securely to building structure using channel pre-imbedded in waffle slab ribs according to structural drawing details.

C.	Install expansion fittings at locations where busway crosses building expansion joints with no more than 90 percent of the manufacturer's recommended distance between fittings.

D.	Install firestop fittings where busway penetrates fire-rated elements such as walls, floors, and ceilings.  Seal around penetration according to Division 7 Section "Firestopping" to satisfy authority having jurisdiction.

E.	Tighten busway joints with torque wrench or similar tool recommended by busway manufacturer.  Retighten joints after busways have been energized for 30 days.

F.	Install busway plug-in units.  Support connecting conduit independently of plug-in unit.

G.	Connect busway and components to wiring system and to ground as indicated and instructed by manufacturer.  Tighten connectors and terminals, including screws and bolts, according to equipment manufacturer's published torque tightening values for equipment connectors.  Where manufacturer's torquing requirements are not indicated, tighten connectors and terminals according to tightening torques specified in UL Standard 486A.

3.02	ADJUSTING

A.	Align busway runs horizontally to eliminate sags and twists.  Provide additional stiffeners if required to restrict excessive movement.

3.03	CLEANING

A.	After completing system installation, including outlet fittings and devices, inspect exposed finish.  Remove burrs, dirt, and construction debris, and repair damaged finishes including chips, scratches, and abrasions.

3.04	TESTING

A.	Testing Agency:  Provide the services of a qualified independent testing agency to perform specified field quality-control testing.

B.	Testing:  After installing busway and after electrical circuitry has been energized, demonstrate product capability and compliance with requirements.

1.	Procedures:  Perform each visual and mechanical inspection and electrical test stated in NETA Standard ATS, Section 7.4.  Investigate any insulation resistance reading less than 100 megohms divided by busway length in feet (30 megohms divided by busway length in meters).  Certify compliance with test parameters.

C.	Remove and replace malfunctioning units with new units, and retest.

D.	Infrared Scanning:  Two months after Substantial Completion, perform an infrared scan of busway including joints and plug-in units.

1.	Use an infrared scanning device designed to measure temperature or detect significant deviations from normal values.  Provide documentation of device calibration.

2.	Perform 2 follow-up infrared scans of busway 4 months and 11 months after Substantial Completion.

3.	Prepare a certified report identifying busway checked and describing results of scanning.  Include notation of deficiencies detected, remedial action taken, and rescanning observations after remedial action.

3.05	DEMONSTRATION

A.	Train Owner's maintenance personnel on procedures and schedules for startup and shutdown, troubleshooting, servicing, and preventive maintenance.

B.	Review data in the "Operating and Maintenance Manual."  Refer to Division 1 Section "Project Closeout."

C.	Schedule training with Owner through the Architect, with at least 7 days' advance notice.

3.06	PROTECTION

A.	Provide final protection and maintain conditions in a manner acceptable to Manufacturer and Installer to ensure that moisture does not enter busway prior to Substantial Completion.

END OF SECTION