July 22, 1994

Contract # TW0592

SPECIAL SPECIFICATION

SECTION 15810

HUMIDIFIERS

Page

PART 1 - GENERAL

1.01 Description.	2

1.02Related Work.	2

1.03Quality Assurance.	3

1.04References.	3

1.05Submittals..	3

1.06Delivery, Storage, and Handling..	4

PART 2 - PRODUCTS

2.01Acceptable Manufacturers.	5

2.02 Materials..	5

2.03 Jacketed Dry Steam Humidifiers..	5

PART 3 - EXECUTION

3.01 Inspection.	7

3.02 Installation/Application/Erection.	7

3.03 Field Quality Control..	8

3.04 Commissioning...	8

SPECIAL SPECIFICATION

SECTION 15810

HUMIDIFIERS

PART 1 - GENERAL

1.01	DESCRIPTION

A.  	This section describes the physical and performance requirements of humidifiers to be provided.

B.  	Include the following humidifier types:

1.  	Steam to steam evaporative humidifier.

C.  	Refer to other Division-15 sections for piping, ductwork, specialties, etc., required external to humidifiers for installation.

D.  	Provide the following electrical work as work of this section, complying with requirements of Division-16 sections:

1.  	Control wiring between field-installed controls, indicating devices, and humidifier control panels.

a. 	Control wiring specified as work of Division-15 for Automatic Temperature Controls is work of that section.

1.02	RELATED WORK

A.  	Section 01300

B.  	Section 15010

C.  	Section 15051

D.  	Section 15401

E.  	Section 15891

F.  	Section 15995

1.03	QUALITY ASSURANCE

A.  	Test and rate humidifiers in accordance with ARI 620 "Standard for Self-Contained Humidifiers".

B.  	Install humidifiers in accordance with ARI 630 "Standard for Selection, Installation, and Servicing of Humidifiers".

C.  	Provide electrical components required as part of humidifiers, which are listed and labeled by Underwriter's Laboratories (UL) and comply with National Electrical Manufacturer's Association (NEMA) Standards.

D.  	Comply with National Fire Protection Association (NFPA) 70, "National Electrical Code" as applicable to installation and electrical connections of ancillary electrical components of humidifiers.

1.04	REFERENCES

A.  	ARI 620, Standard for Self-Contained Humidifiers.

B.  	ARI 630, Standard for Selection, Installation, and Servicing of Humidifiers.

C.  	UL and NEMA Standards.

D.  	NFPA 70, National Electrical Code.

1.05	SUBMITTALS

A.  	Make submittals according to this Section, Section 15010, and Section 01300.

B.  	Submit manufacturer's technical product data, including rated capacities of selected model clearly indicated, weights, installation and start-up instructions, and furnished specialties and accessories.

C.  	Submit manufacturer's assembly-type shop drawings indicating dimensions, weight loadings, required clearances, and methods of assembly of components.

D.  	Submit manufacturer's electrical requirements for power supply wiring to humidifiers.  Submit manufacturer's ladder-type wiring diagrams for interlock and control wiring.  Clearly differentiate between portions of wiring that are factory-installed and portions to be field-installed.

E.  	Submit maintenance data and parts list for each humidifier, control, and accessory; including "trouble-shooting" maintenance guide.  Install this data, product data, shop drawings, and wiring diagrams in maintenance manual; in accordance with Section 01300.

1.06	DELIVERY, STORAGE, AND HANDLING

A.   	See Section 15010.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.  	Provide humidifiers of one of the following:

1.  	Dri-Steem Humidifier Co.

2.  	Herrmidifier Co., Inc.

3.  	Spirax Sarco.

2.02	MATERIALS

A.  	Except as otherwise indicated, provide packaged humidifiers and ancillary equipment with manufacturer's standard materials and components as indicated by published product information, designed and constructed by manufacturer, and as required for complete installation.

2.03	JACKETED DRY STEAM HUMIDIFIERS

A.  	General:  Provide evaporative, single-tube, dry steam humidifiers as indicated on the Drawing Schedule and specified herein.

B.  	Vaporizing chamber, cover and fittings shall be constructed of stainless steel with heli-arc welded seams.  Vaporizing chamber cover and/or front clean-out plate shall be easily removable for access to the vaporizing chamber for physical removal of mineral buildup.

C.  	Heat exchanger shall be constructed of stainless steel with heli-arc welded seams and teflon coated.  The design of the exchanger shall be two alternately spaced paralleled rows of tubes between a supply and return header.

D.  	Electronic water level control system shall provide for automatic refill of the humidifier.  System shall consist of:

1.  	A water level sensing unit comprised of three coated stainless steel probes screwed into a threaded probe head.  Probe head shall incorporate probe isolation skirts and be mounted on the face plate of the vaporizing chamber.

2.  	A solenoid operated fill valve factory mounted on the face plate.

3.  	An electronic level control board mounted and wired in the control panel.

E.  	Surface skimmer shall be provided which is field adjustable to provide for optimum mineral removal with minimum water waste.

F.  	Appropriate number and length of inverted U-Tubes shall be provided for (H-2) steam dispersion into duct.  U-Tube shall allow for mounting the humidifier directly under the duct or inside an air handler.  Tubes shall be constructed of 1 1/2 in. O.D. stainless steel tubing and shall be fitted with two rows of high temperature inserts arranged to discharge the stream in a V-pattern.  Each insert shall extend through and into the center of the dispersion tube and incorporate a properly sized calibrated orifice.  Cover of the humidifier shall be fitted with matching connections so the U-Tube can be connected with the provided sections of vapor hose and stainless steel hose clamps.  Two-piece escutcheon plates for sealing duct openings around the U-Tubes shall be provided.

G.  	The control cabinet shall be factory mounted on humidifier.  Sub-panel shall be enclosed in a UL listed JIC enclosure and contain a control circuit transformer, 120 V power block, numbered terminal strip, electronic level control board and interconnecting wiring.

H.  	Valve shall be a normally closed modulating type with modified linear flow characteristics and electronic actuator.  Valve trim shall be stainless steel.

I.  	Humidifier shall be provided with a float and thermostatic trap and a steam supply line strainer.

J.  	Motor driven brass bodied drain valve shall be factory mounted and wired.  Timer and drain controls shall be incorporated into electronic level control system which provides for drain and flush at timed intervals.  Frequency and duration of drain shall be field adjustable.

K.  	Humidifiers (H-1, 2, &3) shall be supplied with appropriate quantity of vapor hose kits which allow for remote mounting of the humidifier.  Each kit shall consist of one 20 ft. section of 1 1/2 in. I.D. reinforced vapor hose, two stainless steel hose clamps, a two-piece escutcheon plate and one 1 1/2 in. O.D. stainless steel dispersion tube.  Dispersion tube shall extend the width of the duct and shall be fitted with two rows of high temperature inserts arranged to discharge the steam in V-pattern.  Each insert shall extend through and into the center of the dispersion tube and incorporate a properly sized calibrated orifice.

L.  	Diaphragm operated, air flow proving switch shall be provided for field installation.  Switch shall have an adjustable control point range of 0.05 in. W.C. to 12 in. W.C. and be rated for 1/4 H.P. at 125 VAC.

M.  	Humidifier shall be covered with 3/4 in. thick rigid foam duct insulation.  Insulation shall be covered with reinforced aluminum foil.  All surfaces except front panel shall be covered.

PART 3 - EXECUTION

3.01	INSPECTION

A.  	Inspect areas and conditions under which humidifiers are to be installed.  Do not proceed with work until unsatisfactory conditions have been corrected in manner acceptable to Installer.

3.02	INSTALLATION/APPLICATION/ERECTION

A.  	Install humidifier, vaporizing chamber, and vapor hose where indicated, in accordance with equipment manufacturer's written instructions, and with recognized industry practices, to ensure that evaporative humidifiers comply with requirements and serve intended purposes.

B.  	Provide access space around humidifiers for service as indicated, but in no case less than that recommended by manufacturer.

C.  	Provide supports from substrate for humidifiers as indicated and in accordance with manufacturer's installation instructions.

D.  	Install electrical devices furnished by manufacturer but not specified to be factory-mounted.  Furnish copy of manufacturer's wiring diagram submittal to Electrical Installer.

1.  	Verify that electrical wiring installation is in accordance with manufacturer's submittal and installation requirements of Division-16 sections.  Do not proceed with equipment start-up until wiring installation is acceptable to equipment Installer.

E.  	See Section 15891.  Provide air-tight seal at each penetration of humidifiers into ductwork.  Provide access door as recommended by manufacturer for service.

F.  	See Section 15051.  Provide separate valved branch to supply humidifier from top of dripped steam runout.

G.  Provide electrical equipment ground for electrically-operated humidifiers and components.

H.  	Upon completion of installation and prior to initial operation, test and demonstrate that air humidification equipment is leak-tight.

I.  	Repair or replace air humidification equipment as required to eliminate leaks, and retest as specified to demonstrate compliance.

3.03	FIELD QUALITY CONTROL

A.  	Start-up humidifiers in accordance with manufacturer's instructions.

B.  	Clean factory-finished surfaces.  Repair any marred or scratched surfaces with manufacturer's touch-up paint.

3.04	COMMISSIONING

A.  	Provide labor, material, equipment, etc., required to facilitate the commissioning process.  Perform form tests and verification procedures required by the commissioning process when requested by the Commissioning Authority and directed by the General Contractor.  See Section 15995.

END OF SECTION