Helsinki, August 15 2000

Dear MSG members,

Working on draft 4 and performing the pre-integration modelling in frame of BS-7 "HVAC Performance Validation" project we have reviewed IFC R2.X model and encountered following problems, which could have general impact on the IFC-Model, specially in the HVAC Domain:

- BS-7 project is going to extend already defined property sets because of their incompleteness (e.g Pset_AirHandler, Pset_Boiler etc.). BS-7's draft 4 documents in IAI FTP/Web site contain proposed extensions and we propose that they would be accepted already in R2.x. The same kind of extensions we have made for IfcValve, PsetSensor, Pset_ControlDamper and Pset_FluidMover, so they they are proposed to be accepted in a same manner in R2.x.

- Additionally, we have defined new property sets for several components (e.g Pset_Radiator, Pset_CooledBeam etc.) to include these essential types  of IfcFlowEquipment object referring to these property sets. We also propose to expand functionality of R2.x to include these types. The same kind of extension we have made for IfcActuator, IfcController and IfcDamper so they are proposed to be accepted in a same manner in R2.x.

- We think that the property sets definitions are very generic, but they do not allow references to object types . Therefore, we propose to consider if all existing property sets describing HVAC components would be defined as IFC-classes. Such a class would inherit e.g. from IfcFlowEquipment class and hold component specific data such as references to other components (e.g. Pset_AirHandler refers using the attribute Fans to IfcFlowEquipment objects describing fans). We are convinced that it would improve modelling work, because it would simplify adding new components to the existing schema. Using inheritance it would not be necessary to change any existing class for purposes of defining new subclasses (see above).

- The property set Pset_HvacSensor, it is a new class released as 2.0, defines an attribute Range as IfcReal. Typically, range is expressed explicitly by a pair of values (maximum and minimum range). We propose its Data Type would be changed accordingly.

- We have been looking for "clean" way how to extend Pset_Coil to include electrical coil. The main difference is that an electrical coil has also to point to common electrical appliance properties. We propose that such an extension could also be made as a part of R2.x.

- For sound pressure levels R2.x includes the property set Pset_SoundPressureLevels, in which pressure levels are measured in decibels at a reference pressure of 20 microPascals for standardised octave band frequencies. There are also applications in which sound power levels are needed in decibels at a reference power of 10-12 Watts for the standardised octave band frequencies. To expand its functionality we propose to include the corresponding property set Pset_SoundPowerLevels in R2.x.

Please find attached also an additional Excel document that describes BS extensions in the context of IFC object hierarchy.

BS-7 project team

| Schema | Entity / Type / Property Set | Description | Additional description of extension | Proposed solution |
| --- | --- | --- | --- | --- |
| IfcHvacDomain | IfcValve | needed extension for inherent characteristic |  | IfcInherentCharateristicEnum (Linear, Exponential, IfcPolyline, Other, NotKnown, Unset) |
|  | IfcController | extend controller type enumeration to include heating curve. A heating curve defines the dependency between outside temperature and inlet temperature of a radiator heating system |  |  |
|  | IfcActuator | extend actuator type enumeration to include the thermostatic actuator |  |  |
|  | IfcDamper | extend damper type enumeration to include the closing damper |  |  |
| IfcSharedBldgServiceElements | IfcFlowEquipment | extend flow equipment type enumeration to include following components: cooled beam, heat recovery unit, humidifier, ducted silencer, radiator |  |  |
|  | Pset_Boiler | make this property set an IFC class, in order to improve extensibility of IFC model. |  |  |
|  |  | needed extension for operating mode enumeration | reference to the operating mode of the boiler | IfcEnumeratedProperty (Fix, TwoStep, Modulating, Other, NotKnown, Unset) |
|  |  | needed extension for standard thermal output | thermal output of a boiler related to standard test conditions | IfcSimplePropertyWithUnit (IfcPowerMeasure) |
|  |  | needed extension for standard inlet water temperature | inlet water temperature related to standard test conditions | IfcSimplePropertyWithUnit (IfcThermodynamicTemperatureMeasure) |
|  |  | needed extension for standard outlet water temperature | outlet water temperature related to standard test conditions. | IfcSimplePropertyWithUnit (IfcThermodynamicTemperatureMeasure) |
|  |  | needed extension for standard maximum load | maximum energy load rate related to standard test conditions | IfcSimplePropertyWithUnit (IfcPowerMeasure) |
|  |  | needed extension for minimum load | minimum energy load rate | IfcSimplePropertyWithUnit (IfcPowerMeasure) |
|  |  | needed extension for maximum flue gas temperature | flue gas temperature at maximum load | IfcSimplePropertyWithUnit (IfcThermodynamicTemperatureMeasure) |
|  |  | needed extension for part load flue gas temperature | flue gas temperature at part load | IfcSimplePropertyWithUnit (IfcThermodynamicTemperatureMeasure) |
|  |  | needed extension for water capacity | boiler water capacity. | IfcSimplePropertywithUnit (IfcVolumeMeasure) |
|  |  | needed extension for lambda | stoichiometic fuel/air ratio | IfcSimpleProperty (IfcReal) |
|  | Pset_AirHandler | make this property set an IFC class, in order to improve extensibility of IFC model. |  |  |
|  |  | needed extension for heat recovery units | Bag of zero or more references to an IfcFlowEquipment object of type HeatRecoveryUnit that defines the heat recovery unit(s) that are used by the AirHandler | IfcComplexProperty (BAG [0:?] OF IfcObjectReference (IfcFlowEquipment)) |
|  |  | needed extension for humidifiers | Bag of zero or more references to an IfcFlowEquipment object of type Humidifier that defines the humidifier(s) that are used by the AirHandler | IfcComplexProperty (BAG [0:?] OF IfcObjectReference (IfcFlowEquipment)) |
|  |  | needed extension for air leakage rate | Air leakage of the casing of air handler subjected to air pressure (under a standard test) | IfcSimplePropertyWithUnit (IfcVolumetricFlowrateMeasure) |
|  |  | needed extension for transmitted sound | Noise transmitted into the ductwork (under a standard test such as ISO 3741, ISO 3744, ISO 9614, ISO 5136). Reference to a property set Pset_SoundPowerLevels | IfcPropertySet (Pset_SoundPowerLevels) |
|  |  | needed extension for emitted sound | Airborne noise emitted by the casing of the unit (under a standard test such as ISO 3741, ISO 3744, ISO 3746, and ISO 9614). Reference to a property set Pset_SoundPowerLevels | IfcPropertySet (Pset_SoundPowerLevels) |
|  |  | needed extension for thermal insulation | Thermal insulation of the casing | IfcPropertySet (Pset_Insulation) |
|  | Pset_Coil | make this property set an IFC class, in order to improve extensibility of IFC model. |  |  |
|  |  | needed extension for heat source type enum | Heat source of coil. If It is an electric coil, reference to a property set Pset_ElectricCoil | IfcEnumeratedProperty (Fluid, Electric, Steam, Other, NotKnown, Unset) |
|  |  | needed extension for temperature efficiency | Temperature efficiency (under a standard test) | IfcSimpleProperty (IfcReal) |
|  |  | needed extension for entering air temperature | List of air temperatures of entering conditions; the list consists of dry bulb followed by wet bulb | IfcComplexProperty (LIST [1:2] OF IfcSimpleProperty (IfcSimplePropertyWithUnit (IfcThermodynamicTemperatureMeasure))) |
|  |  | needed extension for leaving air temperature | List of air temperatures of leaving conditions; the list consists of dry bulb followed by wet bulb | IfcComplexProperty (LIST [1:2] OF IfcSimplePropertyWithUnit (IfcThermodynamicTemperatureMeasure)) |
|  |  | needed extension for air flow rate | Air flow rate | IfcSimplePropertyWithUnit (IfcVolumetricFlowrateMeasure) |
|  |  | needed extension for air pressure drop | Air pressure drop at the related air flow rate | IfcSimplePropertyWithUnit (IfcPressureMeasure) |
|  |  | needed extension for regenerated sound | Regenerated sound (under a standard test). Reference to a property set Pset_SoundPowerLevels | IfcPropertySet (Pset_SoundPowerLevels) |
|  |  | needed extension for sound attenuation | Sound attenuation (under a standard test). Reference to a property set Pset_SoundPowerLevels | IfcPropertySet (Pset_SoundPowerLevels) |
|  | Pset_ControlDamper | make this property set an IFC class, in order to improve extensibility of IFC model. |  |  |
|  |  | needed extension for inherent characteristic enum | Inherent characteristic of the control damper | IfcEnumeratedProperty (Linear, Exponential, IfcPolyline, Other, NotKnown, Unset) |
|  |  | needed extension for regenerated sound | Regenerated sound (under a standard test). Reference to a property set Pset_SoundPowerLevels | IfcPropertySet (Pset_SoundPowerLevels) |
|  |  | needed extension for sound attenuation | Sound attenuation (under a standard test). Reference to a property set Pset_SoundPowerLevels | IfcPropertySet (Pset_SoundPowerLevels) |
|  |  | needed extension for minimum operating torque | Minimum operating torque (under a standard test) | IfcPropertySetWithUnit (IfcTorqueMeasure) |
|  |  | needed extension for maximum allowable torque | Maximum allowable torque (under a standard test such as EN 1751) | IfcPropertySetWithUnit (IfcTorqueMeasure) |
|  | Pset_FluidMover | make this property set an IFC class, in order to improve extensibility of IFC model. |  |  |
|  |  | needed extension for flow vs. pressure curve | Fluid flow rate versus pressure curve (under a standard test) | IfcComplexProperty (LIST [0,?] OF (x,y)-points (IfcSimplePropertyWithUnit (IfcVolumetricFlowrateMeasure), IfcSimplePropertyWithUnit (IfcPressureMeasure))) |
|  |  | needed extension for flow vs. power curve | Fluid flow rate versus power curve (under a standard test) | IfcComplexProperty (LIST [0,?] OF (x,y)-points (IfcSimplePropertyWithUnit (IfcVolumetricFlowrateMeasure), IfcSimplePropertyWithUnit (IfcPressureMeasure))) |
|  | Pset_HVACSensor | make this property set an IFC class, in order to improve extensibility of IFC model. |  |  |
|  |  | needed extension for time constant | The time constant of sensor | IfcSimplePropertyWithUnit (IfcTimeMeasure) |
|  |  | Instead of Ranger use pair (a pair of values (maximum and minimum range). |  |  |
|  | Pset_ElectricActuator | make this property set an IFC class, in order to improve extensibility of IFC model. |  |  |
|  |  | needed extension for common electrical appliance properties | Reference to the 'parent' SharedPropertySet (Pset_ElectricalApplianceCommon). Contains the shared values for this type -- properties that are stored for all types of ElectricalAppliances | IfcPropertySet (Pset_ElectricalApplianceCommon) |
|  |  | needed extension for hysteresis | Difference between start and stop operation | IfcSimpleProperty (IfcReal) |
|  |  | needed extension for torque | Torque | IfcPropertySetWithUnit (IfcTorqueMeasure) |
|  |  | needed extension for stroke time | Stroke time | IfcSimplePropertyWithUnit (IfcTimeMeasure) |
|  | Pset_AirFilter | make this property set an IFC class, in order to improve extensibility of IFC model. |  |  |
|  |  | needed extension for regenerated sound | Regenerated sound (under a standard test). Reference to a property set Pset_SoundPowerLevels | IfcPropertySet (Pset_SoundPowerLevels) |
|  |  | needed extension for sound attenuation | Sound attenuation (under a standard test). Reference to a property set Pset_SoundPowerLevels | IfcPropertySet (Pset_SoundPowerLevels) |
|  |  | needed extension for dust holding capacity | The amount of dust by weight retained by a filter (under a standard test such as EN779) | IfcSimplePropertyWithUnit (IfcMassMeasure) |

# Comments

Poista tämä, tuntuu turhalta selittelyltä

Korvaa: "...include these essential types..."