## M.E. GROUP PRESENTATION

R. DORTWEGT

June 12, 2001

SUMMARY

- Linac water systems

  - Closed loop water stations

  - Other systems

  - Other work for Linac customers

- SR vacuum chamber water

- Process water quality

- PAR vacuum chambers

- Pressure Technology and Safety Committee (PTSC)

- Mechanical safety

LINAC WATER SYSTEMS

- Closed loop water stations provide temperature conditioning for:

  - Waveguides

  - Accelerating structures

  - SLED’s

  - RF loads

  - RF windows

- Other systems installed to provide D.I. water for:

  - P.C. Gun

  - Laser

  - 75oF water from primary loop for new power supplies for modulators

  - APS injection guns (future) – 2 separate loops for guns

- Assistance for Linac “customers”

  - Mostly in the form of assistance with flowmetering and instrumentation

LINAC CLOSED LOOP SYSTEMS

- History

  - Built by original APS Linac Group

  - Temperature stability an issue at commissioning

  - Change to Johnson Controls

  - Big improvements early on were:

      - Direct immersion RTD’s (improves response time)

      - Beginning of realization that loop tuning was important

  - Control valve tuning class (you can adjust only the errors you can detect)

  - Understanding the impact of signal resolution (i.e. detecting really small temperature changes)

  - Prototype fix (stand-alone controller from Honeywell)

  - Implementation of Allen-Bradley controls (Rick)

  - Communications with EPICS (Rick with help from ASD Controls Group)

### LINAC CLOSED LOOP SYSTEMS

- Important things to understand

  - Feedback loop principles

  - Reduce time lag of error signal processing

  - Direct immersion RTD vs. RTD in a thermowell

  - Resolution of temperature changes

- New requirements

  - New water station to be built in FY-02 for Linac Sector 6

    - Provide separate water loop for SLED (operate at different temperature)

    - Quieter

    - Smaller (??)

    - All PLC control

    - Location, location, location!!!!!

- Improve flow metering on closed loop stations using V-cones and DPT’s

    - Better reliability

    - Install DPT’s in tunnel to avoid failure in tunnel

OTHER LINAC SYSTEMS

- GOAL:	to get away from custom designed systems (a la P.C. Gun) for miscellaneous items such as guns, lasers, etc.

    - Less costly to obtain

    - Less lead time to implement

    - Standardized design

    - Repairs do not impact larger PW secondary system

    - ~K$10

    - First unit for gun testing work in Linac RF Test Room (delivery expected in August, ’01)

    - Vendor is Bay Voltex

    - Standard design modified to achieve 140oF

    - Stability to /-0.1 oC (0.18F)

    - Flow monitoring and water treatment done in-house

    - Remote monitoring/control via EPICS

- Low pressure / cool water for Linac components from primary water (75F)

    - Pumps P-PRMOD-1/2   (75 psig)

    - Same pumps as SRVC cooling skids

    - Pressure and temperature not as severe as secondary system

    - All capacity taken by new modulator power supplies, RF loads and window

#### ASSISTANCE FOR LINAC “CUSTOMERS”

- FLOW METERING PROJECTS

  - Modulator power supplies

  - Klystrons

- Use of V-cones and Yokagawa DP transmitters

  - Accuracy 1% or better

  - Reliability

  - 10:1 turndown

  - Standardization of components across ASD-ME and other groups

  - No moving parts in water stream

  - Built by our own technicians

SR VACUUM CHAMBER COOLING

- COOLING SKIDS

  - One skid for two SR sectors (20 skids)

  - Mechanical mezzanine

  - Separate water stations for aluminum vacuum chambers

  - 52 gpm @ 45 psig nominal operating point

  - Low maintenance

  - Will need to start replacing “sealed for life” bearings

- FUTURE IMPROVEMENTS TO COOLING SKIDS

  - “Clean-up” slipstream piping through resin tanks

  - Install permanent resin tank for till connection

  - Upgrade system monitoring

  - Allen-Bradley temperature controls (95% complete)

  - Disconnect switches for individual pumps

SR VACUUM CHAMBER BAKEOUT

- BAKEOUT SKIDS

  - One skid for two SR sectors (20 skids)

  - SR Utility Aisle

  - Uses same distribution piping as cooling skids

  - ~25 gpm per sector at 110 psig and 135oC (275 oF)

  - Originally designed for 150oC (300 oF)

  - Vacuum group never uses temps that high

  - High pressure to keep water from boiling and dissolved air from flashing

  - Must be used with mobile cart for water purification

- FUTURE IMPROVEMENTS TO BAKEOUT SKIDS

  - Upgrade and automate monitoring

  - Install permanent wiring for beacon system

  - Install permanent signage for bakeout system

- MOBILE CART

  - Used only when bakeout is ongoing

  - HX for heat recovery

  - Pumps 3 gpm of “clean” water from cooling skid to bakeout system

  - Returns 3 gpm of “bakeout” water to cooling system to be purified

WATER QUALITY AT APS

- Copper corrosion continues to be an issue at APS, but at manageable rates

- Manageable corrosion rates have been achieved through filtration and oxygen control

- Information on deaeration system at Building 450

  - ASD invested ~K$500 on improving this system

  - Tripled the throughput (now 450 gpm)

  - DO less than 5ppb coming out of degassifier

  - System DO normally between 5-10ppb

  - Transferred responsibility to PFS in February of this year

- Focal point for ordering filters and chemical analyses

  - Filters from US Filter-Filtration

  - Analyses from McCrone Lab (Westmont)

- What we have learned about pH of DI water and impact on corrosion rate

- DI water production

  - Change to RO production in 1998

  - System is leased from vendor with fixed monthly charges

  - Learned that we must do maintenance only during 1st week of shutdown

PAR VACUUM CHAMBERS

- Evaluation of spares inventory indicates a need for attention

  - Several chambers not complete

  - A few chambers not compatible with existing geometry

- Inconel 625 formed/machined plate still on hand from 1993 effort

- Bill Toter has all the E-B welding parameters on file

- Learning how to work on “hot’ chambers

ANL-E PRESSURE SAFETY COMMITTEE

- Committee was formed around 7-8 years ago

- Goal was to develop a Pressure Safety Manual (PSM) for ANL-E

  - Based on ASME

  - DOE order 440.1 (mandatory)

- First draft manual was complete ~2-3 years ago (done mostly by the Chair at the time)

- Committee and divisional revolt (no buy-in)

- New committee chair appointed (Bill Toter)

- Draft manual completed two months ago

  - Does not give rules on design and fabrication

  - Does give guidelines on what things need to be considered

  - Responsibility for pressure safety put on division Division director & line management

ANL-E PRESSURE SAFETY COMMITTEE (cont.)

- Every division to appoint a Pressure System Advisor (PSA)

- Pressure systems classified into 3 classes:

  - Category A:	significant risk

  - Category B:	relatively low or limited risk

  - Category C:	low-risk systems

- Anticipate all (or most) of our systems to be Category B and C

- The biggest impact on ASD will be:

  - Documenting and testing current systems to ensure compliance

  - Implementing work rules that ensure compliance

ASD MECHANICAL SAFETY COMMITTEE

- R. Dortwegt participation upon request by Jim Lang

- Current effort includes noise reduction of pump motors in building 420 & 411

  - Building 420:

    - Current motors ~90-92dBA (noise from all 3 operating simultaneously)

    - New motors (68dBA individually) could reduce noise to 75-80dBA composite

    - Noise generated mostly from fan blades

    - Motors are larger, so either have to raise pump on baseplate or modify baseplate

    - Figure $2500 per motor

  - Building 411:

    - Current motors ~89dBA (noise from all 3 operating simultaneously)

    - New motors (79dBA individually) would not reduce noise much

    - Need another quote for quieter motor

MECHANICAL SUPPORT

- Lots of help received

  - Technician labor

  - From other staff

  - From Jodi

  - Thoughtfulness when needed

  - Cheerfulness

  - Chop-busting even when not needed

- Many thanks

# Text boxes

Linac Closed Loop Water Station

Typical Example of “Off-the-shelf” System planned for use with new APS Guns

Layout of Components for Klystron Flowmeter Upgrade in Linac

Photo of Components for Klystron Flowmeter Upgrade in Linac

Cooling Skid for SR Vacuum Chambers

Bakeout Skid for SR Vacuum chambers

Mobile  Cart for Maintaining Cleanliness of DI Water During SR Vacuum Chamber Bakeout