## Sheet1
PF-5060 |  | C6F14 |  |  | Prepared by Vic Vacek
t | r | n | n | m | m | Cp | k | Prandtl | b | s | FOM
C | kg m-3 | cSt | m2 s-1 | kg m-1 s-1 | cPoise | J kg-1 C-1 | W m-1 C-1 |  | C-1 | N m-1
-30 | 1818.3 | 0.93537 | 9.3537e-07 | 0.0017008 | 1.7008 | 967.38 | 0.0633 | 25.992 | 0.0014354 | 15.3965 | 15507.9627
-25 | 1805.25 | 0.84412 | 8.4412e-07 | 0.0015238 | 1.5238 | 975.15 | 0.06275 | 23.6809 | 0.0014458 | 14.9344 | 16078.6793
-20 | 1792.2 | 0.76603 | 7.6603e-07 | 0.0013729 | 1.3729 | 982.92 | 0.0622 | 21.6949 | 0.0014563 | 14.475 | 16631.7657
-15 | 1779.15 | 0.69862 | 6.9862e-07 | 0.001243 | 1.243 | 990.69 | 0.06165 | 19.9738 | 0.001467 | 14.0184 | 17168.1112
-10 | 1766.1 | 0.64002 | 6.4002e-07 | 0.0011303 | 1.1303 | 998.46 | 0.0611 | 18.4714 | 0.0014778 | 13.5647 | 17688.2553
-5 | 1753.05 | 0.58876 | 5.8876e-07 | 0.0010321 | 1.0321 | 1006.23 | 0.06055 | 17.1519 | 0.0014888 | 13.1139 | 18192.4434
0 | 1740 | 0.54367 | 5.4367e-07 | 0.00094598 | 0.94598 | 1014 | 0.06 | 15.987 | 0.0015 | 12.666 | 18680.684
5 | 1726.95 | 0.50383 | 5.0383e-07 | 0.00087008 | 0.87008 | 1021.77 | 0.05945 | 14.9541 | 0.0015113 | 12.2211 | 19152.8016
10 | 1713.9 | 0.46848 | 4.6848e-07 | 0.00080293 | 0.80293 | 1029.54 | 0.0589 | 14.0348 | 0.0015228 | 11.7794 | 19608.486
15 | 1700.85 | 0.43701 | 4.3701e-07 | 0.00074329 | 0.74329 | 1037.31 | 0.05835 | 13.2138 | 0.0015345 | 11.3408 | 20047.3348
20 | 1687.8 | 0.40891 | 4.0891e-07 | 0.00069016 | 0.69016 | 1045.08 | 0.0578 | 12.4787 | 0.0015464 | 10.9054 | 20468.8911
25 | 1674.75 | 0.38374 | 3.8374e-07 | 0.00064266 | 0.64266 | 1052.85 | 0.05725 | 11.8189 | 0.0015584 | 10.4734 | 20872.6738
30 | 1661.7 | 0.36114 | 3.6114e-07 | 0.0006001 | 0.6001 | 1060.62 | 0.0567 | 11.2254 | 0.0015707 | 10.0447 | 21258.2049
PF-5060 t: Forced convection heat transfer performance, liquid only; Prepared by Vic Vacek k: FOM: Figure of Merit |  |  |  | 3
Turbulent internal flow; FOM = r0.8 k0.6 Cp0.4 m-0.4
Note: h = FOM 0.023 V0.8 D-0.2
t, C | -30 | -25 | -20 | -15 | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30
FOM | 15507.9627 | 16078.6793 | 16631.7657 | 17168.1112 | 17688.2553 | 18192.4434 | 18680.684 | 19152.8016 | 19608.486 | 20047.3348 | 20468.8911 | 20872.6738 | 21258.2049
Footnotes
PF-5060 t: [0]; PF-5060 r: T, units of Kelvins; t, units of degrees C |  | 1 | 3
PF-5060 t: [1]; PF-5060 r: Based on ASTM standard D-341 correlations (original viscosity in cSt) |  | 2
PF-5060 t: [2]; PF-5060 r: Based on kinematic viscosity from ASTM D-341 and density |  | 3
[3] | Based on linear relationship for r vs t: r = A - B t
[4] | Conversion: 1 cP = 10-6 (m2 s-1)
[5] | Based on linear relationship for Cp vs t: Cp = A - B t
[6] | Based on linear relationship for k vs t: k = A - B t
[7] | Prandtl = Cp m k-1
[8] | b, coefficient of volumetric expansion: (dr/dt)/r.
[9] | Based on relationship between s and T: s = A (1-Tr)B; from McLure et al, J Chem Soc, Faraday Transactions, 1, 1982, 78, 2251 - 2257.
[10] | Based on linear relationship between log (PV) vs T-1: log (torr) = A - B/T; 1 torr = 133.3 Pa
[11] | Based on Mouromtseff number; Saylor et. al., IEEE Transactions on Comp, Hyb, and Mfg Tech, Vol 11, No 4, Dec 1988
Viscosity coef.
2e-07
2e-05
Pixel stave test ---> to remove from 80 W/cm2 to 140 W/cm2; Single fluid - C6F14 liquid !
SET D | SET t in | t out | t aver | D_t |  | t w
3
| -20 | -17 | -18.5 | 3 |  | -19.8
C6F14 m: Turbulent F. |  |  | [cm]
PF-5060 t: dh; PF-5060 r: dh; C6F14 n: T_ID; C6F14 m: 0.316 |  | For L = | 80
[mm] | [m] | [mm]
PF-5060 t: 3.6; PF-5060 r: 0.0036; C6F14 n: 2.5; C6F14 m: Laminar F. |  |  | [m]
C6F14 m: 64 |  |  | 0.8
[12 empty] | Pressure | Pressure
[12 empty] | drop | drop
Q | Cp | D_t | r | m | m | V | V | V | c | m | Re | over_L | over_L | mw
[W=Js-1] | [J kg-1C-1] | [C] | [kg m-3] | [kg/s] | [g/s] | [m3s-1] | l / s | l/min | [m s-1] | [kg m-1 s-1] | [-] | [Pa] | [bar]
80 | 1014 | 3 | 1788.285 | 0.026298 | 26.2985 | 1.4706e-05 | 0.014706 | 0.88236 | 1.4455 | 0.0013385 | 6952.7477 | 14367.4919 | 0.14367 | 0.0013744
100 | 1014 | 3 | 1788.285 | 0.032873 | 32.8731 | 1.8382e-05 | 0.018382 | 1.1029 | 1.8069 | 0.0013385 | 8690.9346 | 21231.1483 | 0.21231 | 0.0013744
120 | 1014 | 3 | 1788.285 | 0.039448 | 39.4477 | 2.2059e-05 | 0.022059 | 1.3235 | 2.1683 | 0.0013385 | 10429.1215 | 29210.6125 | 0.29211 | 0.0013744
140 | 1014 | 3 | 1788.285 | 0.046022 | 46.0224 | 2.5735e-05 | 0.025735 | 1.5441 | 2.5296 | 0.0013385 | 12167.3084 | 38255.8227 | 0.38256 | 0.0013744
[7 empty] | Pr |  | l
[5 empty] | L/D | 222.2222 | x2 | 0.0029 | x | -0.0001
[7 empty] | x | -0.2375 |  | 0.06
15.958
Turbulent flow |  |  | r: Prediction of the HTC for C6F14
[6 empty] | Colburn |  | Seider -Tate |  | Gnielinski
[6 empty] | 0.023 |  | 0.027 |  | 0.012
|  | Q | Re | Pr | l | NuD | HTC | NuD | HTC | NuD | HTC
|  | [W=Js-1] | [-] | [-] | W m-1 C-1 | [-] | [W/m2K] | [-] | [W/m2K] | [-] | [W/m2K]
|  | 80 | 6952.7477 | 21.3443 | 0.06185 | 92.7183 | 1592.9523 | 88.334 | 1517.6267 | 78.4306 | 1347.481
|  | 100 | 8690.9346 | 21.3443 | 0.06185 | 110.8393 | 1904.2799 | 105.598 | 1814.2326 | 97.6841 | 1678.2679
|  | 120 | 10429.1215 | 21.3443 | 0.06185 | 128.2445 | 2203.3109 | 122.1802 | 2099.1234 | 116.44 | 2000.5047
|  | 140 | 12167.3084 | 21.3443 | 0.06185 | 145.0761 | 2492.4888 | 138.216 | 2374.627 | 134.792 | 2315.8008
Colburn Equation
NuD=(HTC*D)/l = 0.023 Re4/5Pr1/3
Seider -Tate Equation:
NuD=(HTC*D)/l = 0.027 Re4/5Pr1/3(m/mw)0.14
Gnielinski Equation:
NuD=(HTC*D)/l = [(f/2)(Re - 103)Pr]/[1+12.7(f/2)0.5(Pr0.66-1)]
where "f" is supplied from the diagram of the friction factor
or for 1.5<Pr<500 and 3 103 < Re < 106 one can use:
NuD=(HTC*D)/l =0.012(Re0.87-280)Pr0.4