USDA-Rural Development

MN 1780 Guide 6

(Rev 12/04)

MINNESOTA PRELIMINARY ENGINEERING REPORT SUPPLEMENT

FOR

WATER, WASTEWATER, STORM WATER AND SOLID WASTE PROJECTS

- GENERAL

  - This supplement is to be used in addition to USDA RUS Bulletins 1780-2, 1780-3, 1780-4 and 1780-5, Preliminary Engineering Reports.

  - Type of report to prepare: Projects that do not include funding from MPCA (i.e., ISTS, Petrol-Fund, etc.) or the Sate Revolving Loan Fund only require the preparation of a Preliminary Engineering Report (PER). In addition to the below requirements for preparing a PER, a Facility Plan (FP) should include all of the requirements listed in Exhibit B as well as any other information requested by MPCA.

  - Modesty: Rural Utilities Service (RUS) projects must be modest in design, size and cost, simple to operate, and constructed and operated in an environmentally responsible manner.

  - Minnesota RUS policies:

    - Contingency funds: The items that are needed for the project must be included in the beginning scope of the project. Contingency Funding is for unforeseen conditions or bids that exceed the engineer’s cost estimates. The Contingency Fund is not intended to be a slush fund or a “want list fund”. The Contingency Fund will be administered in accordance with RUS Instruction 1780.45(f).

    - Growth: Applicants in growth areas are to design systems that will accommodate growth as it is realized. However, Rural Development will allow a system to be 20% larger than currently needed for the residential and business users in those areas that have a history of growth when determining grant and loan amounts. If the Rural Development engineer determines that the system is being proposed for more than 20% growth, the application will be returned to the Area Office for a more in depth determination of the availability of other credit. When such condition exists, Rural Development will only consider grant eligibility based on 120% of the flows that should actually be generated by residential and business users. Any additional capacity will be considered for loan only. When there are phased systems or growth included, the areas of growth must be determined and included in both the determination of median household income and in the environmental review process.

    - Operation and maintenance (O&M) costs: O&M costs vary by type of system; therefore it is difficult to provide exact cost guidelines. However, we suggest that if the operating and maintenance costs of a sewer system are substantially higher or lower than $17.50 per EDU that additional information be obtained to justify the proposed costs. Likewise, if a water system has operating and maintenance costs substantially higher or lower than $15/EDU that additional information be obtained to justify the proposed costs.

- Water

  - All water projects must follow Minnesota Department of Health requirements and guidelines.

  - Fire protection: A primary goal of the RUS Water and Waste program is to develop and maintain reliable, safe drinking water systems.  It is the policy of RUS to include reasonable fire protection where economically feasible.  However, providing full fire protection in a system financed by Water and Waste would quickly deplete program funds.  Therefore, determining reasonable and practicable fire protection is a challenge for both rural communities and RUS and will require creative solutions.

- Wastewater

  - Collection and treatment alternatives shall be considered in the following order:

    - New Individual Sewage Treatment Systems (ISTS) with centralized management to provide assured monitoring, operation and maintenance.

    - Decentralized wastewater systems that combine localized failed ISTS into a multiple-household, soil-based system with centralized management.

    - Connect the failed unsewered area to an existing wastewater treatment facility with available capacity.

    - Connect the failed unsewered area to an existing wastewater treatment facility, which requires additional capacity through an expansion.

    - Development of a new wastewater collection and treatment facility.

  - Infiltration and inflow (I&I): Our policy is that I&I will be corrected to the extent that it is economically practical. There will be times when regulatory agencies, Rural Development and other funding agencies determine that it is economically more practical to provide larger treatment capacity rather than correct all I & I. When such condition exists, Rural Development will only consider grant eligibility for treatment based on 120% of the flows that should actually be generated by residential and business users including normal I & I. Any additional capacity needed because of I & I will be considered for loan only.

  - See Exhibit A Minnesota Pollution Control Agency Design Flow and Loading Determination Guidelines.

- Solid Waste

  - No additional Minnesota RD requirements or clarifications.

- Storm Water

  - No additional Minnesota RD requirements or clarifications.

EXHIBIT A

MINNESOTA POLLUTION CONTROL AGENCY

DESIGN FLOW AND LOADING DETERMINATION GUIDELINES

These guidelines are recommended procedures for estimating design flow and loading conditions. It is expected that the engineer will use good engineering judgment in selecting the design conditions and will give due consideration to unique aspects of the contributors, to the type of treatment, to the return wastewater flows and return sludge, etc.

INTRODUCTION

The flow monitoring period for any particular project must record flow data during critical peak wet weather flow events which have occurred during a sustained wet weather flow period. Data collected during this flow period are used to estimate the four (4) flow conditions that are critical to the design and operation of wastewater treatment plants (see Table 1): average dry weather (ADW), average wet weather (AWW), peak hourly wet weather (PHWW), and peak instantaneous wet weather (PIWW).

The average dry weather flow is the daily average flow when the ground water is at or near normal and a runoff condition is not occurring. Average wet weather flow is the daily average flow for the wettest thirty (30) consecutive days for mechanical plants or for the wettest 180 consecutive days for controlled discharge pond systems. The 180 consecutive days for pond systems should be based on either the storage period from approximately November 15 through May 15 or the storage period from approximately May 15 through November 15. The treatment plant must meet the calendar month average NPDES permit requirements at average dry weather and average wet weather flow conditions.

The peak hourly wet weather flow is the peak flow during the peak hour of the day at a time when the ground water is high and a five-year one-hour storm event is occurring. To determine this five-year one-hour storm event for the specific project, please refer to the attached Map Number 1. The peak instantaneous wet weather flow is the peak instantaneous flow during the day at a time when the ground water is high and a twenty-five year one-hour storm event is occurring. To determine the appropriate twenty-five year one-hour storm event, please refer to Map Number 2. No separate permit limitations are associated with either peak hourly wet weather flow or peak instantaneous wet weather flow.

Clarifiers must be designed to meet the appropriate surface settling rate and weir overflow rate at peak hourly wet weather flow. The disinfection unit must be designed to provide adequate detention at peak hourly wet weather flow. At the treatment facility, all preliminary units, screens, filters, piping and pumping must be designed for peak instantaneous wet weather flow. The collection system must be capable of transporting all flows to the treatment facility. All other units should be designed to allow this flow to pass through the units.

Where the Minnesota Pollution Control Agency (MPCA) determines that the above design flow considerations will not provide adequate protection to the receiving waters, facility capacity in excess of peak instantaneous wet weather flow may be required.

In cases where flow studies are over five years old, or where the consultant designing the treatment or transmission facility did not perform the flow study, a verification of the acceptability of the flow data should be performed.

TABLE 1

DESIGN FLOW CONDITION SUMMARY

| Item | Description | Purpose |
| --- | --- | --- |
| ADW | Average dry weather flow assumes normal ground water with no runoff. | Facility designed to meet the calendar month average permit limitations and to determine if flow equalization should be evaluated. |
| AWW | Average wet weather flow (wettest 30-day average for mechanical plant and wettest 180-day average of controlled discharge pond systems). Assume high ground water with inflow | Facility designed to meet the calendar month average permit limitations and to determine if flow equalization should be evaluated. |
| PHWW | Peak hourly wet weather flow. Assumes high ground water with inflow due to a five-year one-hour storm event. | Clarifier and disinfection sizing and to determine if flow equalization should be evaluated. |
| PIWW | Peak instantaneous wet weather flow. Assumes high ground water with inflow due to a twenty-five year one-hour storm event. | Hydraulic design sizing for preliminary units, screens, filters, piping and pumping at the treatment facility. |

BYPASS/OVERFLOW

All bypass/overflow structures shall be manually controlled and kept locked at all times. All bypassing is prohibited unless:

1. Bypass was unavoidable to prevent loss of life, personal injury or severe property damage;

2. There was no feasible alternative to the bypass;

3. The Permittee gives previous notice of an anticipated bypass.

Any bypassing must be reported to the MPCA in a report consistent with permit requirements. This report shall include, but not be limited to, the bypass duration, estimated volume and associated meteorological conditions. Periodic bypassing at any discharge point under flow

conditions less than PIWW may precipitate the need for a corrective action plan to upgrade the system.

The following design flow consideration shall be incorporated into new or existing treatment facilities in order to reduce frequency as well as degree of adverse environmental impact associated with bypassing:

- The treatment facility shall provide pretreatment for the removal of coarse floatable and/or settle-able solids during flows in excess of peak instantaneous wet weather. In additions, the pretreated waste shall then be blended with the fully treated effluent, where practical, and discharge samples collected for the purpose of determining NPDES/SDS permit compliance of the blended effluent.

- Flow equalization for mechanical plants may be necessary in order to effectively operate treatment plants. Please refer to the section entitled Flow Equalization.

TREATMENT SYSTEMS WITH NEW SANITARY SEWER COLLECTION SYSTEMS

If a new collection system is being constructed and no inflow sources will be connected, the average wet weather flow for this treatment plant shall be based on a minimum of 100 gallon per capita day (GPCD) for the residential flow plus 20 GPCD for out of town students plus the average commercial and industrial flow. The average wet weather flow for seasonal residents shall be based on a minimum of 20 GPCD for day visitors and 80 GPCD for seasonal visitors.

For mechanical plants, if the industrial flow varies during the day or week, the design flow should be based on the average flow on the peak day during the period when the industry or industries are operating. This condition is called “rated flow.” For example, if the industry discharges 10,000 gallons over eight of the twenty-four hours, the rated flow is 30,000 gallons per day. For controlled discharge pond systems, if the industrial flow varies during the day or week, the average design flow may be based on a weekly average.

The peak hourly wet weather design flow and peak instantaneous wet weather design flow are the peak hourly industrial flow plus 2.5 times the sum of the average wet weather design flow for residential (full-time and seasonal), commercial and out of town students. Individual circumstances may dictate higher values than the above minimum requirements.

The MPCA may approve of an alternate flow design with appropriate justification.

For determining the design of the collection system (including design flow), refer to Chapter 20 Design of Sewers from the “Recommended Standards for Sewage Works” (Ten State Standards).

MECHANICAL TREATMENT PLANTS WITH EXISTING SANITARY SEWER SYSTEMS

For mechanical plant, if a separate sanitary sewer system exists, Table 2 should be used to determine the peak hourly wet weather flow, the peak instantaneous wet weather flow, the average dry weather flow and the average wet weather flow.

Part A of Table 2 along with Figure 1 are used to determine the peak hourly wet weather flow. The measured flow should be plotted for a twenty-four hour period when ground water is at or near normal and a runoff condition is not occurring (Curve X on figure 1). The ground water elevation in relation to the sewer elevation should be noted. The present peak hourly dry weather flow[(1) on figure 1 and Table 2] is peak hourly flow during the twenty-four hour period when he ground water is at or near normal and a runoff condition is not occurring. The measured flow should be plotted for a twenty-four hour period when ground water is high and a runoff condition is not occurring (Curve Y). The ground water elevation in relation to the sewer elevation should be noted. Number (2) on Figure 1 and Table 2 is the peak hourly flow during a high ground water period for that specific area and system when a runoff condition is not occurring. This flow (2) minus the present peak hourly dry weather flow (1) is the peak hourly infiltration.

The measured flow should be plotted for a twenty-four hour period when the ground water is high and a runoff condition is occurring (Curve Z). This should include overflow, bypasses and emergency pumping. The amount of rainfall and its duration should be plotted on the same graph. The peak inflow is represented by the greatest distance between Curve Y and Curve Z. The present hourly flow at the point of greatest distance between Curve Y and Z [(5) on Figure 1 and Table 2] minus the present hourly flow during high ground water at the same time of day [(6) on Figure 1 and Table 2] is the peak hourly inflow.

It may be necessary to adjust the measured flow based on a relationship between the data attained during a major storm event and the five-year one-hour designed storm event. Items (10) and (13) are determined through a cost effectiveness evaluation. The GPCD contribution for population increase in Item 15 (also in 25, 33 and 41) should be 100 GPCD.

Part B of the Table determines the peak instantaneous wet weather flow. The present peak hourly inflow adjusted for a five-year one-hour rainfall event (see part A line 8) is subtracted from the peak hourly wet weather flow (see Part A line 19). To this number, add the present peak hourly inflow adjusted for a twenty-five year one-hour storm event. The resulting number is the peak instantaneous wet weather flow.

Part C of the Table determines the average dry weather flow. The present dry weather flow (24) is the average flow received over a twenty-four hour period when the ground water is at or near normal and a runoff condition is not occurring. If the industrial flow varies during the day or week, the present average dry weather flow should be based on the average flow of the peak day during the period when the industry or industries are operating (rated flow). This also applies to the average flow from industrial increases.

Part D of the Table determines the thirty day average wet weather design flow. The average infiltration and inflow after rehabilitation (where rehabilitation is cost effective) is the wettest thirty-day average. The amount of infiltration after rehabilitation averaged over the thirty wettest days should be the same or nearly the same as the peak infiltration after rehabilitation. This is due to the fact that ground water could stay high for a fairly extended period of time. The amount of inflow after rehabilitation averaged over the thirty wettest days depends on the type of sources, their location, the amount of rainfall that affects the source, etc.

Part E of the Table correlates all related information which can impact the degree of accuracy of the determination of design flows. It is recommended that a minimum of six months of accurate data be recorded. Minn. R. 7077.0150, subp. 2B requires a minimum of 30 consecutive days of actual flow monitoring. Data associated with the critical peak wet weather flow events for a sustained wet weather period are essential for accurate estimation of design flows. Critical peak wet weather flow events typically occur in the spring (March-June) and must be include the condition of high ground water with inflow.

CONTROLLED DISCHARGE POND SYSTEMS WITH EXISTING SANITARY SEWER SYSTEMS

The peak hourly wet weather and the peak instantaneous wet weather design flows to a pond system with an existing sanitary sewer system are arrived at in the same manner as in Parts A and B of the previous section. If the present industrial flow varies during the day or week, the present average dry weather flow (24) and (30) may be based on a weekly average. When computing the average wet weather flow, the average infiltration after rehabilitation (31), and the average inflow after rehabilitation (32) are averages over the wettest 180 consecutive days.

FLOW EQUALIZATION

This section applies to all treatment facilities except pond systems. During a period of high ground water for that area and system, if the ratio of peak hourly wet weather design flow to average wet weather design flow [which is (19)/(37)] is three or more, flow equalization shall be evaluated. When the ratio is three or more and flow equalization is not employed, an explanation must be included outlining how the plant will handle this transition from average wet weather design flow to peak hourly wet weather design flow.

During a normal ground water period, if the ratio of the peak hourly design flow during the five-year one-hour storm event (1 + 14 + 15 + 17 + 18) to the average dry weather design flow (29) is three or more, flow equalization shall be evaluated. When the ratio is three or more and flow equalization is not employed, an explanation must be included outlining how the plant will handle this flow transition.

WASTEWATER TREATMENT PLANT DESIGN LOADING

Table 3 should be used to determine the design loadings for the upgraded wastewater treatment plant.

TABLE 2

DETERMINATION OF DESIGN FLOWS

(A) For determination of peak hourly wet weather design flow (PHWW):					  gpd

(1) Present peak hourly dry weather flow								_______

(2) Present peak hourly flow during high ground water  period (no runoff)  					_______

(3) Present peak hourly dry weather flow [Same as (1)]					          	            -	_______

(4) Present peak hourly infiltration					 		         	           =  _______

(5) Present hourly flow during high ground water period and runoff at a point of

greatest distance between Curves Y & Z								_______

(6) Present hourly flow during high ground water (no runoff) at

same time of day as (5) measurement							           -  	_______

(7) Present peak hourly inflow								          =  	_______

(8) Present peak hourly inflow adjusted for a 5-year 1-hour rainfall event				              	_______

(9) Present peak hourly infiltration [Same as (4)]							_______

(10) Peak hourly infiltration cost effective to eliminate					          	            -  _______

(11) Peak hourly infiltration after rehab (where rehab is cost effective)			          	           =  _______

(12) Present peak hourly adjusted inflow [Same as (8)]							_______

(13) Peak hourly inflow cost effective to eliminate					               	           -   _______

(14) Peak hourly inflow after rehab (where rehab is cost effective)				          	           =  _______

(15) Population increase ____@____ gpcd times 2.5 (peaking factor)					_______

(16) Peak hourly flow  from planned industrial increase							_______

(17) Estimated peak hourly flow from future unidentified industries					_______

(18) Peak hourly flow from other future increases							_______

(19) Peak hourly wet weather design flow (1 + 11 + 14 + 15 + 16 + 17 + 18)				_______

(B) For determination of peak instantaneous wet weather design flow (PIWW):

(20) Peak hourly wet weather design flow  [same as (19)]						_______

(21) Present peak hourly inflow adjusted for a 5-year 1-hour rainfall event [same as (8)]	           	            -  _______

(22) Present peak inflow adjusted for a 25-year 1-hour rainfall event				           +  _______

(23) Peak instantaneous wet weather design flow						           =  _______

(C) For determination of average dry weather design flow (ADW):

(24) Present average dry weather flow								_______

(25) Population increase ____@____gpcd						        	           +  _______

(26) Average flow from planned industrial increase					          	           +  _______

(27) Estimated average flow from other future unidentified industries			          	           +  _______

(28) Average flow  from other future increases						           +  _______

(29) Average dry weather design flow (24 + 25 + 26 + 27 + 28)				         	           =  _______

(D) For determination of average wet weather design flow (30-day average for

mechanical plant and 180-day average for controlled discharge ponds): (AWW)

(30) Present average dry weather flow								_______

(31) Average infiltration after rehab (where rehab cost effective)				          	           +  _______

(32) Average inflow after rehab (where rehab cost effective)				          	           +  _______

(33) Population increase ____@____gpcd						         	           +  _______

(34) Average flow from planned industrial increase					          	           +  _______

(35) Estimated average flow from other future unidentified industries			          	           +  _______

(36) Average flow from other future increases						          	           +  _______

(37) Average wet weather design flow (30 + 31 + 32 + 33 + 34 + 35 + 36)			          	           =  _______

(E) Critical data (including a graphical display similar to Figure 1), methodology, and a discussion on the following

items shall be included with the above calculations:

(38) Dates during which actual flow data was recorded and its probable degree of accuracy.

(39) Ground water elevation data relative to the collection system, during the time period when flow data was recorded.

(40) Rainfall data during the time period when flow data was recorded and how the amount of rainfall compares to normal

seasons.

(41) Probable degree of accuracy of flow reduction due to proposed or completed I/I correction or elimination of bypasses.

TABLE 3

DETERMINATION OF DESIGN LOADINGS

* It may be necessary to also test for TKN for certain industrial contributors

EXHIBIT B

# FACILITY PLAN REQUIREMENTS

# GENERAL:

  - Before adopting, municipality must hold at least one public hearing to discuss the proposed project.

  - Must be prepared and signed by a professional engineer registered in the state of Minnesota.

  - Facility plans for individual sewage treatment systems (ISTS) designed to treat 5000 gallons or less per day must be prepared and signed by either a professional engineer or an evaluator/designer.

- CONTENT:

  - Description and evaluation of existing system which must consider:

    - Age;

    - Condition;

    - Design Capacity Treatment capacity;

    - Treatment capabilities of each treatment unit;

    - The system's ability to meet current of proposed permit requirements; and

    - For existing ISTSs, a survey must also be prepared which identifies whether or not each ISTS project in the project area conforms to Minn. Rules ch.7080.

  - Data describing existing residential and non-residential wastewater flows and loadings reported on a form provided by the MPCA.

  - Data describing future residential and nonresidential wastewater flows and loadings with the next 20 year period, using Exhibit A and associated forms, based on;

    - Projected residential growth;

    - Projected nonresidential growth; and,

    - Signed letters of intent from significant industrial users.

  - A discussion of treatment alternative's that were considered during the facility selection process and are capable of meeting the applicable effluent, water quality and public health requirements for 20 years. The discussion must include:

    - A cost-effective comparison of the alternatives that were considered;

    - A site assessment of the existing soil and ground water conditions conducted and signed by a professional engineer;

    - For ISTSs designed to treat less than 5,000 gallons per day, a site assessment must be done by either a professional engineer or a certified evaluator/designer;

    - An evaluation of the impact of the alternatives on all existing wastewater treatment systems, including sewers and lift stations; and,

    - A comparison of the potential environmental impacts.

  - A description of the selected treatment alternatives and the complete wastewater treatment system of which it is a part, including:

    - The specific design parameters of all individual treatment units and the complete treatment system;

    - Estimated construction, annual operation and maintenance, and equipment replacement costs;

    - Estimated annual sewer service charges;

    - A determination of whether pretreatment of any industrial wastes is needed in order to avoid disruption of the proper operation of the proposed system; and,

    - An evaluation of how and where sludge or septage resulting from the treatment process will be disposed.

  - An analysis of the 25- and 100- year flood elevations in relation to the proposed project site or sites, showing that the project will be operable during a 25-year flood and protected during a 100-year flood.

  - An analysis of how interim treatment will be accomplished during construction to meet permit requirements.