Arc Flash Boundary and PPE Table

| Category | Incident Energy (cal/cm2) | Flash Boundary (feet) | Required PPE* | PPE Code** |
| --- | --- | --- | --- | --- |
| -1 and 0 | 0 – 2 | 4 | FR Work Clothing, Class 0 Gloves w/leather protectors, and safety glasses | Green |
| 1 and 2 | 2 – 8 | 6 | FR Work Clothing, Class 0 gloves w/leather protectors, safety glasses, hard hat w/FR-rated face shield, hearing protection, and leather boots or shoes | Blue |
| 3 | 8 – 25 | Contact FMOC Project Lead | Intermediate Switching Clothing, Class 0 gloves w/leather protectors, hearing protection, and leather boots or shoes | Yellow |
| 4 | 25 – 40 |  | Electrical Switching Clothing, Class 0 gloves w/leather protectors, hearing protection, and leather boots or shoes | Orange |
| N/A | > 40 |  | Identified by Electrical System Engineer | Red |

Note:

* The PPE identified in this table represents what FMOC maintenance personnel currently wear and is only included as an example and not a requirement.

** The PPE Color Code represents the Arc Flash labeling colors.  See examples of labels below.

Level I (HC-0) Label				          Level II (HC-1 and HC-2) Label