July 22, 1994

Contract #TW0592

SPECIAL STANDARD SPECIFICATION

SECTION 15250-S

INSULATION - MECHANICAL SYSTEMS

Page

PART 1 - GENERAL

1.01	Description of Work	2

1.02	References	2

1.03	Submittals	3

1.04	Quality Assurance	4

1.05	Delivery, Storage and Handling	4

1.06	Warranty	4

PART 2 - PRODUCTS

2.01	Insulation for Piping Systems	5

2.02	Insulation for Ductwork Systems	5

2.03	Insulation for Equipment	6

2.04	Insulation Requirements	76

2.05	Manufactured Units	7

2.06	Accessories	87

2.07	Sealants	8

PART 3 - EXECUTION

3.01	Examination	9

3.02	Preparation	9

3.03	Installation - Piping Systems	9

3.04	Installation - Ductwork	1412

3.05	Installation - Equipment Systems	1615

3.06	Installation - Repair and Replacement	1816

3.07	Field Quality Control	1817

3.08	Cleaning	1817

3.09	Commissioning	18

SPECIAL STANDARD SPECIFICATION

SECTION 15250-S

INSULATION - MECHANICAL SYSTEMS

PART 1 - GENERAL

1.01	Description of Work

Contractor shall furnish labor, equipment, materials and accessories to perform operations required for the installation of mechanical insulation in accordance with this specification and other contract drawings and documents. Mechanical insulation includes the broad categories of piping, equipment and ductwork.  Piping systems include, but are not limited to, domestic cold and hot water; non-potable hot and cold water; DI water systems; recirculating hot water; heating hot water; interior low and high pressure steam; hot and cold condensate; chilled water; process cooling water systems; roof drain; dual temperature water; underground hot and chilled water lines and refrigerant piping.  Equipment includes, but is not limited to, converters, hot water storage tanks; pumps, boilers, and flues. Ductwork includes, but is not limited to, plenums; air conditioning, heating, ventilating and exhaust ductwork.

1.02	References

The current editions of the following references are to be considered a part of this specification.  They are listed in the order of governance.

A.	Sandia National Laboratories (SNL) Standard Specifications

01065	Environment, Safety & Health Regulations for Construction (Special)

01300	Submittals

B.	Department of Justice

28 CFR Part 36	Non-discrimination on the Basis of Disability by Public Accommodations and in Commercial Facilities

C.	National Fire Protection Association (NFPA)

90A	Standard for Installation of Air Conditioning and Ventilation Systems

D.	Underwriter's Laboratories (UL)

Fire Resistance Directory

181	Factory-Made Air Ducts and Air Connectors

723	Test for Surface Burning Characteristics of Building Materials

E.	American Society for Testing and Materials (ASTM) Standard Specifications

C167	Thickness and Density of Blanket- or Batt Type Insulating Materials

C208	Insulating Board, Structural and Decorative

C533	Calcium Silicate Block and Pipe Thermal Insulation

C534	Preformed Flexible Elastomeric Cellular Thermal Insulation in Sheet and Tubular Form

C547	Mineral Fiber Preformed Pipe Insulation

C552	Cellular Glass Block and Pipe Thermal Insulation

C553	Mineral Fiber Blanket and Felt Thermal Insulation (Industrial Type)

C585	Practice for Inner and Outer Diameters of Rigid Thermal Insulation for Nominal Sizes of Pipe and Tubing

C612	Mineral Fiber Block and Board Insulation

C665	Mineral Fiber Blanket Thermal Insulation for Light Frame Construction and Manufactured Housing

C916	Adhesives for Duct Thermal Insulation

C921	Practice for Determining Properties of Jacketing Materials for Thermal Insulation

C1146	Guide for Prefabricated Panel Insulation Systems for Ducts and Equipment Operating at Temperatures Above Ambient Air

D 903	Test for Peel or Stripping Strength of Adhesive Bonds

D3654	Test Method for Holding Power of Pressure Sensitive Tapes

E84	Test Method for Surface Burning Characteristics of Building Materials

1.03	Submittals

Proposed substitutions to the manufacturers, products or model numbers cited in this specification shall be included in the submittal package furnished to the Sandia Delegated Representative (SDR) for approval prior to commencement of work.  Submittals shall be in accordance with Sandia National Laboratory (SNL) Standard Specification 01300.

A.	Product Data:	Submit manufacturer's catalog data and published certification data.

B.	Shop Drawings:	Submit for factory fabricated insulation units.

C.	Material Safety Data Sheets (MSDS):	Submit MSDSs on insulation, sealants, cements, adhesives and mastics.

D.	Quality Control:	Submit manufacturer's certification that insulation meets the appropriate American Society for Testing and Materials or UL Specification.

1.04	Quality Assurance

A.	Asbestos Free:	Insulating and sealing materials must be certified to be free of asbestos.

B.	Manufacturer's Qualifications:	Manufacturing firms shall be regularly engaged in the manufacture of mechanical insulation products, of the types and sizes required, whose products have been in satisfactory use in similar service for not less than 3 years.

C.	Installer's Qualifications:	Firms with at least 3 years successful installation experience on projects with similar mechanical insulation.

D.	Flame/Smoke Ratings:	Provide composite mechanical insulation (insulation, jackets, coverings, sealers, mastics and adhesives) with flame spread index of 25 or less and smoke developed rating of 50 or less, as tested by ASTM E84 for interior applications.  For exterior applications, a composite flame spread index of 75 or less with a smoke developed rating of 150 is allowable.

E.	Insulation and insulating materials shall be listed in the UL Fire Resistance Directory, UL 181 or UL 723.

1.05	Delivery, Storage and Handling

A.	Insulation and insulating materials (coatings, adhesives, coverings and cements) shall be delivered to the construction site in containers suitable for protection from the elements.

B.	Containers shall be labeled with the manufacturer's identification and with the fire hazard ratings.

C.	Wet or otherwise visibly damaged insulation shall not be used.

D.	Insulation shall be stored in original containers to preserve shop cleanliness levels prior to insulation.

1.06	Warranty

Insulation and components furnished under this contract shall be guaranteed against defective design, materials, and workmanship for the full warranty time, which is standard with the manufacturer or supplier, but in no case less than one year from the date of system acceptance.

PART 2 - PRODUCTS

2.01	Insulation for Piping Systems

A.	Fiberglass:	Shall conform to requirements for composition, dimensions, sizes and physical properties as set forth in ASTM C665 or ASTM C547, Classes 1, 2 or 3.  Material shall be manufactured from glass, slag, rock or other mineral substances processed from a molten state into a fibrous form.  Insulation shall be faced with laminated foil, reinforcing scrim and flame resistant Kraft paper.  Manufactured by  Accessible Products, Owens-Corning, or Manville.

B.	Calcium Silicate:	Shall conform to the requirements for physical dimensions, properties, composition and sizing as stated in ASTM C533, Type I, pipe.  Material shall be composed of hydrous calcium silicate with a fibrous reinforcement.  Insulation shall be supplied as either hollow cylinders, split in half or as curved segments.  Long edges of grooved block shall be beveled.  Thicknesses greater than 3 in. (76 mm) may be furnished in two or more layers.  Manufactured by Pipe Shields or Owens-Corning.

C.	Cellular glass:	Shall conform to the composition, dimensions, sizes, and physical properties as stated in ASTM C552, Type II (piping and tubing) and either Class 1 (unjacketed) or Class 2 (jacketed.)  Material shall consist of a glass composition that has been cellulated or foamed under molten conditions to form an incombustible, rigid, hermetically sealed cell material.  The pipe insulation shall be fabricated from standard blocks with heat sealable multi-ply laminate jacketing of glass, asphalt, aluminum and polyester.  Manufactured by Pittsburgh Corning Corporation, types StrataFab or Foamglas, plain or supplied with Pittwrap jacketing factory applied.

D.	Flexible Cellular:	Shall conform to requirements specified in ASTM C534, Type I, tubular, for physical dimensions, shape, size and materials.  Material shall consist of flexible cellular elastomers, such as polyurethane foam or other polymeric or copolymer material.  Insulation shall be supplied with natural skins on inner and outer surfaces.  Manufactured by Owens-Corning or Pittsburgh Corning.

2.02	Insulation for Ductwork Systems

A.	Rigid Fiberglass Board:	Shall conform to requirements for physical properties, dimensions and composition as set forth for rigid and semi-rigid board in ASTM C612, class 1.  Insulation shall be faced with laminated foil, reinforcing scrim and flame resistant Kraft paper.  Manufactured by Manville or Owens-Corning.

B.	Flexible Fiberglass Blanket:	Shall conform to requirements for composition, physical properties, dimensions and sizes as stated in ASTM C553, Type I, class B-4, resilient and flexible fiberglass.  Insulation fiber shall be derived from rock, slag, glass or other mineral substances and processed from a molten state into a fibrous form.  Insulation shall be faced with laminated foil, reinforcing scrim and flame-resistant Kraft paper.  Manufactured by Manville or Owens-Corning.

C.	Cellular Glass:	Shall conform to the composition, dimensions, sizes, and physical properties as stated in ASTM C552, Type IV (board), Class 1 (unjacketed.)   Material shall consist of a glass composition that been cellulated or foamed under molten conditions to form an incombustible, rigid, hermetically sealed cell material.  Manufactured by Pittsburgh Corning.

D.	Flexible Cellular:	Shall conform to requirements specified in ASTM C534, Type II, sheet, for physical dimensions, shape, size and materials.  Material shall consist of flexible cellular elastomers.  Insulation shall be supplied with natural skins on both surfaces  Use for temperatures between -40 (F (-40 (C) and 200 (F (93 (C).  Manufactured by Owens Corning or Manville.

C.	Fire Wrap:  Shall be 1/2-inch wrapping material such as 3M’s fireproofing wrap or Nelson Firestop wrap (see FM approval guide).

2.03	Insulation for Equipment

A.	Rigid Fiberglass:	Shall conform to requirements for dimensions, composition and physical properties as set forth in ASTM C612.  Allowable Classes 1 through 5.  Insulation shall be faced with laminated foil, reinforcing scrim and flame resistant Kraft paper.  Manufactured by Manville or Owens Corning.

B.	Flexible Fiberglass Blanket:	Shall conform to requirements for composition, physical properties, dimensions and sizes as stated in ASTM C553, Type I, class B-4, resilient and flexible fiberglass.  Insulation fiber shall be derived from rock, slag, glass or other mineral substances and processed from a molten state into a fibrous form.  Insulation shall be face with laminated foil, reinforcing scrim and flame-resistant Kraft paper.  Manufactured by Manville or Owens Corning.

C.	Calcium Silicate:	Shall conform to the requirements for physical dimensions, properties, composition and sizing as stated in ASTM C533, Type I, block, for temperatures up to 1200 °F (649 (C).  Use Type II for temperatures up to 1600ºF (871 ºC.)  Material shall be composed of hydrous calcium silicate with a fibrous reinforcement.  Insulation shall be supplied as either hollow cylinders, split in half or as curved segments.  Long edges of grooved block shall be beveled.  Thicknesses greater than 3 in. (76 mm) may be furnished in two or more layers.  Manufactured by Pipe Shields or Owens Corning.

D.	Cellular glass:	Shall conform to the composition, dimensions, sizes, and physical properties as stated in ASTM C552, Type I (flat block), Class 1 (unjacketed.)   Material shall consist of a glass composition that been cellulated or foamed under molten conditions to form an incombustible, rigid, hermetically sealed cell material.  Use for cold applications between -450 (F (-267 (C) and 800 (F (427 (C.)  Acceptable Manufacturer:  Pittsburgh Corning.

E.	Flexible Cellular:	Shall conform to requirements specified in ASTM C534, Type II, sheet, for physical dimensions, shape, size and material.  Material shall consist of flexible cellular elastomers.  Insulation shall be supplied with natural skins on both surfaces.  Use for condensation control at temperatures up to 180 (F (82 (C.)  Manufactured by Owens Corning.

2.04	Insulation Requirements

A.	The following are recommended minimum thermal conductivities (k) and density requirements for the generic insulation types.  The thermal conductivities are given at the indicated mean temperatures.

Type		Mean Temperature		"k" 			Density

(F ((C) 		Btu-in./h-ft²-F (W/m-K)	lb./ft³ (kg/m³)

Fiberglass:

ASTM C547

Class 1	75  (24)	0.26  (0.037)	10  (160)

Class 2 	75  (24)	0.31  (0.045)	12  (192)

Class 3 	75  (24)	0.36  (0.052)	18  (288)

ASTM C553

Class B-4	75  (24)	0.31  (0.045)	1.5  (24)

ASTM C612

Class 1	75  (24)	0.26  (0.037)	10  (160)

Class 2	75  (24)	0.26  (0.037)	12  (192)

Class 3	100  (38)	0.30  (0.043)	12  (192)

Class 4	300  (149)	0.42  (0.061)	12  (192)

Class 5	300  (149)	0.53  (0.076)	20  (320)

Calcium Silicate:

Type I 	200  (93)	0.45  (0.065)	15  (240)

Type II 	400  (204 )	0.66  (0.095)	15  (240)

Cellular Glass:

Type I & IV	75  (24)	0.38  (0.055)	9.5  (152)

Flexible Cellular:

Type I & II	75  (24 )	0.30  (0.043)	8.5  (136)

B.	Insulation shall meet thickness and density requirements as set forth in 10 CFR 435.  ASTM C585, C167 or C208, as applicable.

2.05	Manufactured Units

A.	Lavatory safety kit:	Shall comply with the Americans with Disabilities Act (ADA).  Safety kit shall consist of durable, chemical and UV resistant, 1/8" (3.2 mm) thick vinyl plastisol covers with nylon fasteners for hot and cold water valves, waste line, tail piece and P-trap.  Manufactured by Brocar Products, model Wrap Trap.

B.	Valve, flange and fitting coverings:	Shall be supplied by the insulation manufacturer, if available.  Covers shall be constructed from field fabricated aluminum or constructed of one-piece pre-molded PVC.

C.	Jacketed Fiberglass Insulation:	Shall be constructed of fiberglass with an attached self-sealing PVC or polyester impregnated PVC jacket.  Manufactured by Accessible Products; type Thermazip, for pipe, tank and vessel insulation.

2.06	Accessories

A.	Jackets:	Shall conform to ASTM C921.  Acceptable manufacturers:  Owens Corning, Accessible Products or Manville.

1.	Classification:

a.	Type I:	Jacket with vapor barrier shall be used over pipes, ducts or equipment operating at temperatures below ambient, or wherever vapor barriers are required.

b.	Type II:	Water vapor permeable jacket shall be used over pipes, ducts or equipment operating at temperatures above ambient., for use with temperatures above ambient, or wherever vapor barrier is not required.

2.	Materials

a.	Aluminum jacketing shall be of the banded, embossed type, coated on the interior to resist corrosion.  Jacket shall be a minimum of 0.016 inches thick (  0.400 mm.)

b.	Plastic jacketing shall be manufactured from rigid PVC, or PVF and be of the banded type.  Jacket shall be a minimum of 0.015 inches thick  ( 0.40 mm.)

bc.	Cloth jacketing shall be manufactured from white or gray vinyl acrylic breather mastic reinforced with a minimum 7.8 ounce per yard (0.26 kg/m²) glass or nylon plastic cloth.

B.	Shields, saddles and sleeves:	Shall be made from PVC or 16 ga. (1.25 mm) galvanized steel.  Size shall be a minimum of 3 times the insulation diameter in length one third the insulation circumference in width.

C.	Staples, bands, wires, anchors, angles and similar fasteners shall be as recommended by the insulation manufacturer for the indicated applications.

D.	Mechanical fasteners:	Shall be of galvanized steel, suitable for adhesive, mechanical or welding attachment.  Provide fasteners that will not damage the insulation when applied as recommended by the manufacturer, that do not cause leakage within the duct and that will sustain a 50 pound (6.9 N) tensile dead load perpendicular to duct wall.

E.	Tapes:	Shall conform to ASTM D3654.

2.07	Sealants

A.	Sealants, mastics, adhesives, cements and protective finishes shall be provided as recommended by the manufacturer and shall conform to SNL Standard 07900 and the appropriate specification or test method as outlined in the UL Fire Resistance Directory, UL 181, UL 723 or ASTM E84.

B.	Fire Resistant Sealant:

C.	Adhesives shall conform to ASTM C916 for ductwork and D903 for other uses.  Acceptable manufacturers:  United McGill, Pittsburgh Corning or Foster.

PART 3 - EXECUTION

3.01	Examination

Examine areas and conditions under which mechanical insulation is to be installed.  Do not proceed until unsatisfactory conditions have been corrected in a manner acceptable to the SDR.

3.02	Preparation

A.	Protection:	Insulation and insulating materials shall be protected against damage from water, wind, dirt, chemical and mechanical mishaps.

B.	Precleaning:	Ductwork, equipment, piping, or other surfaces to be insulated shall be cleaned and dried prior to insulating.

C.	Testing:	Systems shall be tested before insulation is applied.  If this is not feasible, then joints shall be left exposed, until tests have been performed.

D.	Installation:	Contractor shall ensure that installation is in compliance with the requirements for personnel protection set forth in SNL Special Specification 01065: Environment, Safety and Health Regulations for Construction.

3.03	Installation - Piping Systems

A.	General:	Install insulation products in accordance with manufacturer's written instructions and contract documents.  Insulation shall be installed neatly and professionally.  Insulation shall be neatly terminated at fire walls and fire dampers, unless otherwise permitted by NFPA 90A and the SDR.  Seal penetrations through floors, walls and ceilings with fire resistant sealant.

B.	Piping application systems shall include the following, unless otherwise noted on the contract documents:

1.	Domestic and Service Cold Water Piping:	Shall include chilled water piping; potable and non-potable cold water piping concealed above ceilings or within 24 in. (600 mm) of exterior walls,  or concealed in partitions, basements, equipment rooms or penthouses; and interior above ground storm water piping.  Insulation shall be fiberglass and shall comply with the Table in Article 3.03, paragraph C.

2.	Domestic and Service Hot Water Piping:	Shall include potable recirculating hot water piping, potable hot water piping, and hot drain piping.  Insulation shall be fiberglass and shall comply with the Table in Article 3.03, paragraph C.

3.	Handicapped Fixtures:	Shall include exposed lavatory hot and cold piping supply and waste lines.

4.	Cooling and Heating System PipingHVAC Piping:	Shall include the following applications:

a.	Cooling Systems:  Chilled water supply and return piping, process cooling water system and DI water systems.  Insulation shall be fiberglass and shall comply with the Table in Article 3.03, paragraph C.

b.	Heating Systems:  Steam, steam condensate and heating water supply and return piping.  Insulation shall be fiberglass for heating water and calcium silicate for steam and steam condensate and shall comply with the Table in Article 3.03, paragraph C.

a.	Sub-zero piping:	Low temperature, below 0(F (-18(C), refrigerant piping.

b.	Sub-freezing piping:	Refrigerant suction lines located between evaporators and compressors and brine refrigerant piping.  Temperature range 0 to 39 (F (-18 to 4 (C.)

c.	Cold piping:	Air conditioning condensate drain, make-up water, and chilled water supply and return piping.  Temperature range 40 (F (4.4 (C) to 75ºF (24 ºC.)

d.	Dual temperature piping:	Hot and chilled water supply and return piping.  Temperature range 40 to 250(F (4.4 to 121 (C.)

e.	Hot low pressure piping:	Hot gas refrigerant, condenser supply and return, low pressure steam and condensate, heated fuel piping and hot water supply and return.  Pressures up to 15 psi (109 kPa) and temperatures up to 250(F (121(C.)

f.	Hot medium pressure piping:	Hot water supply and return, and medium pressure steam and condensate.  Pressures between 16 to 75 psi (110 and 517 kPa) and temperatures between 251 to 305 (F (122 to 152 (C.)

g.	Hot high pressure piping:	High temperature hot water supply and return and high pressure steam and condensate.  Pressures range from 76 to 200 psi (519 and 1379 kPa) and temperatures between 306 to 450 (F (153 to 232 (C.)

5.	Underground piping:	Piping for hot, cold and HVAC piping systems as defined above, only located underground.

C.	Minimum insulation thicknesses for piping systems are shown below:

Minimum Pipe Insulation (in)

Fluid Design

Operating			Insulation Condictivity					Nominal Pipe Diameter (In.)

Temperatuare

Range, (F		Conductivity		Mean Rating

Range			Temperature		Runouts1	1 and		1-1/4	2-1/2	5 &	8 &

Btu-in./F-h-ft2		          (F		up to 2		less   		to 2   	to 4   	6    	  up

Heating Systems (Steam, Steam Condensate, & Hot Water)

Above 350		0.32-0.34		         250		     1.5		  2.5		 2.5	3.0	3.5	3.5

251-350		0.29-0.31		         200		     1.5		  2.0		 2.5	2.5	3.5	3.5

201-250		0.27-0.30		         150		     1.0		  1.5		 1.5	2.0	2.0	3.5

141-200		0.25-0.29		         125		     0.5		  1.5		 1.5	1.5	1.5	1.5

105-140		0.24-0.28		         100		     0.5		  1.0		 1.0	1.0	1.5	1.5

Domestic and Service Hot and Cold Water Systems2

105 and greater		0.24-0.28		        100			     0.5		  1.0		 1.0	1.5	1.5	1.5

Cooling Systems (Chilled Water, Brine, & Refrigerant)3

40-55			0.23-0.27		         75			     0.5		  0.5		 0.75	1.0	1.0	1.0

Below 40		0.23-0.27		         75			     1.0		  1.0		 1.5	1.5	1.5	1.5

1.	Runouts to individual terminal units not exceeding 12 feet in length.

2.	Applies to recirculating sections of service or domestic hot water systems and first 8 feet from stoarge tank

for nonrecirculating systems.

3.	The required minimum thicknesses do not consider wster vapor transmission and condensation.  Add vapor

retarders as specified herein to limit water vapor transmission and condensation.

Application	Insulation Type	Pipe Size in. (mm)	Thickness in. (mm)

Cold Piping:	Fiberglass	all	1.0  (25)

Cellular Glass	all	1.5  (38)

Calcium Silicate	all	1.5  (38)

Flexible Cellular	all	0.5  (12)

Hot Piping:	Fiberglass	(6  ((150)	1.0  (25)

>6  (>150)	1.5  (38)

Cellular Glass	(6  ((150)	1.5  (38)

>6  (>150)	2.5  (62)

Calcium Silicate	(6  ((150)	1.5  (38)

>6  (>150)	2.5  (62)

Flexible Cellular	(2  (50)	0.5  (12)

HVAC Piping:

Sub-zero	Fiberglass	(2  ((50)	1.5  (38)

>2  (>50)	2.0  (50)

Cellular glass	(2  ((50)	2.5  (62)

>2  (>50)	3.0  (75)

Flexible Cellular	all	0.75  (18)

Sub-freezing	Fiberglass	(1  (25)	1.0  (25)

>1  (>25)	1.5  (38)

Cellular glass	(1  (25)	1.5  (38)

>1  (>25)	2.5  (62)

Flexible Cellular	all	0.5  (12)

Cold	Fiberglass	(4  ((100)	1.0  (25)

>4  (>100)	1.5  (38)

Cellular glass	(4  ((100)	1.5  (38

>4  (>100)	2.0  (50)

Flexible Cellular	all	0.5  (12)

Dual Temp.	Fiberglass	(4  ((100)	1.0  (25)

>4  (>100)	1.5  (38)

Cellular glass	(4  ((100)	1.5  (38)

>4  (>100)	2.0  (50)

Hot Low 	Fiberglass	(1  (25)	1.0  (25)

Pressure		(4  ((100)	1.5  (38)

>5  (>125)	3.0  (75)

Cellular Glass or	(1  (25)	1.5  (38)

Calcium Silicate	(4  ((100)	2.5  (50)

>5  (125)	3.0  (75)

Hot Medium	Fiberglass	(1.  (25)	1.5  (38)

Pressure		(2  ((50)	2.0  (50)

(4  ((100)	2.5  (62)

>5  (>125)	3.0  (75)

Cellular Glass or	(1  (25)	2.5  (62)

Calcium Silicate	(2  ((50)	3.0  (75)

(4  ((100)	4.0  (100)

>5  (125)	4.5  (112)

Hot High 	Fiberglass	(1.  (25)	1.5  (38)

Pressure		(2  ((50)	2.0  (50)

(4  ((100)	2.5  (62)

>5  (>125)	3.5  (87)

Cellular Glass or	(1  (25)	2.5  (62)

Calcium Silicate	(2  ((50)	3.0  (75)

(4  ((100)	4.0  (100)

>5  (125)	5.0  (125)

Note:	For exterior exposed piping, increase insulation thickness by 0.5 inch (12 mm.)

D.	Procedure for insulating aboveground piping:  Install insulation products in accordance with this specification and manufacturer's instructions, in a neat and professional manner.

1.	Insulate piping with full-length pieces of insulation on continuous runs of piping.

2.	Do not use scraps and cut pieces on continuous runs.

3.	Butt joints firmly together to ensure a tight fit.

4.	Butt pipe insulation firmly against pipe hanger insulation inserts.

5.	Cover valves, fittings and like items with insulation of equivalent thicknesses and composition as that applied to pipe runs.

6.	Apply vapor barrier tape or band over butt joints on hot piping.

7.	Protect vapor barrier jackets from punctures and other damage.

8.	Extend insulation without interruption through walls, floors and ceiling penetrations.

E.	Procedure for installing underground insulation:  Install per manufacturer's recommendations.

1.	Clean and dry the piping.

2.	Place insulation over pipe.  Temporarily tape the insulation to secure it, until longitudinal laps are sealed and butt strips are applied.

3.	Butt joints tightly and lap seal.

4.	Apply a weather-proof coating to the insulation to finish.

F.	Procedure for insulating handicapped fixtures:  Install lavatory safety kit as directed by manufacturer's instructions and in accordance with section 4.19.4 of 28 CFR Part 36.

G.	Protection of piping insulation:

1.	Insulation on piping systems shall be protected by saddles from hangers, guides and rollers.

2.	Shields, saddles or sleeves shall be installed at hangers, guides and rollers.

3.	Piping exposed to weather and piping located between floor level and an elevation of 8 feet (24 m) above the floor shall be protected by a 0.016" (0.400 mm) thick corrugated aluminum jacket.  Jacket shall be attached to the insulation by aluminum lock-type bands 12 inches (300 mm) apart.

4.	Piping exposed to the weather shall be coated with two layers of weatherproof coating of the type recommended by the manufacturer and this specification.

3.04	Installation - Ductwork

A.	General:

1.	Install insulation products in accordance with manufacturer's written instructions and with contract documents.

2.	Insulation shall be installed neatly and professionally.

3.	Do not insulate FRP ductwork or externally insulate lined ductwork.  Installation shall comply with NFPA 90A.

4.	Insulation shall be extended without interruption through walls, floors and ceiling penetrations.  Openings shall be sealed with fire resistant sealant per NFPA 90A.

5.	Installation of prefabricated ductwork panels shall comply with ASTM C1146.

B.	Ductwork systems:	Insulate the following ductwork systems:

System					Location			Insulation Type, Finish &Thickness

Supply and Return (Rectangular) 	Exposed			Rigid fiberglass and acrylic mastic

cloth - 1-1/2 inch

Supply and Return (Rectangular)		Concealed			Flexible Fiberglass Blanket - 1-1/2 inch

Supply and Return (Round)		Exposed			Flexible fiberglass blanket and acrylic

mastic cloth - 1-1/2 inch

Supply and Return (Round)		Concealed			Flexible fiberglass blanket - 1-1/2 inch

Outdoor Air Intake 			Exposed			Rigid fiberglass and acrylic mastic

cloth - 1-1/2 inch

Outdoor Air Intake				Concealed			Flexible fiberglass blanket - 2 inch

Tritium Exhaust (up to fan inlet)		All				Fire wrap

Except drops to equipment

1.	Hot ductwork:	Hot supply and return between fan or heater discharge; terminal outlets; and prefabricated, uninsulated plenums and housings.

2.	Cold ductwork:	Cold supply and return between fan or HVAC unit and terminal outlet; make-up air intake between air entrance and inlet to fan or HVAC unit; neck and bells of supply diffusers; and prefabricated, uninsulated, plenums and unit housings.

3.	Dual temperature ductwork:	Hot/cold supply and return ductwork between discharge or HVAC unit discharge and terminal outlets.  Omit insulation on return ductwork located in return air ceiling plenums.

4.	Exhaust ductwork:  Ductwork for fume and heat exhaust from rooms.  Materials conveying exhaust ductwork systems are not included in this specification.

5.	Underground ductwork:	Includes hot, cold, dual temperature and exhaust ductwork that is located under slab.

C.	Minimum insulation thicknesses are shown below:

System	Insulation                 Thickness, in. (mm)

Cold	Rigid Fiberglass	2.0  (50)

Flexible Fiberglass	2.0  (50)

Cellular glass	2.5  (62)

Flexible Unicellular	1.0  (25)

Dual Temp.	Rigid Fiberglass	2.0  (50)

Flexible Fiberglass	2.0  (50)

Calcium Silicate	3.0  (72)

Hot 	Rigid Fiberglass	2.0  (50)

Flexible Fiberglass	2.0  (50)

Calcium Silicate	3.0  (72)

CD.	Installation Procedure for Rectangular Duct Insulation:  Install insulation in accordance with manufacturer's written instructions and the contract documents.

1.	Do not apply insulation to ductwork with surface temperatures greater than 25 (F (14 (C) above or below ambient.

2.	Apply insulation adhesive to outer edge of duct.

3.	Butt insulation joints together to ensure a tight and complete fit over surfaces to be covered.

4.	Install insulation materials smoothly and evenly.  Do not use sealers or mastics as fillers on poorly fitted joints.  Redo joints.

5.	Maintain integrity of vapor barrier on ductwork insulation by protecting it from punctures and other damages.

6.	Extend ductwork insulation continuously through floors, walls, ceilings and other penetrations, unless otherwise directed by the SDR or the contract documents.

7.	Provide neatly terminated edges at interruptions in insulation, such as at locking quadrants or balancing dampers.

8.	Protect outdoor insulation from the environment by installing weather-barrier mastic protective finish or jacketing as recommended by the manufacturer or as directed by the SDR.

9.	Install corner angles on external corners of ductwork insulation before covering with jacketing or insulating cement.

DE.	Installation Procedure for Insulation of Round and Flat Oval Ductwork: Install insulation in accordance manufacturer's written instructions and the contract documents.

1.	Do not apply insulation to ductwork with surface temperatures at time of application greater than 25 (F (14 (C) above or below ambient.  Allow to cool or heat up to ambient temperature before application of insulation.

2.	Apply adhesive to outer side of duct, as recommended by manufacturer.

3.	Roll insulation around adhesive.

4.	Butt insulation joints together to ensure a tight and complete fit over surfaces to be covered.

5.	Install insulation materials smoothly and evenly.  Do not use sealers or mastics as fillers on poorly fitted joints.  Redo joints.

6.	Maintain integrity of vapor barrier on ductwork insulation by protecting it from punctures and other damages.

7.	Extend ductwork insulation continuously through floors, walls, ceilings and other penetrations, unless otherwise directed by the SDR or the contract documents.

8.	Protect outdoor insulation from the environment by installation of weather-barrier mastic protective finish or jacketing as recommended by the manufacturer or as directed by the SDR.

3.05	Installation - Equipment Systems

A.	General:	Install insulation products in accordance with manufacturer's written instructions.  Install insulation neatly and professionally.  Insulation shall be installed over cold and hot equipment when not supplied by equipment manufacturer.

B.	Equipment application systems shall include the following, unless otherwise indicated on the contract documents:

1.	Cold equipment is defined as that operating at temperatures below ambient.  Its purpose is primarily for energy conservation.  Cold equipment includes such items as refrigeration equipment, including chillers, tanks, pumps, and drip pans; cold water storage tanks; water softeners; cold and chilled water pumps; pneumatic water tanks; chilled water cooler; and roof drain bodies.

2.	Hot equipment is defined as equipment operating at temperatures above ambient.  Insulation is used over hot surfaces of equipment for energy conservation and to prevent surface temperatures above 140 (F (60 (C) where inadvertent contact is possible and to prevent surface temperatures above 120 (F (49 (C) where contact is likely or necessary for operation and maintenance of equipment.  Hot equipment includes boilers; hot water pumps, expansion and storage tanks; heat exchangers; hot water pumps, storage; expansion and flash tanks; receivers and separators; breechings, flues and stacks; converters and generators.  Prefabricated panels on hot equipment shall conform to ASTM C1146.

C.	Minimum insulation thicknesses for equipment systems are shown below:

System	Insulation	Thickness, in. (mm)

Cold,  above 35ºF  (2 ºC)	Rigid Fiberglass	2.0  (50)

Flexible Fiberglass	2.0 (50)

Cellular Glass		3.0  (72

Flexible Cellular	1.0  (25)

Cold, below 35ºF  (2 ºC)	Rigid Fiberglass	3.0  (72)

Flexible Fiberglass	2.5  (64)

Cellular Glass		4.5  (114)

Flexible Cellular	1.0  (25)

Hot,

Breechings, Stacks & Flues	Rigid Fiberglass	3.5  (88)

Calcium Silicate	5.0  (125)

Hot,

Heating Water Pumps &	Rigid Fiberglass	2.0  (50)

Storage Tanks, Condensate	Flexible Cellular	1.0  (25)

Pumps & Tanks	Calcium Silicate	3.0  (72)

Hot,

Expansion & Flash Tanks,	Rigid Fiberglass	1.5  (238)

Receivers, Separators	Flexible Cellular	1.0  (25)

& Converters

Hot,

Generators, Boilers	Rigid Fiberglass	3.5  (88)

& Fuel Oil Heaters	Calcium Silicate	4.5  (113)

D.	Installation procedure for equipment systems insulation:	Install insulation in accordance with manufacturer's written instructions or as directed by the SDR.

1.	Do not apply insulation to equipment with surface temperatures at the time of application greater than 25 (F (14 (C) above or below ambient.  Allow to cool or heat up to ambient temperature.

2.	Apply insulation using the staggered joint method for single layer only construction.

3.	Install insulation materials smoothly and evenly.  Do not use sealers or mastics as fillers on poorly fitted joints.  Redo joints.

4.	Maintain integrity of vapor barrier on equipment insulation by protecting it from punctures and other damages.

5.	Coat insulated surfaces with a layer of insulating cement and trowelled smooth, to leave a smooth continuous surface.  Fill in chipped edges, slight depressions, scored block, seams and wire netting to remove surface irregularities.

6.	Neatly fit 0.016 inch thick (0.400 mm) aluminum all-service jacketing over the insulated surfaces.  Lap seams a minimum of 2 in. (50 mm), and firmly secure.

7.	Provide neatly terminated edges at interruptions in insulation.

8.	Do not insulate boiler manholes, handholds, cleanouts, nameplates and ASME certification stamps.

9.	Provide insulation housings over areas that must be periodically accessed for maintenance, including pumps, tanks, generators, and converters.  Include removable covers, fasteners, flanges, frames and accessories.

10.	Provide covers of rigid fiberglass, in the same thickness as surrounding insulation, adhered to aluminum sheet metal.

11.	Protect outdoor insulation from the environment by installing weather-barrier mastic protective finish or jacketing as recommended by the manufacturer or as directed by the SDR.

3.06	Installation - Repair and Replacement

Repair damaged sections of insulation by first removing damaged sections. Replace with insulation meeting or exceeding properties of existing insulation.  Lap new jacket over existing jacket and seal, as stated in previous sections of this specification.

3.07	Field Quality Control

A.	Inspector shall ensure that insulation is installed according to this specification in a neat and professional manner.

B.	Contractor shall be required to repair or replace insulation that is not applied in strict accordance with this specification.

3.08	Cleaning

Contractor shall allow any sealants, mastics or adhesives time to cure before insulated items or systems are cleaned.  Contractor shall ensure that items or systems insulated are cleaned and that the insulation does not affect the operation of system that it is insulating nor that of the surrounding nor that of connecting systems.

3.09  COMMISSIONING

Provide labor, material, equipment, etc., required to facilitate the comissioning process.  Perform form tests and verification procedures required by the commissioning process when requested by the Commissioning Authority and directed by the General Contractor.  See Section 15995.

END OF SECTION