July 22, 1994

Contract #TW0592

SPECIAL SPECIFICATION

SECTION 01065

environment, safety and health regulations for construction

Page

1.01	GENERAL	2

1.02	STANDARDS & REGULATIONS	2

1.03	SUBMITTALS	2

1.04	QUALITY ASSURANCE	3

1.05	MEDICAL	4

1.06	PERSONAL PROTECTIVE EQUIPMENT	5

1.07	HOUSEKEEPING	5

1.08	HAZARDOUS WASTES	6

1.09	SAFETY PRACTICES	9

1.10	HEALTH PROTECTION	9

1.11	EQUIPMENT	9

1.12	FIRE PROTECTION	10

1.13	HAZARD COMMUNICATION PROGRAM	11

1.14	CONFINED SPACE ENTRY	14

1.15	LOCKOUT AND TAGOUT OF UTILITIES AND EQUIPMENT (LOTO)	18

1.16	OTHER SAFETY PRACTICES	20

1.17  CONSTRUCTION VEHICLE & HEAVY EQUIPMENT SAFETY REQUIREMENTS	23

ATTACHMENTS	24

sPECIAL SPECIFICATION

SECTION 01065

environment, safety and health regulations for construction

1.01	GENERAL

The Contractor shall provide and maintain all safeguards, safety devices and protective equipment. The Contractor shall take any other actions as required by Sandia National Laboratories (SNL) to protect the life and health of employees on the job, the safety of the public, the environment, and government property in connection with the performance of the work required by the contract. This specification may identify additional requirements not contained in 29 CFR 1910 and 29 CFR 1926.

1.02	STANDARDS & REGULATIONS

Requirements of compliance with standards and regulations include, but are not necessarily limited, to compliance with all applicable sections of the following Occupational Safety and Health Administration Standards (OSHA):

A.	29 CFR Part 1926, Safety and Health Regulations for Construction, latest edition.

B.	29 CFR Part 1910, General Industry Occupational Safety and Health Standards which are applicable to construction work, latest edition.

C.	49 CFR Part 325 and Parts 350-399, Department of Transportation Motor Vehicle Transportation Requirements.

1.03	SUBMITTALS

The Contractor shall submit job site specific safety plan per Section II, Article No. A67, Part V of Standard Terms and Conditions for Fixed-Price Construction Contracts. The Contractor shall also submit proof that its subcontractors are contractually obliged to follow the safety plan submitted for the project. Additionally the following documents must be submitted for review and approval prior to the start of on-site work.

A.	Safety Officer:  The Contractor shall identify the on-site safety officer and any alternates for work on this contract.  The Safety Officer will insure compliance with applicable construction Safety Health and Environment Protection requirements. This individual will be subject to approval by SNL's Sandia Delegated Representative (SDR) based upon the scope of the work, the anticipated hazards, and the training and experience of the designated safety officer.

B.	Safety Report:  	The Contractor shall submit a weekly safety report when requested by the (SDR).  This safety report shall contain but not necessarily be limited to the minutes of the weekly safety meetings and attendance rosters, as described in Section 1.04 of this specification.  Also to be included are the accident/incident statistics pertaining to the contract for work performed by the Contractor and their subcontractors

C.	Accident Reporting:  All on-site accidents, regardless of how incidental, including those sustained by subcontractors, are to be reported to the Contractor's safety officer.

1.	The Contractor's safety officer shall fully investigate all accidents and shall fill out the appropriate accident report form on the day of the accident.

2.	The Contractor's safety officer shall notify the SDR and shall submit a completed SNL form, SF 2050-PC, "Contractors/Visitors Report of Occupational Occurrences" (Attachment 'A'), on all accidents which result in an injury or work related illness to any person.  The notification shall describe in writing the circumstances of the accident and the corrective action taken.  The notification and submittal shall be within 24 hours of any such injury.

3.	The Contractor's safety officer shall submit, at the SDR's request, a report outlining details involving any safety-related incident occurring on the job site.  The report shall describe the circumstances of the incident and the corrective action taken.

1.04	QUALITY ASSURANCE

The Contractor shall comply with the following site specific operations:

A.	Safety Meeting: The Contractor shall conduct weekly safety meetings. The meeting agenda and required report shall contain the following topics:

1.	Contract number and date of the meeting.

2.	Person conducting the meeting.

3.	Signatures, printed names, and social security number of employees in attendance.

4.	Topics discussed.

5.	Findings and corrective actions.

6.	Warnings issued.

7.	Report signed by preparer.

B.	Documents On-site:  The Contractor shall have the following documents and signage posted:

1.	SNL - supplied poster with emergency telephone numbers.

2.	SNL - supplied poster with project personnel telephone numbers.

3.	Contractor project personnel poster with telephone numbers.

4.	SNL - supplied OSHA poster EH F 5480.1, latest edition.

5.	Hazard identification signage and barricades to warn personnel of construction hazards.  Hazardous areas or conditions requiring marking include but are not limited to safety glasses areas, hard hat areas, high pressure areas, overhead work areas, open excavation areas, loading limits, non-potable water, high-voltage, hazardous material storage areas, explosive hazards, flammable hazards, floor opening hazards, open-sided platforms, hearing hazards, sandblasting and welding or cutting flash hazards.

6.	Other postings as specified in the drawings or any specifications or by the SDR.

The Contractor shall provide and maintain a safety bulletin board per standard drawing No. 101726 (Attachment 'B') required in Section I of this contract.

C.	Documents Readily Available:  The Contractor shall have the  latest edition of the following documents readily available for all projects and available on-site for projects greater than $50,000:

1.	29 CFR Part 1926, Safety and Health Regulations for Construction

2.	29 CFR 1910 - Safety & Health Regulations for General Industry

3.	SNL Special Specification 01065 - Environment, Safety and Health Regulations for Construction

4.	A copy of the Contractor's SNL approved safety plan

1.05	MEDICAL

A. 	On-site First Aid

1. The Contractor shall provide and maintain first aid kits, commensurate with the number of employees on the job site as outlined in 29 CFR 1926.23, and on all company vehicles.  The Contractor shall assure that an individual trained in first aid procedures is available at or near the work site.

2.	Medical and non-medical emergency telephone numbers are to be posted on the site within view of telephones.

B.	Emergency Action

1.	The Contractor shall be responsible for transportation of all  non life-threatening injuries that require medical attention.

2.	For all life-threatening injuries or illnesses, the Contractor shall immediately call for medical assistance by dialing 144 on a SNL telephone or (505) 846-0081 on an outside telephone.

1.06	PERSONAL PROTECTIVE EQUIPMENT

A.	The following list of personal protective safety equipment shall be used, as required by 29 CFR 1910 and 29 CFR 1926, on SNL projects by the Contractor's and the subcontractor's employees.

1.	Safety glasses/eye and face protection

2.	Safety shoes

3.	Hearing protection

4.	Hard hats and warning vests

5.	Respirators

6.	Gloves

7.	Safety belts/harnesses/slings

8.	Fall protection

B.	Hard hats shall be worn at all times during the performance of work on SNL construction contracts unless a written waiver is obtained from the SDR.  This waiver must be visibly posted at the job site.

1.07	HOUSEKEEPING

During the course of construction, non-regulated waste material that is not to be used for its intended purpose and that cannot be reapplied, is likely to develop. Excess materials such as lumber, nails, spent welding rods, cans, and personal trash must be properly disposed.  This waste material should never be left in trenches or excavations.  Waste material should be properly stored or contained until it is removed from the job site.   The discarding of such waste material needs to be done according to guidelines established by Sandia National Laboratories.

Both the Contractor's and all subcontractor's employees shall at all times during construction keep all debris clear from work areas, passageways, stairs and in and around buildings or other structures.  The following shall be performed to ensure a safe work environment:

A.	Continuous policing of all work areas.

B.	Daily and regular clean up and waste disposal of non-regulated material.

C.	Assignment of personnel to regular clean-up duties and responsibilities.

D.	Segregation of hazardous and non-hazardous waste.

E.	Documented legal disposal of debris.

1.08	HAZARDOUS WASTES

A.	Wastes generated during construction are considered hazardous wastes if they are listed waste under 40 CFR 261, Subpart D or are characteristic waste, or is a mixture of a listed waste and solid waste. Characteristic hazardous wastes are those that are ignitable, corrosive, reactive or toxic. Examples of construction wastes that can fall into one or more of these classifications are ignitable wastes, strong acids and bases and solvents.

B.	How you handle these hazardous wastes and the precautions necessary are dependent on the type and quantity of hazardous wastes generated.  Check with the SDR or Construction Inspector/Observer concerning the requirements for management and disposal of these wastes.  The practices to insure environmental protection when dealing with hazardous wastes should include but not necessarily limited to the following:

1.	Contain hazardous wastes in acceptable containers, provided by SNL, capable of isolating the hazardous waste from the environment. All hazardous wastes should be placed in the container, not on the container, with no evidence of dripping, pooling, or overfilling. Containers must always be kept closed, except when immediately adding or removing waste. Screw in funnels with spring lids may be used with drums for easier access and are considered closed when the lid is down. Containers must be made of or lined with materials compatible with the wastes stored: Use the original container or a similar type of container to hold waste; don't use metal containers to hold corrosive wastes; do not use plastic containers to hold solvent wastes; incompatible wastes or materials must not be placed in the same container. Waste must not be placed in an unwashed container that previously held an incompatible waste or material.

2.	Segregate all wastes	. Do not mix incompatible waste in the same container. Segregate halogenated solvents from non-halogenated solvents. Segregate flammables from combustibles. Maintain a "Waste Addition Log" of every addition of waste into the container. The log should contain the date, quantity, unit, composition, and generator. It should be submitted with the Chemical Waste Disposal Request (CWDR) form when ready for disposal.

3.	Label all containers that hold chemical waste. The label must be affixed to the container as soon as the container contains waste. All waste labels, provided by SNL, must contain the following information and must be filled in with permanent, weather-resistant ink: Accumulation Start Date; Full date; Contents; Company Name; SNL Organization; Telephone Number; and Disposal Request Number (corresponds to CWDR form).

4.	Store all wastes at or near the point of generation. Containers must be stored to prevent accidental ignition or reaction of ignitable or reactive waste by storing away from sources of ignition or reaction such as flames, smoking, cutting and welding, hot surfaces, friction heat, strong oxidizers, sparks, and radiant heat such as direct sunlight. Protect wastes that are subject to volatilization and container over pressurization from direct sunlight or heat.

Physically separate containers with incompatible wastes from each other such that leaks and spills will not mix by using berms or spill absorbent barriers or by storing the incompatible wastes in separate boxes, cabinets, or locations.

Secondary containment is required for waste containers located outside, inside near a floor drain, or where the possibility exists that spilled liquid or solid waste could be discharged to the environment. Under no circumstances should waste be stored on the ground. Containment pallets will be provided by SNL on an as needed basis. Spilled or leaked hazardous waste must be removed from the containment collection the same day the spill is noticed and managed as hazardous waste. If waste is stored outside, efforts should be made to prevent precipitation from collecting in the secondary containment pallet, such as building protective sheds or covers. If precipitation collects in secondary containment and some hazardous waste is present, the water may have to be managed as hazardous waste. Under no circumstances should this water be discharged to the ground or the sanitary sewer before it has undergone analysis or a determination is made whether the material is a hazardous waste. If required by the scope of the project the contractor shall construct a satellite waste storage area as per drawing HW/1 (Attachment 'C').

Special storage requirements must be met when handling flammable and combustible hazardous waste. Flammable wastes should be stored in their original labeled containers or in an approved flammable storage cabinet or in a safety can that is left intact (do not remove the flame-suppresser). Check with your SDR or Construction Inspector/Observer concerning requirements when flammable storage cabinets may be required. Containers should be visually inspected weekly for leaks, spills, and excessive deterioration and noted in a log. Provide "No Smoking" signs whenever there is a hazard from flammable or reactive waste.

5.	All hazardous wastes must be listed on a CWDR form for removal to the Hazardous Waste Treatment Storage and Disposal Facility within 240 days of the accumulation start date. No more than 55 gallons (solid or liquid) of hazardous waste or 1 quart of acutely hazardous waste will be allowed in accumulation on any site, the excess must be removed within 3 calendar days.

A container that has held any hazardous waste (except a waste identified as an acute hazardous waste) is defined as empty if: all wastes have been removed that can be removed by pouring, pumping, and/or aspirating; no more than 2.5 centimeters (1 inch) of residue remains on the bottom of the container; or no more than 3 percent by weight remains in the container (if the container is less then 110 gallons.) All empty containers that have held acute hazardous waste must be noted as "Empty", listed on a CWDR, and disposed of. All empty drums, 5-gallons or greater, must be labeled "Empty", listed on CWDR, and disposed of . Empty containers, less than 5-gallon capacity, that held hazardous-but not acutely hazardous waste or chemicals, may be disposed of in the SNL trash. Glass containers should be segregated and labeled "Glass" to prevent injury to trash handlers.

Gas cylinders are considered empty when the cylinder pressure reaches 25 psig or approaches ambient atmospheric pressure. In order to prevent contamination of the cylinder, a minimum pressure of 25 psig should be maintained. Lecture bottles that are no refillable and non returnable should be accurately described on a CWDR for waste disposal. Larger gas cylinders should be returned for reuse to the compressed gas vendor.

6.	All hazardous waste must be disposed of through the Chemical Waste Department and the Construction Acceptance Department at SNL. Following is the procedure for disposal of waste:

a.	Fill out a CWDR form and submit it to your Construction Inspector/Observer within 240 days of the waste accumulation start date or before the volume limit (55 gallons) is anticipated. When the volume limit is exceeded the waste must be removed within 3 calendar days. CWDR forms are available through the Construction Acceptance Department.

b.	Finish filling out the appropriate label and information on the container, full date, company name, company telephone number, etc..

c.	Ensure that all storage requirements are met until personnel from the Chemical Waste Department remove the waste.

7.	All contractors must have appropriate spill response equipment readily available on site. Spill response equipment includes absorbents (such as "pigs" or "hot dogs"), plastic buckets with lids or plastic bags for containing used absorbents, etc. Spilled materials should be treated as hazardous waste until assessed and cleared by SNL personnel. If a spill occurs, if possible, try to contain the spill, evacuate unnecessary personnel, contact your Construction Inspector/Observer immediately and, if there is an injury, immediately call 144 on a SNL telephone or (505) 846-0081 on an outside telephone. The Construction Inspector/Observer will notify the appropriate Facilities personnel to determine the proper response and necessary PPE to be used during all chemical handling and spill clean up.

8.	Contractors with hazardous waste management activities or hazardous waste sites, in the scope of their project, must have the necessary regulatory mandated training to perform the duties required.

Check with the SDR or Construction Inspector/Observer concerning all SNL/NM policies associated with hazardous waste management requirements that will apply during the course of the project.

1.09	SAFETY PRACTICES

A.	Both the Contractor's and subcontractor's employees shall practice safe operating procedures during on-site work.

B.	Hard hat area designations will be respected and adhered to by all personnel, including visitors.

C.	Other requirements from SNL for personal protective equipment will be respected and adhered to.

1.10	HEALTH PROTECTION

A.	Drinking Water:  In accordance with 29 CFR 1926.51, potable drinking water shall be provided at all job sites.  Drinking water containers shall be available at the job sites.  These containers will be kept in a sanitary condition and cleaned daily.  Disposable cups and trash containers shall be provided.

B.	Toilet Facilities:  Chemical toilets shall be serviced on a weekly basis.

C.	Hazardous Environments:

1.	The Contractor's employees and any subcontractors employees shall not be exposed to a hazardous environment without first fully investigating and analyzing the dangers of such an environment.  The Contractor shall seek assistance from SNL or other agencies to overcome or remove any such environment or to recommend protection for the workers prior to any work activities in hazardous environment areas.

2.	The Contractor shall direct their employees and any subcontractor's employees as to where to eat. The designated eating area shall be separate from areas that have toxic materials present. The Contractor's and subcontractor's employees may eat in areas "owned" by SNL with the SDR's permission.

1.11	EQUIPMENT

A.	The Contractor and any subcontractor shall adhere to the following safety practices:

1.	Conduct and document operator indoctrination and briefing on operating procedures.  Documentation shall be readily available.

2.	Conduct and document periodic inspection of equipment in use. Documentation shall be readily available.

3.	Report equipment and safety problems noted by the operator.

4.	Perform daily maintenance procedures per manufacturer's recommendations.

5.	Defective hand tools shall be removed from the job site or repaired immediately.

6.	Conduct daily site inspections by project foreman and/or general superintendent.

7.	Conduct weekly site safety inspections by project foreman and/or general superintendent and shall have written documentation of these inspections readily available.

8.	Adhere to and obey motor vehicle regulations, such as posted speed limits, seat belts usage, pedestrian right-of-way, entry to authorized areas and roadways only, and any other safety practice which will ensure the safe operation of equipment and vehicles.

B.	Electric Power Tools:  All electric power operated tools shall be used with extreme caution.  Only listed extension cord sets will be allowed.  Listed extension cord sets shall be of the three-wire type and shall be designed for hard or extra-hard usage.  Listed extension cord sets shall be protected from damage when passing through doorways and other pinch points.  All electric power operated tools shall be properly maintained.  Any tool that is not working properly or that develops a defect during use, shall be immediately removed from service and not used until properly repaired and tested.

C.	Powder Actuated Tools:  Authorization shall be obtained from the SDR prior to any use of powder actuated tools.  Extreme caution will be taken and only qualified and authorized personnel shall use any powder actuated tool.  The Contractor shall have readily available documentation of power actuated tool training.  These tools shall only be used when no other tools are available to perform the task successfully.  Requirements for the use of powder actuated tools are listed in 29 CFR 1926.302.

D.	Hand Tools:  All hand tools shall be used in a safe and workmanlike manner.  Hand tools shall be picked up and stored in appropriate tool storage boxes when not in use.  Defective hand tools shall be removed from the job site or repaired immediately.

1.12	FIRE PROTECTION

A. 	Equipment

1.	Provide fire extinguishers that have a current certification of acceptability, as required by size and type and meet OSHA regulations and employee training the their use as required by OSHA regulations.

2.	Provide water barrels near critically dry areas.

3.	Conspicuously post necessary action to take in the event of fire.

4.	Mark and identify all fire hazard activities and materials.

5.	Provide clear access to all areas for fire-fighting equipment and hose lines.

6.	Provide and maintain clear aisle ways and means of egress.

B.	Emergency Telephone Numbers

1.	Dial 117 from an 844, 845, or 846 exchange number.

2.	Dial 844-0903 from outside numbers.

C.	Fire Prevention

1.	Continuously eliminate hazardous, combustible, and flammable materials and debris.

2.	Clean-up rubbish daily.

3.	Provide separate storage for flammable materials.

4.	If more than 5 gallons of flammable liquids or gases are stored in any contractors on-site trailer, the trailer needs to be placard on the outside with either a NFPA 704 Diamond placard or a Sandia hazard sign.

5.	If more than 25 gallons of flammable liquids are stored in any on-site trailer, these materials need to be stored in a flammable liquids storage cabinet.

6.	Provide approved, contained storage for waste flammable and combustible materials that provides environmental protection in the event of a spill or leak.

7.	Provide regular inspections of internal combustion equipment, heating equipment, and wiring.

8.	Cans and containers used for the storage or dispensing of flammable liquids must meet OSHA requirements

D. 	Permits:  The Contractor shall obtain a permit from SNL for the following:

1.	Cutting and welding.

2. 	Any open flame.

3. 	Tar kettles and roofing solvents.

4.	Fire Sprinkler or Fire Alarm impairment or modification.

5.	Exothermic welding.

1.13	HAZARD COMMUNICATION PROGRAM

This program has been prepared to provide the Contractor with information to comply with the requirements of the 29 CFR 1926.59 and 29 CFR 1910.1200 and to ensure that information necessary for the safe use, handling and storage of hazardous materials is provided to and made available upon request to employees and to all SNL, local, state, and federal officials who have proper authority.

This program includes guidelines on identification of materials and material hazards and the preparation and proper use of container labels, placards and other types of warning devices.

A.	Chemical Inventory:  The project superintendent shall inventory the site and record the identity and location of any hazardous substance existing or brought on-site.  The project superintendent shall obtain the material safety data sheet (MSDS) provided by the supplier.  The hazardous substance shall be added to the job site master chemical inventory list.  This list is to be readily accessible on the job site. The master chemical inventory list shall be maintained and updated weekly by the superintendent.

B.	Material Safety Data Sheets (MSDS)

1.	MSDS shall be kept in a central repository on-site for each hazardous substance.

2.	MSDS shall be obtained for each hazardous substance. If MSDS are not provided with the shipment, the superintendent shall obtain one from the manufacturer, importer or distributor. Hazardous materials shall not be used on-site until MSDS have been provided and are on the job site.

3.	Employees working with a hazardous substance may request a copy of the MSDS.

C.	Container Labeling

1.	All chemicals on-site shall be stored in their original or approved containers with a proper label attached, except small quantities for immediate use during the work shift.  Labeling requirements become effective after one shift of work (they are, if the product in the unlabeled containers product is not used in the shift or workday, it must be labeled).  Any container not properly labeled should be given to the superintendent or his designated representative for labeling and/or proper disposal.

2.	Workers may dispense chemicals from original containers only in quantities intended for immediate use.  Any chemical left after work is completed must be returned to a properly labeled container or to the superintendent or his designated representative for proper handling.

3.	No unmarked containers of any size are to remain in the work area unattended.

4.	The Contractor shall rely on manufacturer-applied labels whenever possible and shall ensure that these labels are maintained.  Containers that are not labeled or on which the manufacturer's label has been removed shall be relabeled.

5.	The Contractor shall ensure that each container is labeled with the identity of the hazardous substance contained and shall identify any appropriate hazard warning.

6.	Labels must be legible and in English.

D.	Employee Training:  Employees shall be trained to work safely with hazardous materials.  Employee training shall include, but not necessarily be limited to documented training in:

1.	Methods that may be used to detect a release of a hazardous substance(s) in the workplace.

2.	Physical and health hazards associated with chemicals.

3.	Protective measures to be taken.

4.	Safe work practices, emergency responses and use of personal protective equipment.

5.	Information on hazard communication standard including:

a.	Labeling and warning systems.

b.	An explanation of MSDS.

c.	An explanation of the right to access the MSDS.

E.	Personal Protective Equipment (PPE):  Required PPE must be available from the Contractor, kept in good condition, properly maintained, and properly worn.  Any Contractor employee found in violation of PPE requirements may be subject to removal from the job site.

F.	Emergency Response

1.	Any incident of over-exposure to an employee or an uncontained spill of hazardous substance must be reported to the superintendent immediately.

2.	The superintendent or the immediate supervisor shall notify the SDR immediately of such an occurrence.

3.	The superintendent or the immediate supervisor shall be responsible for ensuring that proper emergency response actions are taken in leak/spill situations.

G.	Hazards of Non-Routine Tasks

1.	Supervisors shall inform employees of any special tasks that may arise which would involve possible exposure to hazardous materials.

2.	Supervisors shall review with the affected employees safe work procedures and the use of required PPE prior to the start of such tasks.  Where necessary, areas shall be posted to indicate the nature of the hazard involved.

H.	Information to Other Employees

1.	All on-site employers are required to adhere to the provisions of the hazard communication program.  Employers shall be responsible for providing necessary information to their employees and to provide their employees with the training mandated in 29 CFR 1926.59 and 29 CFR 1910.1200 as applicable.

2.	Each subcontractor on each job site is required to present to the general contractor verification that subcontractor employees have received hazard communication training.

3.	All on-site employers (subcontractors) shall be provided with a copy of this hazard communication program.

4.	Each subcontractor on each job site is required to present to the general contractor, through the superintendent or the safety officer, an MSDS for each hazardous substance which it will bring to the job and to which any employee on the job may be exposed.  The compilation of MSDS from subcontractors shall be added to the Contractor's repository.

I.	Posting:  The Contractor shall post information for employees at each job site on the hazard communications program.  This information shall be posted on the project safety bulletin board.

1.14	CONFINED SPACE ENTRY

This section sets forth minimum requirements for equipment, training and procedures for the safe entry, continued work in, and egress from confined spaces in connection with work on this job site at SNL/NM. It is the Contractor's responsibility to insure that these requirements are met for each entry. Additionally the contractor is required to have at each confined space entry point where contractor personnel are making a confined space entry, copies of the following:  the entry permit (reference Attachment 'D'), a copy of the contractor's confined space entry program, a copy of this specification and written documentation of the confined space safety training of those individuals making the confined space entry and or serving as the attendant.

A.	This program applies to all confined or enclosed spaces as described below:

1.	An area large enough and configured in such a way that it can be bodily entered.

2.	An area with limited means of access and egress.

3.	An area which has a known hazard or a potential for hazard.

4.	An area with poor or unfavorable ventillation.

5.	An area not designed for continuous occupancy.

B.	Confined or enclosed spaces include but are not necessarily limited to storage tanks, vessels, manholes bins, boilers, ventilation or exhaust ducts, sewers, utility vaults, tunnels, pipe, and open top spaces more than four (4) feet in depth, such as pits, tubs, vaults vessels, and in some instances excavations.

C.	Surface Precautions:  A barricade or other means to prevent unintended entry into the confined space shall be erected around the entrance to the confined space. In addition to barricading, in instances where the confined space is in or adjacent to a road or travel way, a vehicle or Jersey Barrier shall be positioned to protect personnel from vehicular and pedestrian traffic.

D.	Equipment: As a minimum the contractor shall provide the following equipment, for use by their personnel whenever confined space entry is made.

Air Monitoring/Sampling Meter  --  The meter as a minimum shall meet the following criteria:

1.	Shall be direct reading.

2.	Shall read % volume for oxygen deficient and enriched atmospheres.

3.	Shall be intrinsically safe for Class 1, Division 1 atmospheres, per the National Electric Code Standards.

4.	Shall read combustibles in % Lower Explosive Limit (LEL).

5.	Shall have both audible and visual alarms.

6.	Shall be capable of continuous, automatic operation.

7.	Shall have intrinsically safe, motorized pump for remote sampling.

8.	Shall be intrinsically rated by a Nationally Recognized Testing Laboratory (NRTL).

9.	Shall read toxic substances in units of measure (i.e. ppm, ppb, mg/m) appropriate for the hazards or contaminants involved. The selection of the sensor shall be determined by the work to be performed and the type of materials used.

10.	Shall be capable of field calibration.

11.	Shall be used and maintained by trained personnel in accordance with the manufacturers requirements.

12.	Shall have written documented field calibration prior to each entry.

13.	Shall have factory calibration records for this equipment readily available.

14.	Shall be RFI hardened.

15.	Should be easy to maintain and calibrate.

Fall Arrest and Retrieval Equipment - the equipment as a minimum shall meet the following criteria:

1.	Shall have a full body harness with a back centered, near shoulder-head level, retrieval line attachment point.

2.	Shall have a mechanical retrieval system that shall be "man rated", designed for human lifting and lowering. This system shall not be vehicle mounted, shall be capable of handling a minimum 300 pound working load and shall have a "dead man" or "fall arrest" brake to prevent uncontrolled slippage while lowering-raising personnel.

3.	Shall have a mechanical retrieval system that is attached to a fixed anchor point (generally a tripod) outside of the confined space.

4.	Retrieval tripods and winches should be NRTL approved.

5.	Wristlets should not be used in vertical entries.

6.	Shall be used by trained personnel in accordance with manufacturers guidance.

Ventilation Equipment - the equipment as a minimum shall meet the following criteria:

1.	Shall be electric motor driven and the motor shall be explosion proof.

2.	Shall be capable of delivering a minimum of 700 CFM of air.

3.	Shall be heavy duty, industrial grade design of centrifugal (squirrel cage), axial, or a venturi type. Note: venturi type ventilators run by compressed air shall not introduce contaminants into the ventilation equipment.

4.	Shall not create a noise level greater than 90 dBA inside the confined space.

5.	Shall be capable of providing one fresh air exchange in the confined space every three minutes.

6.	Shall have sufficient ducting to allow lowering of the ducting to at least the bottom of the space while still allowing topside/outside positioning of the blower at least five (5) feet from the surface entrance.

7.	Shall be used and maintained by trained personnel in accordance with the manufacturers guidance.

E.	Training:

The contractor shall provide documented proof of formal confined space training to the SDR or his/her designee prior to the commencement of on-site confined space work for all contractor and sub-contractor personnel entering into confined spaces, serving as a confined space attendant or as an individual monitoring the atmosphere in the confined space. This training shall include all applicable regulatory requirements including but not necessarily limited to:

1.	The hazards associated with confined space entry and work.

2.	The hazards associated with oxygen deficient and enriched atmospheres.

3.	The hazards associated with toxic materials or air concentrations either present or potentially present in the confined space or introduced into the confined space during the course of the entry.

4.	The operation and use of rescue and retrieval equipment.

5.	The operation, field calibration, and use of the air monitoring/sampling equipment used at the job site.

6.	Emergency procedures.

7.	The roles and responsibilities of the entry, attendant, and supervisory personnel.

F.	Preparation for Confined Space Entry:

The following is general guidance concerning confined space entry. Contractors shall check with the SDR or his/her designee concerning any specific requirements or unusual hazards in the confined spaces they will be entering before any entry is made. In most cases the contractor will utilize the permit and process in Attachment 'D'. The Sdr or his/her designee shall be the Contractor's primary point of contact for operations relating to confined space activities.

The following list identifies some confined spaces that generally require additional pre operational review before confined space entry is made. Other known or suspected hazards may also require additional pre operational review.

1.	Confined space entry into known high hazard spaces previously identified by SNL.

2.	Activities such as welding, hot work, high voltage work, or high noise generation

3	The use, generation, or presence of toxic substances that the contractor is incapable of monitoring for.

4.	The use of respiratory protection equipment.

5.	The presence of ionizing radiation.

The Contractor's employees and any subcontractor's employees shall not enter the confined space until the following conditions have been completed in the listed sequence:

1.	The Contractor's employees making the entry review and utilize the standard confined space entry permit and accompanying flow chart (attachment 'D'). This permit to be posted at the entry site during the entire duration of the entry.

2.	The on-site contractor supervisor will be responsible for conducting a pre-entry safety briefing with the entry personnel, attendants, and others working in the immediate area.

3.	The contractor will insure that energy sources within the confined space area are secured as required in the lock-out/tag-out section of this specification, Section 1.15.

4.	The atmosphere in the confined space is found to be safe by testing at all levels in the space for oxygen deficiency/enrichment and the presence of combustible, explosive, or toxic gases or liquids for a minimum of 3 to 5 minutes. The minimum oxygen content is 19.5% (percentage by volume) and the maximum allowable oxygen content is 23.5% (percentage by volume). The maximum allowable LEL is 5%. If toxic material is suspected and sampled for, the maximum allowable levels will be one-half the current OSHA Permissible Exposure Level (PEL) or action level whichever is lower. Prior to use in confined spaces the testing equipment shall be field tested in fresh air in accordance with the manufacturer's instructions.

5.	If initial tests indicate an Immediately Dangerous To Life and Health (IDLH) situation, entry procedures will be halted. This situation is unacceptable for entry per SNL's requirements. The SDR or his/her designee shall be contacted and SNL Industrial Hygiene will be contacted for further evaluation of the confined space.

6.	The confined space shall be purged for a minimum of 3 air exchanges, or as specified in the confined space entry permit.

7.	After venting, the atmosphere in the confined space will be retested exactly as described above (step 4).

G.	Work in Confined Spaces

1.	Continuous air monitoring equipment is required in all cases and ventilation is required to be provided for almost all confined spaces. The ventilation to be provided by a power-driven blower, the output of which will be blown into the space so that any accumulating gases will be replaced by fresh air. The blower shall be located such that the exhaust fumes from vehicles or the equipment itself shall not be forced into the confined space.

2.	Retrieval equipment is required to be provided and used in almost all confined space entry. This retrieval equipment must meet the requirements set forth in Section D, Fall Arrest and Retrieval Equipment.

3.	While individuals are in the confined space an employee shall be a "designated attendant" at the surface of the confined space.  The duty of this individual is to observe and provide emergency assistance as required to other personnel working in the confined space.  The "designated attendant" cannot leave the confined space area and their sole job is as "designated attendant."

4.	The SDR or the Inspector/Observer shall be notified immediately and personnel shall be prohibited from entry or re-entry into the confined space when conditions are deemed unsafe for entry. The SDR or Inspector/Observer may arrange for additional testing and consultation.

5.	Contractor personnel SHall NOT attempt confined space rescue that requires entry into the confined space to retrieve personnel.  Contact SNL security by phoning 144 on a SNL telephone or (505) 846-0081 on an outside telephone.

1.15	LOCKOUT AND TAGOUT OF UTILITIES AND EQUIPMENT (LOTO)

A.	The Contractor shall comply with the following when performing lockout and tagout of utilities and equipment:

1.	Verify that normal stopping procedures have occurred.

2.	Relieve, restrain, or otherwise render safe all potentially hazardous-stored energy.

3.	Operate the associated controls to make certain that there is no release of energy.  After checking controls ensure they are returned to the neutral or off position.

In addition to the requirements of 29 CFR 1926.417 and 1926.950(d)  the following conditions shall apply, in order of precedence:

B.	Lockout Requirements

1.	NEC and SNL required lock(s) and tag(s) shall be applied on de-energized equipment or circuit(s) at energy isolating devices capable of being locked out.  Tag(s) shall be attached by a means that will stand a 50 lb. force (i.e. plastic cable tie). Where locking provisions do not exist locking mechanisms shall be added by the use of additional equipment (i.e., chains, valve "doughnuts," etc.).

2.	Where energy-isolating devices are not capable of being locked out:

a.	De-energized equipment or circuit(s) shall have the ungrounded conductor(s) removed from the energy isolating device and be insulated.

b.	Valve handles shall be removed from the valve assembly and secured adjacent to the valve assembly.

3.	Where locking provisions do not exist, and it is impractical to comply with Item #2 above, tag(s) alone will suffice.

C.	Lock Requirements

1.	Locks shall be capable of withstanding the environment to which they are exposed for the maximum period of time that exposure is expected.  Locks can be either keyed or combination.

2.	The key or combination of the lock shall be under the exclusive control of the employee applying the lock.

3.	Locks shall be applied by all personnel who could be endangered by the restoration of energy.

4.	Multiple hasp arrangements shall be used where more locks are required than the locking provisions provide for.

D.	Tagging Requirements

1.	Tags shall be applied wherever a lock is applied.

2.	Tags shall be capable of withstanding the environment to which they are exposed for the maximum period of time that exposure is expected.  Exposure to weather conditions, wet or damp locations, or corrosive environments shall not cause the tag to deteriorate or the message on the tag to become illegible.

3.	Tags shall include the following:

a.	A description which warns against the introduction of the energy source, and a legend such as DO NOT START, DO NOT ENERGIZE, DO NOT OPERATE, etc.

b.	The employee's name and employer.

c.	The date of installation.

1.16	OTHER SAFETY PRACTICES

A.	Storage Areas:  The location of all temporary storage shall be approved by the SDR.

B.	Protection of Government Property and Access

1.	Locate existing utilities.

2.	Make necessary traffic arrangements for transporting heavy equipment or materials.

3.	Locate temporary buildings and storage areas to facilitate access to construction areas.

4.	Contact the SDR for any road blockage.

C.	Construction Operations

1.	Excavation

a.	"Competent person" as required as per 29 CFR 1926.650.

b	Obtain a digging permit prior to any digging.

c.	Insure proper clearance between machines and/or equipment and any other objects or structures.

d.	Illuminate and barricade holes and trenches as necessary.

e.	Shore, bench, and or slope trenches as required.

f.	Provide proper access/egress from excavation wherever people are working in excavation (i.e., ladder every 25' laterally).

g.	Provide daily inspection by competent person and additionally as required per 29 CFR 1926.650.

2.	Concrete

a.	Ground all portable electric tools that are not double insulated.

b.	Provide a signal man for directing transit mix trucks.

c.	Use goggles or other appropriate eye protection as needed when pouring, chipping or grinding concrete.

d.	Clean out concrete trucks only at the designated areas.

3.	Overhead Work:  All work performed in concealed overhead areas shall be accomplished during SNL non-standard hours. These areas include, but are not limited to, work around roof openings and on walkways and platforms above ceilings. Work in concealed overhead areas may require special site work procedures before beginning such work.  The Contractor shall coordinate with, and obtain a permit through, the SDR for work to be performed during non-standard hours.

4.	Crane Operations:  SNL has special requirements for cranes brought onto the job site.  The Contractor shall check with the SDR or the Construction Inspector/Observer concerning these requirements.

a.	Use extreme caution when moving cranes to insure that there is no contact with aerial power lines.

b.	Constantly check slings and riggings and immediately remove damaged, worn, frayed slings and riggings from service and from SNL property as soon as possible.

c.	Provide adequate escorts, signal and flag-men when moving crane equipment.

5.	Roof Operations

a.	SNL roof work permits may be required. The Contractor shall check with the SDR or the Construction Inspector/Observer concerning this requirement.

b.	Provide secured ladders at all times, extended a minimum of three (3) feet above roof line.

c.	Provide railing or other equivalent protection at all roof openings.

d.	The Contractor shall conform to 29 CFR 1926.500 section (g) during the performance of all work on low pitched or flat roofs with a ground to eave height greater than 16 feet using safety lines and/or safety observers.

6.	Plumbing:  In some instances the Contractor may be required to furnish approriate certified back vlow prevention devices.

a.	Contractor will protect all potable water supplies.

b.	It is the Contractors responsibility, when hooking up to SNL potable water systems, to prevent backflow and back-siphonage of non-potable substances.  In some instances the Contractor may be required to furnish appropriate back-flow prevention devices.  The Contractor shall check with the SDR or the Construction Inspector/Observer concerning these requirements prior to hooking up to any SNL potable water system.

c.	Provide excavation shoring, sloping or benching when required.

d.	Inspect area adjacent to cutting, welding or lead pours.

e.	A burn permit may be required.

f.	A digging permit may be required.

g.	All potable water line disinfection is to be done per current American Water Works Association (AWWA) standards.

7.	Electrical:  The Contractor shall remain in compliance with current NEC provisions and shall provide listed ground-fault circuit interrupter protection for all 120-volt, single phase, 15 and 20 ampere receptacle outlets on construction-sites which are not a part of the permanent wiring of the building or structure and which are in use by employees. Receptacles on the ends of listed extension cords are not part of the permanent wiring and therefore must be protected by ground-fault circuit interrupter whether or not the listed extension cord is plugged into permanent wiring(No-job made extension cords.)

8.	Ramps and Runways

a.	Construct as flat as possible.

b.	Provide cleats for inclines greater than 1 to 5 slope.

c.	Provide sufficient width to accommodate workmen and materials delivery.

d.	Design and brace to accommodate safe project usage.

e.	Where required, the Contractor will provide handrails, midrails, and toe boards.

9.	Traffic Control

a.	Keep access roads clear of vehicles and materials.

b.	Locate, mark and protect utilities to prevent damage.

c.	Obtain authorization and clearance from using service and contracting agencies for any utility cuts in existing roads.

d.	Provide vehicle parking for workmen.

e.	Provide flagmen when required.

10.	Safety Inspections

a.	The general superintendent or his designee shall make daily inspections of construction work areas and document these inspections.  This documentation shall be documented and readily available for each job site and shall be included in the weekly report.

b.	The project or craft foreman is responsible for constant surveillance for safety hazards and safety practices.

11.	Procedures for Rectifying Safety Deficiencies

a.	All personnel on the job site shall be notified immediately when unsafe conditions or equipment are discovered that affect their work.

b.	The general superintendent or his designee and the project foreman shall oversee the correction of any safety deficiency.

12.	Fence Penetrations

a.	No contractor shall make any penetrations over, under or through existing security fences, barricades, wall or roofs located within or on the perimeter of any security area with out the permission of Sandia Security and the SDR.

13.	Other Work Requiring Additional Planning/Documentation

a.	The Contractor will be required to provide the SDR with detailed information concerning safety measures to be incorporated in:

i.	Scaffolding Operations

ii.	Trenching / Shoring operations

iii.	Other high hazard operations as determined by Sandia

14.	Requirements for use of instruments containing licensable Quantities of nuclear materials:  Whenever instruments containing licensable quantities of nuclear materials (source materials) are brought onto SNL property as a minimum the following information must be available on site with the instrument.

a.	A copy of the latest license documents from the State of New Mexico or other licensing agency. These documents shall contain a description of the nuclear source including its radionucleide constituents and their power.

b.	A copy of the latest instrument radiological background survey results.

c.	A copy of the training certification, including required radiation safety training, for the technician(s) that will be operating the instrument on SNL property.

d.	A copy of the contractor's safety requirements for use of the instrument and emergency procedures should the integrity of the instrument be compromised.

1.17  CONSTRUCTION VEHICLE & HEAVY EQUIPMENT SAFETY REQUIREMENTS

A.	Mobile Cranes and Personnel Hoisting Devices

1.	The Contractor shall give the SDR a 48-hour notice prior to using mobile cranes or personnel hoisting devices on SNL construction sites.  The 48-hour notice provides time necessary for SNL personnel or their designated representatives to schedule and conduct inspections of the equipment prior to their use on the job sites.

2.	Inspections will be conducted according to the standards and requirements outlined in OSHA 29 CFR 1926.550, .251, .600, .601 and ANSI B30.5b-1991 and B30.9.  In addition, annual load test certificates are required for cranes and personnel hoisting devices.

3.	All deficiencies noted during inspections must be corrected before the equipment can be placed into service.  Any structural repair made to equipment must be done according to manufacturer's specifications and the supporting documentation shall be readily available upon request.

4.	Crane operators shall be properly trained and experienced on operation of equipment.

5.	Records will be kept of daily crane checks by the crane operator.

6.	Maintain written documentation of crane inspections, preventative maintenance procedures, and test records at the job site during the entire period the crane or hoist is on the job site.

B.	Construction Vehicles and Heavy Equipment:  All construction vehicles and equipment being stored, awaiting use or in use on SNL property shall be in a serviceable and safe operating condition.  Any defective or unsafe equipment shall be repaired immediately or removed from SNL property until proper repairs are completed.  All idle equipment awaiting safety or non-safety related maintenance or repairs will be tagged and removed from service. The maintenance or repairs will be completed within a reasonable time frame or they will be removed from SNL property until properly maintained or repaired.  These requirements apply to all vehicles and equipment used or intended for use on SNL construction projects or on associated SNL property.  Only vehicles with pneumatic/solid tires will be allowed on existing paved roads unless otherwise approved by the SDR.

ATTACHMENTS:

A:	Contractor/Visitor Report of Occupational Occurrences

B:	Sample of Standard Safety Bulletin Board

C:	Satellite Waste Accumulation Site Requirements

D:	Confined Space Entry Permit and Guidance

END OF SECTION