### ITEM D-705   PIPE UNDERDRAINS FOR AIRPORTS

DESCRIPTION

705-1.1  This item shall consist of the construction of pipe drains in accordance with these specifications and in reasonably close conformity with the lines and grades shown on the plans.

MATERIALS

705-2.1  GENERAL.  Materials shall meet the requirements shown on the plans and specified below.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

The Engineer should indicate the required class, schedule, SDR, gage, and/or strength of pipe desired.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

705-2.2  PIPE.  The pipe shall be of the type called for on the plans or in the proposal and shall be in accordance with the following appropriate requirements.

Perforated Concrete Pipe 	ASTM C 444

Porous Concrete Pipe 	ASTM C 654

Polymer Precoated Perforated Corrugated Steel Pipe	ASTM A 762

Perforated Corrugated Aluminum Alloy Pipe	AASHTO M 196

Smooth-Wall Perforated PVC Pipe 	ASTM F 758

Poly (Vinyl Chloride) Ribbed Drain Pipe & Fittings

Based on Controlled Inside Diameter	ASTM F 794

Poly (Vinyl Chloride)(PVC) Corrugated Sewer

Pipe With a Smooth Interior and Fittings	ASTM F 949

Perforated Corrugated Steel Pipe 	ASTM A 760

Bituminous-Coated Perforated Corrugated	AASHTO M 196

Aluminum Alloy Pipe	  and M 190

Corrugated Polyethylene Drainage Tubing (all types)	AASHTO M 252

Corrugated Polyethylene Pipe, 300 to 1200 mm Diameter (all types)	AASHTO M 294M

Poly (Vinyl Chloride) (PVC) Profile Wall Drain Pipe  and 	AASHTO M 304

Fittings Based on Controlled Inside Diameter

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

The Engineer shall select the pipe used for the project and may delete inappropriate requirements from paragraph 705-2.2 and from the list of material requirements.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

705-2.3  JOINT MORTAR.  Pipe joint mortar shall consist of one part portland cement and two parts sand.  The portland cement shall conform to the requirements of ASTM C 150, Type I.  The sand shall conform to the requirements of ASTM C 144.

705-2.4  ELASTOMERIC SEALS.  Elastomeric seals shall conform to the requirements of ASTM F 477.

705-2.5  POROUS BACKFILL.  Porous backfill shall be free of clay, humus, or other objectionable matter, and shall conform to the gradation in Table 1 when tested in accordance with ASTM C 136.

| TABLE 1. GRADATION OF POROUS BACKFILL |
| --- |
| Sieve Designation (square openings) | Percentage by Weight Passing Sieves |
|  | Porous Material No. 1 | Porous Material No. 2 |
| 1-1/2 inch (38 mm) |  | 100 |
| 1 inch (25 mm) |  | 90 - 100 |
| 3/8 inch (9.5 mm) | 100 | 25 - 60 |
| No. 4 (4.75 mm) | 95 – 100 | 5 - 40 |
| No. 8 (2.36 mm) |  | 0 - 20 |
| No. 16 (1.18 mm) | 45 – 80 |  |
| No. 50 (0.30 mm) | 10 – 30 |  |
| No. 100 (0.15 mm) | 0 – 10 |  |

When two courses of porous backfill are specified in the plans, the finer of the materials shall conform to particle size tabulated herein for porous material No. 1.  The coarser granular material shall meet the gradation given in the tabulation for porous material No. 2.

705-2.6.  GRANULAR MATERIAL.  Granular material used for backfilling shall conform to the requirements of ASTM D 2321 for Class IA, IB, or II materials, or shall meet the requirements of AASHTO Standard Specification for Highway Bridges Section 30.

705-2.7.  FILTER FABRIC.  The filter fabric shall conform to the requirements of AASHTO M 288-99, Class 2.

| TABLE 2 |
| --- |
| Fabric Property | Test Method | Test Requirement |
| Grab Tensile Strength, lbs | ASTM D 4632 | 125 min |
| Grab Tensile Elongation % | ASTM D 4632 | 50 min |
| Burst Strength, psi | ASTM D 3785 | 125 min |
| Trapezoid Tear Strength, lbs | ASTM D 4533 | 55 min |
| Puncture Strength, lbs | ASTM D 4833 | 40 min |
| Abrasion, lbs | ASTM D 4886 | 15 max loss |
| Equivalent Opening Size | ASTM D 4751 | 70-100 |
| Permittivity sec-1 | ASTM D 4491 | 0.80 |
| Accelerated Weathering | ASTM D 4355 | 70 |
|  | (UV Stability) | *(500 hrs exposure) |  |
|  | (Strength Retained - %) |  |  |

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

The Engineer shall specify Class 2 unless sufficient survivability information is available for a reduction in minimum property requirements.  Permittivity and Apparent Opening Size requirements shall be based on knowledge of in situ soil.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

705-2.8.  CONTROLLED LOW STRENGTH MATERIAL (CLSM).   Controlled low strength material shall conform to the requirements of Item P-153.  When CLSM is used all joints shall have elastomeric seals.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

Specification Item P-153 Controlled Low Strength Material (CLSM)contains guidance for use of CLSM.  The locations where CLSM is permitted shall be shown on the plans.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

CONSTRUCTION METHODS

705-3.1  EQUIPMENT.  All equipment necessary and required for the proper construction of pipe underdrains shall be on the project, in first-class working condition, and approved by the Engineer before construction is permitted to start.

705-3.2  EXCAVATION.  The width of the pipe trench shall be sufficient to permit satisfactory jointing of the pipe and thorough tamping of the bedding material under and around the pipe, but shall not be less than the external diameter of the pipe plus 6 inches (150 mm) on each side.  The trench walls shall be approximately vertical.

Where rock, hardpan, or other unyielding material is encountered, it shall be removed below the foundation grade for a depth of at least 4 inches (100 mm).  The excavation below grade shall be backfilled with selected fine compressible material, such as silty clay or loam, and lightly compacted in layers not over 6 inches (150 mm) in uncompacted depth to form a uniform but yielding foundation.

Where a firm foundation is not encountered at the grade established, due to soft, spongy, or other unstable soil, the unstable soil shall be removed and replaced with approved granular material for the full trench width.  The Engineer shall determined the depth of removal necessary.  The granular material shall be compacted to provide adequate support for the pipe.

Excavated material not required or acceptable for backfill shall be disposed of by the Contractor as directed by the Engineer.  The excavation shall not be carried below the required depth; when this is done, the trench shall be backfilled at the Contractor's expense with material approved by the Engineer and compacted to the density of the surrounding earth material.

The bed for the pipe shall be so shaped that at least the lower quarter of the pipe shall be in continuous contact with the bottom of the trench.  Spaces for the pipe bell shall be excavated accurately to size to clear the bell so that the barrel supports the entire weight of the pipe.

The Contractor shall do such trench bracing, sheathing, or shoring necessary to perform and protect the excavation as required for safety and conformance to governing laws.  Unless otherwise provided, the bracing, sheathing, or shoring shall be removed by the Contractor after the completion of the backfill to at least 12 inches (300 mm) over the top of the pipe.  The sheathing or shoring shall be pulled as the granular backfill is placed and compacted to avoid any unfilled spaces between the trench wall and the backfill material.  The cost of bracing, sheathing, or shoring, and the removal of same, shall be included in the unit price bid per foot (meter) for the pipe.

705-3.3  LAYING AND INSTALLING PIPE.

a.  Concrete Pipe.  The laying of the pipe in the finished trench shall be started at the lowest point and laid upgrade.  When bell and spigot pipe is used, the bells shall be laid upgrade.  If tongue and groove pipe is used, the groove end shall be laid upgrade.  Holes in perforated pipe shall be placed down, unless otherwise shown on the plans.  The pipe shall be firmly and accurately set to line and grade so that the invert will be smooth and uniform.  Pipe shall not be laid on frozen ground.

Pipe which is not true in alignment, or which shows any settlement after laying, shall be taken up and relaid without extra compensation.

b.  Metal Pipe.  The metal pipe shall be laid with the separate sections joined firmly together with bands, with outside laps of circumferential joints pointing upgrade, and with longitudinal laps on the sides.  Any metal in the pipe or bands that is not protected thoroughly by galvanizing shall be coated with a suitable asphaltum paint.

During installation, the asphalt-protected pipe shall be handled without damaging the asphalt coating.  Any breaks in the bitumen or treatment of the pipe shall be refilled with the type and kind of bitumen used in coating the pipe originally.

c.  PVC or Polyethylene Pipe.  PVC or polyethylene pipe shall be installed in accordance with the requirements of ASTM D 2321 or AASHTO Standard Specification for Highway Bridges Section 30.  Perforations shall meet the requirements of AASHTO M 252 or M 294 Class 2, unless otherwise indicated on the plans.  The pipe shall be laid accurately to line and grade.

d.  All Types of Pipe.  The upgrade end of pipelines, not terminating in a structure, shall be plugged or capped as approved by the Engineer.

Unless otherwise shown on the plans, a 4-inch (100 mm) bed of granular backfill material shall be spread in the bottom of the trench throughout the entire length under all perforated pipe underdrains.

Pipe outlets for the underdrains shall be constructed when required or shown on the plans.  The pipe shall be laid with tight-fitting joints.  Porous backfill is not required around or over pipe outlets for underdrains.  All connections to other drainage pipes or structures shall be made as required and in a satisfactory manner.  If connections are not made to other pipes or structures, the outlets shall be protected and constructed as shown on the plans.

e.  Filter Fabric.  The filter fabric shall be installed in accordance with the manufacturer's recommendations, or in accordance with AASHTO M 288-99 APPENDIX, unless otherwise shown on the plans.

705-3.4  MORTAR.  The mortar shall be of the desired consistency for caulking and filling the joints of the pipe and for making connections to other pipes or to structures.  Mortar that is not used within 45 minutes after water has been added shall be discarded.  Retempering of mortar shall not be permitted.

705-3.5  JOINTS IN CONCRETE PIPE.  When open or partly open joints are required or specified, they shall be constructed as indicated on the plans.  The pipe shall be laid with the ends fitted together as designed.  If bell and spigot pipe is used, mortar shall be placed along the inside bottom quarter of the bell to center the following section of pipe.

The open or partly open joints shall be surrounded with granular material meeting requirements of porous backfill No. 2 or as indicated on the plans.  This backfill shall be placed so its thickness will be not less than 3 inches (75 mm) nor more than 6 inches (150 mm), unless otherwise shown on the plans.

When the original material excavated from the trench is impervious, commercial concrete sand or granular material meeting requirements of porous backfill No. 1 shall surround porous backfill No. 2, as shown on the plans or as directed by the Engineer.

When the original material excavated from the trench is pervious and suitable, it may be used as backfill in lieu of porous backfill No. 1, when indicated on the plans or as directed by the Engineer.

705-3.6  BACKFILLING.

a.  Earth.  All trenches and excavations shall be backfilled within a reasonable time after the pipes are installed, unless other protection of the pipe is directed.  The backfill material shall be selected material from excavation or borrow; material which is placed within a nominal pipe diameter distance at the sides of the pipe and 1 foot (30 cm) over the top shall be material that can be readily compacted.  It shall not contain stones retained on a 3-inch (75 mm) sieve, frozen lumps, chunks of highly plastic clay, or any other material that is objectionable to the Engineer.  The material shall be moistened or dried, if necessary to be compacted by the method in use.  Backfill material shall be approved by the Engineer.  Special care shall be taken in placing the backfill.  Great care shall be used to obtain thorough compaction under the haunches and along the sides to the top of the pipe.

The backfill shall be placed in loose layers not exceeding 6 inches (150 mm) in depth under and around the pipe, and not exceeding 8 inches (200 mm) over the pipe.  Successive layers shall be added and thoroughly compacted by hand and pneumatic tampers, approved by the Engineer, until the trench is completely filled and brought to the proper elevation.  Backfilling shall be done in a manner to avoid injurious top or side pressures on the pipe.

In embankments and for other areas outside of pavements, the backfill shall be compacted to the density required for embankments in unpaved areas under Item P-152.  Under paved areas, the subgrade and any backfill shall be compacted to the density required for embankments for paved areas under Item P-152.

b.  Granular Material.  When granular backfill is required, its placement in the trench and about the pipe shall be as shown on the plans.  Special care shall be taken in placing the backfill.  The granular backfill shall not contain a damaging amount of foreign matter, nor shall earth from the sides of the trench or from the windrow be allowed to filter into the backfill.  When required by the Engineer, a template shall be used to properly place and keep separate the two sizes of backfill.  The backfill shall be placed in loose layers not exceeding 6 inches (150 mm) in depth and compacted by hand and pneumatic tampers to the requirements as given for earth backfill.  Backfilling shall be done in a manner to avoid injurious top or side pressure on the pipe.  The granular backfill shall be made to the elevation of the trench, as shown on the plans.

When perforated pipe is specified, granular backfill material shall be placed along the full length of the pipe.  The position of the granular material shall be as shown on the plans.  If the original material excavated from the trench is pervious and suitable, it shall be used in lieu of porous backfill No. 1.

When porous backfill is to be placed in paved or adjacent areas prior to the completion of grading or subgrade operations, the backfill material shall be placed immediately after laying the pipe.  The depth of this granular backfill shall be not less than 12 inches (300 mm), measured from the top of the underdrain.  During subsequent construction operations, this minimum backfill of 12 inches (300 mm) of depth shall not be disturbed until such time as the underdrains are to be completed.  When the underdrains are to be completed, the unsuitable material shall be removed until the porous backfill is exposed.  That part of the porous backfill that contains objectionable material shall be removed and replaced with suitable material.  The cost of removing and replacing any such unsuitable material shall be borne by the Contractor.

Whenever a granular subbase blanket course is to be used under pavements which extends several feet beyond the edge of paving to the outside edge of the underdrain trench, the granular backfill material over the underdrains shall be placed in the trench up to an elevation of 2 inches (50 mm) above the bottom surface of the granular subbase blanket course.  Immediately prior to the placing of the granular subbase blanket course, the Contractor shall blade this excess trench backfill from the top of the trench onto the adjacent subgrade where it can be incorporated into the granular subbase blanket course.  Any unsuitable material that remains over the underdrain trench shall be removed and replaced.  The subbase material shall be placed to provide clean contact between the subbase material and the underdrain granular backfill material for the full width of the underdrain trench.

c.  Controlled Low Strength Material (CLSM).  Controlled low strength material shall conform to the requirements of Item P-153.

d.  Deflection Testing.  The Engineer may at any time, not withstanding previous material acceptance, reject or require re-installation of pipe that exceeds 5 percent deflection when measured in accordance with ASTM D 2321, including Appendices.

705-3.7  CONNECTIONS.  When the plans call for connections to existing or proposed pipe or structures, these connections shall be watertight and made so that a smooth uniform flow line will be obtained throughout the drainage system.

705-3.8  CLEANING AND RESTORATION OF SITE.  After the backfill is completed, the Contractor shall dispose of all surplus material, dirt, and rubbish from the site.  Surplus dirt may be deposited in embankments, shoulders, or as ordered by the Engineer.  Except for paved areas of the airport, the Contractor shall restore all disturbed areas to their original condition.

METHOD OF MEASUREMENT

705-4.1  The length of pipe to be paid for shall be the number of linear feet (meters) of pipe underdrains in place, completed, and approved; measured along the centerline of the pipe from end or inside face of structure to the end or inside face of structure, whichever is applicable.  The several classes, types, and sizes shall be measured separately.  All fittings shall be included in the footage as typical pipe sections in the pipeline being measured.

705-4.2  The quantity of porous backfill to be paid for shall be the number of cubic yards (cubic meters) of porous backfill No. 1 and No. 2, complete in place and accepted, and shall be determined from the dimensions given on the plans by typical trench sections indicating the placement of porous backfill or dimensions ordered by the Engineer.

705-4.3  The quantity of filter fabric to be paid for shall be the number of square yards (square meters) of filter fabric in place, completed, and approved; and shall be determined from the dimensions given on the plans by typical trench sections indicating the placement of filter fabric or dimensions ordered by the Engineer.

BASIS OF PAYMENT

705-5.1  Payment will be made at the contract unit price per linear foot (meter) for pipe underdrains of the type, class, and size designated; at the contract unit price [per cubic yard (cubic meter)][per ton (metric ton)] for porous backfill No.1; the contract unit price [per cubic yard (cubic meter)][per ton (metric ton)] for porous backfill No. 2, and at the contract unit price per square yard (square meter) for filter fabric. [per linear foot (meter) COMPLETE (including porous backfill and filter fabric.]  These prices shall be full compensation for furnishing all materials and for all preparation, excavation, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete the item.

Payment will be made under:

Item D-705-5.1		[    ] inch pipe (mm pipe) [    ] per linear foot (meter)

Item D-705-5.2		Porous Backfill No. 1—[per cubic yard (cubic meter)][per ton (metric ton)]

Item D-705-5.3		Porous Backfill No. 2—[per cubic yard (cubic meter)][per ton (metric ton)]

Item D-705-5.4		Filter Fabric—per square yard (square meter)

[Item D-705-5.5		[    ] inch pipe (mm pipe) [    ] per linear foot (meter) COMPLETE (including porous backfill and filter fabric]

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

The Engineer shall specify the size and type of pipe, filter fabric, and backfill material for each pipe size and type specified in the plans.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

MATERIAL REQUIREMENTS

|  | ASTM A 760 | Corrugated Steel Pipe, Metallic-Coated for Sewers and Drains |
| --- | --- | --- |
|  | ASTM A 762 | Corrugated Steel Pipe, Polymer Precoated for Sewers and Drains |
|  | ASTM C 136 | Sieve Analysis of Fine and Coarse Aggregates |
|  | ASTM C 144 | Aggregate for Masonry Mortar |
|  | ASTM C 150 | Portland Cement |
|  | ASTM C 444 | Perforated Concrete Pipe |
|  | ASTM C 654 | Porous Concrete Pipe |
|  | ASTM D 2321 | Underground Installation of Thermoplastic Pipe for Sewers and Other Gravity-Flow Applications |
|  | ASTM D 3034 | Type PSM Poly(Vinyl Chloride) (PVC) Sewer Pipe and Fittings |
|  | ASTM F 477 | Elastomeric Seals (Gaskets) for Joining Plastic Pipe |
|  | ASTM F 758 | Smooth-Wall Poly(Vinyl Chloride) (PVC) Plastic Underdrain Systems for Highway, Airport, and Similar Drainage |
|  | ASTM F 794 | Poly (Vinyl Chloride) Ribbed Drain Pipe & Fittings Based on Controlled Inside Diameter |
|  | ASTM F 949 | Poly (Vinyl Chloride)(PVC) Corrugated Sewer Pipe with a Smooth Interior and Fittings |
|  | AASHTO M 190 | Bituminous Coated Corrugated Metal Culvert Pipe and Pipe Arches |
|  | AASHTO M 196 | Corrugated Aluminum Alloy Culverts and Underdrains |
|  | AASHTO M 252 | Corrugated Polyethylene Drainage Tubing |
|  | AASHTO M 288-99 | Geotextile Specification for Highway Applications |
|  | AASHTO M 294M | Corrugated Polyethylene Pipe, 300 to 1200 mm Diameter |
|  | AASHTO M 304 | Poly (Vinyl Chloride) (PVC) Profile Wall Drain Pipe and Fittings Based on Controlled Inside Diameter |
|  | AASHTO | Standard Specifications for Highway Bridges |

END OF ITEM D-705

Intentionally Left Blank