RESPONSE TO COMMENTS

National Weather Service River and Weather Forecast Office, Portland Oregon and

Remote Data Acquisition Site, Washington County, Oregon

I.	Comments from Minh Trinh

NWS - Remote Data Acquisition Site in Washington County of Oregon.

Part IV, Subpart B, Paragraph 1.  Is tightness testing every 3 years necessary?  What is the manufacturers recommendation?  I think the testing is too conservative.  The tightness testing should be done only if the structure integrity of the system is compromised by either mechanical joint breaching due to repairs, corrosion, and/or sign of cracking.  I would like to see your rebuttal.

The recommendation for tightness testing has been removed.  The interstitial monitoring devices should signal a problem with the integrity of the primary tank.  Visual inspections of the outside of the secondary tank for cracks or leaks or other anomalies should serve to signal a potential problem with its integrity.  If a problem is suspected with either tank, tightness testing should be initiated soon after discovery.

Part IV, Subpart B, Paragraph 2.  Who specifically needs the training?  “Facility personnel” is a vague body.  If they are the “Responsible Manager” and the “Spill Prevention Representative”, then let’s spell it out.  It does not to define these titles.  Is there any OSHA training for conducting countermeasures (e.g., use of spill cleanup kits)

All personnel who are responsible for supervising the filling of the tank and who are responsible for the inspection, maintenance, and operation of the emergency backup power system (tank, piping, alarms, and generator) are required to have training.  Part II.A.5 has been revised to clarify this issue.

Appendix B.  Being a remote site, how often do we go up there?  Is monthly inspection practical?

According to National Weather Service (NWS) personnel at the Portland Weather Forecast Office and River Forecast Center (WFO/RFC), technicians are at the Remote Data Acquisition (RDA) site on a routine basis at least once a week, and more often if there are issues that need resolution.

Appendix B, Tank Inspection.  Should add a visual check of the tank exterior for cracks.

This has been added to the checklist.

General.  Should date all pages (as a footer) to reflect the proper version of SPCC plan.

The final version will have the date on all page footers.

General.  Please ensure the SPCC plan is printed double-side where possible.

The final versions of all Spill Prevention, Control, and Countermeasure(SPCC) plans have been printed double-sided

Do we have a date of initial operation?

The date of initial operation is March of 1995 and is in Part I, paragraph 3.

General.  From your description, it is remotely likely that a spill from this site could reach US navigate-able water.  Thus an SPCC plan is not required.  However, that does not mean we shouldn’t have a spill response plan in place.  I think what you’ve developed is a good precautionary measure.  But what worries me is the commitment to the formal SPCC requirements once we finalize the plan.   This is a resource intensive commitment and I don’t know if it’s something that NWS is willing to accept.  What’s your recommendations for this site that could preserve/promote the precautionary measure to prevent and control spills but at the same time would not sign us up to the rigorous requirements of SPCC regulations.

The RDA site is not located adjacent to navigable water or waters of the U.S. and there are no storm drains that may directly convey spilled fuel to these waters.   If this site was located in a drier climate, I would tend to agree that it could not reasonably be expected to impact navigable waters or waters of the U.S. The site, however, is located in the hills west of Portland, Oregon that gets relatively large amounts of precipitation (there were 4 inches of snow when we did the inspection).  The U.S. Geological Survey (USGS) topographic map of the area shows a tributary to McKay Creek about 1/4 to 1/2 mile from the site.  My contact at the U.S. Environmental Protection Agency (U.S. EPA) Region 10 on a "hypothetical site" like this one, told me that they assume (under a worst case scenario) that the ground is frozen and the fuel would runoff down the access road into the ditches along the main road.  If it then warmed up and rained heavily (again worst case scenario) the fuel could be washed from the ditches to tributaries to McKay Creek, too small to show up on the USGS map.

I agree that committing NWS to the full SPCC requirements at sites where there is serious doubt regarding affecting navigable waters or water of the U.S. is a bad idea.  For remote sites in drier climates like Salt lake City and other areas, we will make a judgment on a site by site basis whether there is a threat to navigable waters or waters of the U.S.  This likely can only be done after looking at the facility.  Therefore, there may be some sites where we visit a site but not prepare a formal SPCC plan.  For these sites, I would recommend that they use the inspection checklists (to minimize spills from worn equipment) and a refueling checklist with training (to minimize spills during refueling).

NW Weather Forecast & River Forecast Center

Comments number 1, 2, 5, and 6 of the RDA SPCC plan in Washington County apply.

See responses to comments 1,2,5, and 6, above.

Should have a refueling checklist develop to ensure the following:  1) the catch basin drain valve is shut prior to fuel transfer, 2) if the tank automatic shut-off valve is removed, then ensure the fuel supplier is using the self shut-off nozzle (similar to the one used at gas station), 3) ensure sufficient spill response materials are sufficiently stocked for potential spill, 4) ensure power to high level alarm is on, and 5) the catch basin drain valve is re-positioned open after refueling operation.

Part II.A.2 (renamed Tank Truck Unloading Operations) in the final version contains a step-by-step procedure for preventing spills during refueling. This includes requiring the presence of a NWS employee at all times during the procedure.  A checklist outlining these procedures has been added to Appendix A.

Might consider enlisting a contractor to call upon for assistance in a spill situation.  Someone who is capable of handling a 2000-gal spill and familiar with Oregon environmental regulations in both areas of spill response and petroleum soil contamination.

The names and telephone numbers of 3 spill response contractors have been received from Brian Alley and have been incorporated in the final version in Part III.B.5.

II.	Comments from Robert Kinsinger

SPCC for WFO

Page 6 - Spill Reporting:  Change the name from Neil Lutz to Bob Kinsinger, same phone number, but ext 223.

This change has been made and included in the final version.

Page 7:  Please provide the name and phone number of at least 1 (2 preferred) emergency response contractors whom the Portland Office could call to assist with clean-up.  Brian Alley at Portland may be able to assist you with some info he already has.

See response to comment 11.

Page 8:  For my info only, could you provide the names and part numbers of urethane spill barriers you mention?

One of the suppliers we have used is called “New Pig” (www.newpig.com or 1-800-468-4647).  The model PLR230 is a urethane spill barrier, triangular in cross-section, 2-1/4 inches high and 10 feet long.  This supplier also sells urethane mats for covering catch basin inlets which may prove to be useful.

Appendix C:  Could a copy of Title 40 CFR Part 112 be incorporated into the SPCC as another appendix section?  It would be most useful for each office to have a copy of such.

A copy of the regulations has been included in the final version after Appendix C, Training Outline.

SPCC for RDA

Page 6 - Spill Reporting:  Change the name from Neil Lutz to Bob Kinsinger, same phone number, but ext 223.

See response to comment 12.

Page 7:  Please provide the name and phone number of at least 1 (2 preferred) emergency response contractors whom the Portland Office could call to assist with clean-up.

See response to comment 13.

Appendix C:  Could a copy of Title 40 CFR Part 112 be incorporated into the SPCC as another appendix section?  It would be most useful for each office to have a copy of such.

See response to comment 15.

Page 9, Table 1:  Typo - "grater" should be "greater".

This correction has been made in the final version.

Also when the final versions are ready, please be sure to send one copy of each to me at the Region HQ in Salt Lake City as well as to the offices.

Five copies of the final version will be produced one each for: the person at the facility responsible for spill prevention (Brian Alley), the responsible manager (Steve Todd), the Contracting Officers Technical Representative (COTR-Minh Trinh), the NWS Regional Environmental/Safety Coordinator (Robert Kinsinger), and the NWS Environmental Compliance Officer (Mike Jacob).

III.	Comments From Yelena Platt

Part I:  Page 1.  Replace “Area Safety Representative” with “Environmental/Safety Focal Point”

According to Brian Alley, “Area Safety Representative” is his title.

Part I, Section B(1), first paragraph - remove “one” before “tank” in the last sentence.

This change has been made in the final version.

Part III, Section B: Add NWS Safety Officer, Olga Kebis (301) 713-1838 ext 173 and NWS Environmental Compliance Officer, Mike Jacob (301) 713-1838 ext 165

This change has been made in the final version.

Part III, Section B: Add National Response Center 1-800 number.

This change has been made in the final version.

Part III, Section B: First sentence states that all oil spills are to be reported.  Later, the instructions are given on how to report all significant spills.  It is not clear, what quantity of spill should require reporting and to whom.   What is “threatened” release?  Does EPA need to be notified and under which circumstances?  A name and phone number of the local emergency response contractor needs to be included

Part III.B has been revised to provide instructions on whom to notify and when.  It should be noted that Title 40 CFR Part (entitled “Oil Pollution Prevention”) does not require that immediate spill notification information be in SPCC plans, since these plans are primarily designed to prevent spills.  In regards to notification, the SPCC regulations only require that EPA be notified within 60 days if either of the following occurs:

- A discharge of more than 1,000 gallons of oil into or upon navigable waters or adjoining shore lines in a single event, or

- Two spill events that cause visible sheens upon navigable waters or adjoining shore lines within any 12-month period

However, Title 40 CFR Part 110.6 (Discharge of Oil-Notice) requires the National Response Center (or the U.S. Coast Guard) be notified as soon as anyone has knowledge of any discharges of oil in quantities that “may be harmful.” Title 40 CFR Part 110.3 defines “may be harmful” as:

- Violates applicable water quality standards; or

- Causes a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or cause a sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines

The requirement to notify the National Response Center is usually put in SPCC plans for convenience.  Detailed internal procedures for responding to spills are beyond the scope of this SPCC plan.

Part IV, Section B(1): Regulations do not require tightness testing every 3 years.

See response to comment number 1.

In some places, SPCC plans are written as audit reports: deficiencies were observed and documented and corrective actions were recommended.  The style of presentation could be modified.  Recommendations may be included as a separate attachment.

The style of the text has been made more consistent with a “plan.”  Recommendations have been moved to the cover letter.

IV	Comments From Olga Kebis

Page iii, Management Approval:  Second paragraph states that reporting to EPA should be done when single event occurs or when two spill events in harmful quantities occur within 12 months.  This paragraph could be moved to Part III, Section B, Spill Reporting, unless it is required to be on a signature page.  Harmful quantities should be defined or an excerpt from regulations (Title 40 CFR 110) shall be added to the plan as an attachment.

The Management Approval Page and Part II.B have been revised to clarify these issues.

Part I, Section B(1), first paragraph:  Check the size of an emergency generator.  I believe it should be 150 kW instead of 1,500 kW.

According to Tom Page, NWS Salt Lake City, the generator is rated at 300 kW.  This change has been made in the text.

Part I, item 6: The phone number shown here is the number during business hours.  I believe that MIC is on 24-hour call (or may be other designated personnel).  Therefore, I suggest to include an alternative phone number that allows to reach somebody after regular duty hours.

After business hours, the same number is called, then extension zero is keyed in at the prompt.  The caller is then routed through to someone actively working at the facility.  This information has been included in the final version.  This information has been added to Part I, Paragraph 6.

Part I, item 2:  River and weather forecast office - start with capital letters

Part I.A.1 has the name of the facility beginning with capital letters.  Item 2 merely describes what they do at the facility and is not a name.

Part II, Section A(1):  The fuel oil tank, piping, valves and associated alarm system diagram shall be part of this plan.  The plan calls for training on tank monitoring system, however, we do not even know the parts of the system.  The requirement is also part of SOW.

The example SPCC format in the SOW was taken from a plan Tetra Tech prepared for the National Marine Fisheries Service (NMFS) in Little Port Walter, Alaska.  This site had multiple storage tanks and day tanks and the piping diagram was necessary for clear presentation of the operation of the facility.  The information in the piping diagram was provided to Tetra Tech from NMFS and was redrafted to include some updates.  If the NWS has similar diagrams, they can be incorporated into these plans to assist in the required training.

Part II, Section A(2):  The bulk transfer operations shall be described in a bullet format as a checklist.  Add a bullet stating that any oil spilled in the spill box should be cleaned up immediately.

See response to comment 10.  A bullet that includes cleaning up oil in the spill box has been added.

Part II, Section B(1):  Word “elements” should be replaced with more appropriate word.

The word has been removed.

Part III, Section B: It is done very poorly.  This section should describe what to do in case of small and big spills (e.g., to call fire department, 911 or clean up company first).  It looks like bullet No. 1 is out of place.  It also should describe what to do with used absorbent material.

See response to comment 25.  Proper disposal of used absorbent is beyond the scope of an SPCC plan.  I recommend calling the local garbage collection contractor to see if, and how much, they will accept.  The spill cleanup contactors listed in the final plan can also help on this issue.

Part III, Section B:  The first paragraph should state: “...all oil spills that result from facility operations to NWS/NOAA representatives and to local, State, and Federal agencies if applicable.”  Local Emergency Commission is not mentioned in the plan.  Have reporting procedures been checked with local authorities?

See response to comment 25.  The Oregon Emergency Management (OEM) Division listed in the plan is the local emergency commission.  Under the Federal Emergency Planning and Community Right-to Know Act (EPCRA), the OEM should know that the facility is storing more than 10,000 pounds of number two diesel (approximately 1,450 gallons).   The local fire department should also be aware of the fuel storage at the facility.  These notifications are beyond the scope of an SPCC plan.

Appendix D: Is this a standard State of Oregon form?  If not, we would like to add additional box - NOAA/NWS points of contact.   A note should be added somewhere in the document that copies of spill reporting forms must be sent to NOAA RECO and NWS Environmental Compliance Officer.

This is not a State of Oregon form but one Tetra Tech developed to do the notifications.  The NOAA/NWS points of contact have been added.  A note has been added in the plans and to the form specifying that copies of the forms must be sent to the NOAA RECO and NWS Environmental Compliance Officer.

V.	Comments From Jeff Walker

Comments to SPCC Plan for NWS RDA Site, Washington County, Oregon

Table 2, Potential Spill Sources and Volumes does not include a scenario for a leak or break in the overhead piping between the Convault tank and generator building.  Is this a valid scenario?

The likelihood of a break in the overhead piping appears to be low and it is secondarily contained in another pipe.  This has been described in the final version.

Are there any scenarios in which the generator room pump could keep operating after a leak or rupture develops and drain the entire Convault tank?

Table 2 has been revised to include a scenario when a line fails and the pump drains the entire tank.

In Part II.A.1, the explanation of the 10-gallon spill box is confusing.  Does the spill box drain to the primary tank or drain the primary tank?  Also, why isn’t the generator tank considered in the plan?

The explanation regarding the spill box has been clarified.  The generator is fed directly from the day tanks.  The 1,000-gallon tank that is referred to as the “Generator Tank” feed the day tanks. The name of this tank has been changed to “Storage Tank” to avoid confusion.

Is there a procedure for reacting to a day tank high-level alarm from the WFO/RFC?

There are currently no written procedures for this particular occurrence.  The revamped spill reporting section (III.B) is written such that it includes spills caused by the day tank.

In Part II.A.2, 3rd part, consider rewording “...the main tank is scheduled to have an audible alarm ...” to “... the main tank is scheduled for installation of an audible alarm...”.  Make similar change to Table 1, Additional Information, for the Generator tank.

These changes have been made.

In Part IV.A.1, consider increasing the quantity of spill kit material.  Supplies for a four-gallon spill seem inadequate for a site with 1500 gallons.

This recommendation has been incorporated in the final version.

In Part IV.B.3, the term “portable tank” is used in reference to the Convault tank.  This is confusing.  Also, it appears that the term “generator tank” is used to describe the Convault tank.  Tank names should be consistent.

See response to comment 40.

The text infers that a NWS employee has been present when the contractor fills the Convault tank.  If this is true, I think we should state it as normal procedure.

See response to comment 10.

The issue of this being an unmanned site is not addressed.  The point is that a leak or spill may go undetected for some time.  Is there a normal frequency of checking this tank?  Should we try to find a way to increase the frequency?

The primary purpose of this plan is to prevent spills from occurring.  Also, See response to comment 3.

In Table 1, “... grater ...” should be “... greater ...”.

See response to comment 19.

App. C.A, “... Tile 40 ..." should read “... Title 40 ...”

This change has been made in the final version.

In App. E, some of the paragraph references in the column “Plan Location” are incomplete (e.g., “Part I 3" should be “Part I B.3").

These changes have been made in the final version.

Additional Comments for WFO/RFC SPCC Plan

Are there no day-tanks at the WFO/RFC?

Information on the day tank has been included in the final plan.

Comments for the RDA SPCC Plan should be checked for applicability to the WFO/RFC plan.

Applicable changes to the RDA SPCC have also been made to the WFO/RFC SPCC.