## list
source
cond
emiss
feed
process
df c1
df c2

## source
Source Description
Phase II ID No. | 771
EPA ID No. | WAD092899574
Facility Name | Kalama Chemical (BF Goodrich)
Facility Location
City | Kalama
State | WA
Unit ID Name/No. | U-3 Boiler
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Watertube boiler. A-type package watertube, 30,000 lb/hr steam @ 250 psig, refractory lined combustion chamber, 50 MMBtu/hr
Capacity (MMBtu/hr) | 50
Soot Blowing | Yes
APCS Detailed Acronym | FF
APCS General Class | FF
APCS Characteristics | Air-to-cloth ratio of 4.06:1, fiberglass bags, reverse pulse jet cleaning
Hazardous Wastes | Liq
Haz Waste Description | Liquid organic chemicals -- tars, aromatic hydrocarbon and alcohol liquid wastes (methanol, benzene)
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft) | 3.33
Height (ft) | 50
Gas Velocity (ft/sec) | 28.95
Gas Temperature (°F) | 295
Permitting Status | Tier I metals (except Cr) and HCl/Cl2
HWC Burn Status (Date if Terminated)

## cond
Cond Description
771C1
Report Name/Date | Trial Burn Report Addendum U-3 Boiler, December 1997
Report Prepare | IT Corporation
Testing Firm | IT Corporation
Testing Dates | June 28-30, 1996
Cond Dates | 1996-06-01
Condition Descr | Trial burn; max comb temp, max prod rate, max benzene
Content | CO, PM, Cr+6, D/F (spiked ash, Cr, Cl)
771C2
Report Name/Date | Trial Burn Report Addendum U-3 Boiler, December 1997
Report Prepare | IT Corporation
Testing Firm | IT Corporation
Testing Dates | June 25-27, 1996
Cond Dates | 1996-06-01
Condition Descr | Trial burn; min comb temp and min prod rate, max moisture/methanol feed
Content | CO, PM, D/F (spiked ash, Cl)

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
1 | 771C1 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.00255 | 0.00391 | 0.00358 | 0.0027
| CO (RA) | E1 | ppmv | y | 17.13 | 5.58 | 1.92 | 8.21
| Chromium (Hex) |  | gr/dscf | y | 2.81e-06 | 3.18e-06 | 4.26e-06
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  | 8874 | 8186 | 8997 | 8686
| O2 |  | % |  | 4.5 | 4.8 | 4.2 | 4.5
| Moisture |  | % |  | 12.91 | 15.54 | 13.04 | 13.83
| Temperature |  | °F |  | 297 | 295 | 298 | 296.7
| Sampling Train | Cr (+6) | E2
| Stack Gas Flowrate |  | dscfm |  | 9090 | 7955 | 8165 | 8430
| O2 |  | % |  | 4.5 | 4.8 | 4.2 | 4.5
| Moisture |  | % |  | 12.91 | 15.54 | 13.04 | 13.83
| Temperature |  | °F |  | 293 | 299 | 303 | 298
| Chromium (Hex) | E2 | µg/dscm | y | 6.4399 | 7.2878 | 9.7629 | 7.8302
| POHC DRE | Benzene
| POHC Feedrate |  | lb/hr |  | 1156 | 1285 | 1208
| Emission Rate | E1 | lb/hr |  | 0.00262 | 0.00134 | 0.0022
| DRE | E1 | % |  | 99.9998 | 99.9999 | 99.9998
| POHC DRE | Methanol
| POHC Feedrate |  | lb/hr |  | 410 | 354 | 359
| Emission Rate | E1 | lb/hr |  | 0.00108 | 0.00981 | 0.0072
| DRE | E1 | % |  | 99.9974 | 99.9972 | 99.998
[6 empty] | Sootblow | Sootblow
2 | 771C2 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.00239 | 0.00468 | 0.00546 | 0.0037
| CO (RA) | E1 | ppmv | y | 8.71 | 4.59 | 7.8 | 7.03
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  | 10000 | 10030 | 10062 | 10031
| O2 |  | % |  | 8 | 7.4 | 10.1 | 8.5
| Moisture |  | % |  | 10.86 | 11 | 10.97 | 10.94
| Temperature |  | °F |  | 300 | 294 | 286 | 293.3
| POHC DRE | Benzene
| POHC Feedrate |  | lb/hr |  | 585 | 545 | 516
| Emission Rate | E1 | lb/hr |  | 0.000949 | 0.00337 | 0.00163
| DRE | E1 | % |  | 99.9998 | 99.9993 | 99.9997
| POHC DRE | Methanol
| POHC Feedrate |  | lb/hr |  | 1619 | 1607 | 1603
| Emission Rate | E1 | lb/hr |  | 0.00923 | 0.00677 | 0.00866
| DRE | E1 | % |  | 99.9994 | 99.9996 | 99.9995

## feed
Feedstreams
* | 771C1 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 |  | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  | Li q HW |  | Li q HW |  | Li q HW |  | Li q HW | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Liq. wastes |  | Liq. wastes |  | Liq. wastes |  | Liq. wastes | Natural gas | Natural gas | Natural gas | Natural gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/min |  | 27.34 |  | 27.46 |  | 27.2 |  | 27.33 | 16.41 | 15.49 | 16.21 | 16.04
| Heating Value | Btu/lb |  | 14000 |  | 14000 |  | 14000 |  | 14000 | 23452 | 23452 | 23452 | 23452
| Ash | lb/hr |  | 110.7 |  | 100.5 |  | 109.3 |  | 106.9 | [12 empty] | spiked, ?
| Chlorine | lb/hr |  | 2.051 |  | 1.895 |  | 2.366 |  | 2.1 | [12 empty] | spiked, ?
| Antimony | ppmw | nd | 0.025 | nd | 0.025 |  | 0.03 |  | 0.027
| Arsenic | ppmw |  | 0.04 |  | 0.19 |  | 0.21 |  | 0.15
| Barium | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Beryllium | ppmw | nd | 0.2 | nd | 0.2 | nd | 0.2 |  | 0.2
| Cadmium | ppmw | nd | 0.2 | nd | 0.2 | nd | 0.2 |  | 0.2
| Chromium | ppmw |  | 81 |  | 76 |  | 83 |  | 80 | [12 empty] | spiked, ?
| Copper | ppmw |  | 74 |  | 56 |  | 61 |  | 63.7
| Lead | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Mercury | ppmw | nd | 0.25 | nd | 0.25 | nd | 0.25 |  | 0.25
| Nickel | ppmw |  | 1.3 |  | 2 |  | 2.1 |  | 1.8
| Selenium | ppmw | nd | 0.05 | nd | 0.05 | nd | 0.05 |  | 0.06
| Silver | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Thallium | ppmw | nd | 0.025 | nd | 0.025 | nd | 0.025 |  | 0.025
| Stack Gas Flowrate | dscfm |  | 8874 |  | 8186 |  | 8997 |  | 8686 | [11 empty] | 8686
| Oxygen | % |  | 4.5 |  | 4.8 |  | 4.2 |  | 4.5 | [11 empty] | 4.5
| Thermal Feedrate | MMBtu/hr |  | 22.9656 |  | 23.0664 |  | 22.848 |  | 22.9572 | 23.0908 | 21.7963 | 22.8094 | 22.5702 |  | 46.0564 |  | 44.8627 |  | 45.6574 |  | 45.5274
| Estimated Firing Rate | MMBtu/hr | [7 empty] | 45.4981 | [11 empty] | 45.4981
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 2830.0262 |  | 2836.779 |  | 2706.8199 | 0 | 2791.2084 |  |  |  |  | 0 | 2830.0262 | 0 | 2836.779 | 0 | 2706.8199 | 0 | 2791.2084
| Chlorine | ug/dscm |  | 52433.4573 |  | 53489.5152 |  | 58594.1071 | 0 | 54839.0265 |  |  |  |  | 0 | 52433.4573 | 0 | 53489.5152 | 0 | 58594.1071 | 0 | 54839.0265
| Antimony | ug/dscm | 100 | 1.0484 | 100 | 1.1627 |  | 1.2125 | 64.5838 | 1.1412 |  |  |  |  | 100 | 1.0484 | 100 | 1.1627 | 0 | 1.2125 | 64.5838 | 1.1412
| Arsenic | ug/dscm |  | 1.6775 |  | 8.8362 |  | 8.4875 | 0 | 6.3337 |  |  |  |  | 0 | 1.6775 | 0 | 8.8362 | 0 | 8.4875 | 0 | 6.3337
| Barium | ug/dscm | 100 | 20.9683 | 100 | 23.2531 | 100 | 20.2083 | 100 | 21.4766 |  |  |  |  | 100 | 20.9683 | 100 | 23.2531 | 100 | 20.2083 | 100 | 21.4766
| Beryllium | ug/dscm | 100 | 8.3873 | 100 | 9.3012 | 100 | 8.0833 | 100 | 8.5906 |  |  |  |  | 100 | 8.3873 | 100 | 9.3012 | 100 | 8.0833 | 100 | 8.5906
| Cadmium | ug/dscm | 100 | 8.3873 | 100 | 9.3012 | 100 | 8.0833 | 100 | 8.5906 |  |  |  |  | 100 | 8.3873 | 100 | 9.3012 | 100 | 8.0833 | 100 | 8.5906
| Chromium | ug/dscm |  | 3396.8597 |  | 3534.4743 |  | 3354.5745 | 0 | 3428.6362 |  |  |  |  | 0 | 3396.8597 | 0 | 3534.4743 | 0 | 3354.5745 | 0 | 3428.6362
| Copper | ug/dscm |  | 3103.304 |  | 2604.3495 |  | 2465.4102 | 0 | 2724.3545 |  |  |  |  | 0 | 3103.304 | 0 | 2604.3495 | 0 | 2465.4102 | 0 | 2724.3545
| Lead | ug/dscm | 100 | 20.9683 | 100 | 23.2531 | 100 | 20.2083 | 100 | 21.4766 |  |  |  |  | 100 | 20.9683 | 100 | 23.2531 | 100 | 20.2083 | 100 | 21.4766
| Mercury | ug/dscm | 100 | 10.4841 | 100 | 11.6266 | 100 | 10.1041 | 100 | 10.7383 |  |  |  |  | 100 | 10.4841 | 100 | 11.6266 | 100 | 10.1041 | 100 | 10.7383
| Nickel | ug/dscm |  | 54.5175 |  | 93.0125 |  | 84.8748 | 0 | 77.4683 |  |  |  |  | 0 | 54.5175 | 0 | 93.0125 | 0 | 84.8748 | 0 | 77.4683
| Selenium | ug/dscm | 100 | 2.0968 | 100 | 2.3253 | 100 | 2.0208 | 100 | 2.1477 |  |  |  |  | 100 | 2.0968 | 100 | 2.3253 | 100 | 2.0208 | 100 | 2.1477
| Silver | ug/dscm | 100 | 20.9683 | 100 | 23.2531 | 100 | 20.2083 | 100 | 21.4766 |  |  |  |  | 100 | 20.9683 | 100 | 23.2531 | 100 | 20.2083 | 100 | 21.4766
| Thallium | ug/dscm | 100 | 1.0484 | 100 | 1.1627 | 100 | 1.0104 | 100 | 1.0738 |  |  |  |  | 100 | 1.0484 | 100 | 1.1627 | 100 | 1.0104 | 100 | 1.0738
| SVM | ug/dscm | 100 | 29.3556 | 100 | 32.5544 | 100 | 28.2916 | 100 | 30.0672 |  |  |  |  | 100 | 29.3556 | 100 | 32.5544 | 100 | 28.2916 | 100 | 30.0672
| LVM | ug/dscm | 0.24618 | 3406.9245 | 0.26181 | 3552.6117 | 0.23978 | 3371.1453 | 0.24947 | 3443.5605 |  |  |  |  | 0.24618 | 3406.9245 | 0.26181 | 3552.6117 | 0.23978 | 3371.1453 | 0.24947 | 3443.5605
* | 771C2 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 |  | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  | Li q HW |  | Li q HW |  | Li q HW |  | Li q HW | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Liq. wastes |  | Liq. wastes |  | Liq. wastes |  | Liq. wastes | Natural gas | Natural gas | Natural gas | Natural gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/min |  | 45.35 |  | 45.39 |  | 45.29 |  | 45.32 | 0.02 | 0.02 | 0.01 | 0.01
| Heating Value | Btu/lb |  | 8583 |  | 8583 |  | 8583 |  | 8583 | 23452 | 23452 | 23452 | 23452
| Ash | lb/hr |  | 98 |  | 95.3 |  | 119.6 |  | 104.3 | [12 empty] | spiked, ?
| Chlorine | lb/hr |  | 0.816 |  | 2.179 |  | 2.446 |  | 1.814 | [12 empty] | spiked, ?
| Antimony | ppmw | nd | 0.025 | nd | 0.025 | nd | 0.025 |  | 0.025
| Arsenic | ppmw |  | 0.04 | nd | 0.025 |  | 0.06 |  | 0.042
| Barium | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Beryllium | ppmw | nd | 0.2 | nd | 0.2 | nd | 0.2 |  | 0.2
| Cadmium | ppmw | nd | 0.2 | nd | 0.2 | nd | 0.2 |  | 0.2
| Chromium | ppmw |  | 2.1 |  | 0.9 |  | 1.6 |  | 1.53
| Cumene | ppmw |  | 44 |  | 50 |  | 45 |  | 46.3 | [12 empty] | spiked, ?
| Lead | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Mercury | ppmw | nd | 0.25 | nd | 0.25 | nd | 0.25 |  | 0.25
| Nickel | ppmw |  | 1.3 |  | 0.5 |  | 0.8 |  | 0.87
| Selenium | ppmw | nd | 0.05 | nd | 0.05 | nd | 0.05 |  | 0.05
| Silver | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Thallium | ppmw | nd | 0.025 | nd | 0.025 | nd | 0.025 |  | 0.025
| Stack Gas Flowrate | dscfm |  | 10000 |  | 10030 |  | 10062 |  | 10031 | [11 empty] | 10031
| Oxygen | % |  | 8 |  | 7.4 |  | 10.1 |  | 8.5 | [11 empty] | 8.5
| Thermal Feedrate | MMBtu/hr |  | 23.3543 |  | 23.3749 |  | 23.3234 |  | 23.3389 |  |  |  | 0.014071 |  | 23.3543 |  | 23.3749 |  | 23.3234 |  | 23.353
| Estimated Firing Rate | MMBtu/hr | [19 empty] | 39.8056
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 2821.8175 |  | 2615.166 |  | 4081.9396 | 0 | 3172.9744 |  |  |  |  | 0 | 2821.8175 | 0 | 2615.166 | 0 | 4081.9396 | 0 | 3172.9744
| Chlorine | ug/dscm |  | 23495.95 |  | 59794.8239 |  | 83481.8077 | 0 | 55590.8605 |  |  |  |  | 0 | 23495.95 | 0 | 59794.8239 | 0 | 83481.8077 | 0 | 55590.8605
| Antimony | ug/dscm | 100 | 1.9587 | 100 | 1.8683 | 100 | 2.3186 | 100 | 2.0486 |  |  |  |  | 100 | 1.9587 | 100 | 1.8683 | 100 | 2.3186 | 100 | 2.0486
| Arsenic | ug/dscm |  | 3.1339 | 100 | 1.8683 |  | 5.5647 | 17.681 | 3.5223 |  |  |  |  | 0 | 3.1339 | 100 | 1.8683 | 0 | 5.5647 | 17.681 | 3.5223
| Barium | ug/dscm | 100 | 39.1743 | 100 | 37.367 | 100 | 46.3723 | 100 | 40.9712 |  |  |  |  | 100 | 39.1743 | 100 | 37.367 | 100 | 46.3723 | 100 | 40.9712
| Beryllium | ug/dscm | 100 | 15.6697 | 100 | 14.9468 | 100 | 18.5489 | 100 | 16.3885 |  |  |  |  | 100 | 15.6697 | 100 | 14.9468 | 100 | 18.5489 | 100 | 16.3885
| Cadmium | ug/dscm | 100 | 15.6697 | 100 | 14.9468 | 100 | 18.5489 | 100 | 16.3885 |  |  |  |  | 100 | 15.6697 | 100 | 14.9468 | 100 | 18.5489 | 100 | 16.3885
| Chromium | ug/dscm |  | 164.5321 |  | 67.2605 |  | 148.3915 | 0 | 126.728 |  |  |  |  | 0 | 164.5321 | 0 | 67.2605 | 0 | 148.3915 | 0 | 126.728
| Cumene | ug/dscm |  | 3447.3396 |  | 3736.6963 |  | 4173.5102 | 0 | 3785.8487 |  |  |  |  | 0 | 3447.3396 | 0 | 3736.6963 | 0 | 4173.5102 | 0 | 3785.8487
| Lead | ug/dscm | 100 | 39.1743 | 100 | 37.367 | 100 | 46.3723 | 100 | 40.9712 |  |  |  |  | 100 | 39.1743 | 100 | 37.367 | 100 | 46.3723 | 100 | 40.9712
| Mercury | ug/dscm | 100 | 19.5872 | 100 | 18.6835 | 100 | 23.1862 | 100 | 20.4856 |  |  |  |  | 100 | 19.5872 | 100 | 18.6835 | 100 | 23.1862 | 100 | 20.4856
| Nickel | ug/dscm |  | 101.8532 |  | 37.367 |  | 74.1957 | 0 | 71.1386 |  |  |  |  | 0 | 101.8532 | 0 | 37.367 | 0 | 74.1957 | 0 | 71.1386
| Selenium | ug/dscm | 100 | 3.9174 | 100 | 3.7367 | 100 | 4.6372 | 100 | 4.0971 |  |  |  |  | 100 | 3.9174 | 100 | 3.7367 | 100 | 4.6372 | 100 | 4.0971
| Silver | ug/dscm | 100 | 39.1743 | 100 | 37.367 | 100 | 46.3723 | 100 | 40.9712 |  |  |  |  | 100 | 39.1743 | 100 | 37.367 | 100 | 46.3723 | 100 | 40.9712
| Thallium | ug/dscm | 100 | 1.9587 | 100 | 1.8683 | 100 | 2.3186 | 100 | 2.0486 |  |  |  |  | 100 | 1.9587 | 100 | 1.8683 | 100 | 2.3186 | 100 | 2.0486
| SVM | ug/dscm | 100 | 54.844 | 100 | 52.3137 | 100 | 64.9213 | 100 | 57.3597 |  |  |  |  | 100 | 54.844 | 100 | 52.3137 | 100 | 64.9213 |  | 57.3597
| LVM | ug/dscm | 8.547 | 183.3358 | 20 | 84.0757 | 10.7527 | 172.5051 | 11.6008 | 146.6388 |  |  |  |  | 8.547 | 183.3358 | 20 | 84.0757 | 10.7527 | 172.5051 |  | 146.6388
BIF Feedrate Limits
| Arsenic | lb/hr | [7 empty] | 0.0044
| Antimony | lb/hr | [7 empty] | 1.09
| Beryllium | lb/hr | [7 empty] | 0.0033
| Barium | lb/hr | [7 empty] | 181
| Cadmium | lb/hr | [7 empty] | 0.0033
| Chromium | lb/hr | [7 empty] | 0.00026
| Lead | lb/hr | [7 empty] | 0.33
| Mercury | lb/hr | [7 empty] | 0.29
| Silver | lb/hr | [7 empty] | 10.87
| Thallium | lb/hr | [7 empty] | 1.09
| Chlorine | lb/hr | [7 empty] | 1.45

## process
Process Information
771C1
Baghouse Temp | F | 324
Steam Prod | lb/hr | 37840
Furnace Temp | F | 1908
771C2
Baghouse Temp | F | 319
Steam Prod | lb/hr | 20380
Furnace Temp | F | 1357

## df c1
PCDD/PCDF
N
Facility Name and ID: |  | Kalama Chemical, Inc.
Condition ID: |  | 771C1
Condition/Test Date: |  | Risk burn, June 28-30 1996
|  | I-TEF |  | Run 4 |  |  |  |  | Run 5 |  |  |  |  | Run 6
|  | Wght Fact |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ
|  |  |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND
Detected in sample volume (pg)
| 2,3,7,8-TCDD | 1 | nd | 7.9 | 7.9 | 3.95 | 3.95 | nd | 7 | 7 | 3.5 | 3.5 | nd | 18 | 18 | 9 | 9
| TCDD Total | 0 |  | 53 | 0 | 53 | 0 |  | 190 | 0 | 190 | 0 |  | 240 | 0 | 240 | 0
| 1,2,3,7,8-PCDD | 0.5 | nd | 4.1 | 2.05 | 2.05 | 1.025 | nd | 5.2 | 2.6 | 2.6 | 1.3 | nd | 14 | 7 | 7 | 3.5
| PCDD Total | 0 | nd | 28 | 0 | 14 | 0 |  | 350 | 0 | 350 | 0 |  | 290 | 0 | 290 | 0
| 1,2,3,4,7,8-HxCDD | 0.1 | nd | 25 | 2.5 | 12.5 | 1.25 | nd | 1.6 | 0.16 | 0.8 | 0.08 | nd | 34 | 3.4 | 17 | 1.7
| 1,2,3,6,7,8-HxCDD | 0.1 | nd | 23 | 2.3 | 11.5 | 1.15 | nd | 30 | 3 | 15 | 1.5 | nd | 32 | 3.2 | 16 | 1.6
| 1,2,3,7,8,9-HxCDD | 0.1 | nd | 26 | 2.6 | 13 | 1.3 | nd | 21 | 2.1 | 10.5 | 1.05 | nd | 36 | 3.6 | 18 | 1.8
| HxCDD Total | 0 |  | 320 | 0 | 320 | 0 |  | 1100 | 0 | 1100 | 0 |  | 560 | 0 | 560 | 0
| 1,2,3,4,6,7,8-HpCDD | 0.01 |  | 81 | 0.81 | 81 | 0.81 |  | 180 | 1.8 | 180 | 1.8 |  | 73 | 0.73 | 73 | 0.73
| HpCDD Total | 0 |  | 170 | 0 | 34 | 0 |  | 430 | 0 | 430 | 0 |  | 190 | 0 | 190 | 0
| OCDD | 0.001 |  | 350 | 0.35 | 350 | 0.35 |  | 580 | 0.58 | 580 | 0.58 |  | 280 | 0.28 | 280 | 0.28
| 2,3,7,8-TCDF | 0.1 | nd | 7.6 | 0.76 | 3.8 | 0.38 | nd | 4.5 | 0.45 | 2.25 | 0.225 | nd | 9.4 | 0.94 | 4.7 | 0.47
| TCDF Total | 0 |  | 53 | 0 | 53 | 0 |  | 120 | 0 | 120 | 0 |  | 18 | 0 | 18 | 0
| 1,2,3,7,8-PCDF | 0.05 | nd | 5.1 | 0.255 | 2.55 | 0.1275 | nd | 5.4 | 0.27 | 2.7 | 0.135 | nd | 11 | 0.55 | 5.5 | 0.275
| 2,3,4,7,8-PCDF | 0.5 | nd | 4.4 | 2.2 | 2.2 | 1.1 | nd | 7.7 | 3.85 | 3.85 | 1.925 | nd | 10 | 5 | 5 | 2.5
| PCDF Total | 0 | nd | 15 | 0 | 7.5 | 0 | nd | 22 | 0 | 11 | 0 | nd | 12 | 0 | 6 | 0
| 1,2,3,4,7,8-HxCDF | 0.1 | nd | 5 | 0.5 | 2.5 | 0.25 | nd | 8.7 | 0.87 | 4.35 | 0.435 | nd | 6.8 | 0.68 | 3.4 | 0.34
| 1,2,3,6,7,8-HxCDF | 0.1 | nd | 3.7 | 0.37 | 1.85 | 0.185 | nd | 6.2 | 0.62 | 3.1 | 0.31 | nd | 4.1 | 0.41 | 2.05 | 0.205
| 2,3,4,6,7,8-HxCDF | 0.1 | nd | 4.8 | 0.48 | 2.4 | 0.24 | nd | 9.5 | 0.95 | 4.75 | 0.475 | nd | 6.8 | 0.68 | 3.4 | 0.34
| 1,2,3,7,8,9-HxCDF | 0.1 | nd | 2.1 | 0.21 | 1.05 | 0.105 | nd | 2.2 | 0.22 | 1.1 | 0.11 | nd | 3.2 | 0.32 | 1.6 | 0.16
| HxCDF Total | 0 | nd | 7.4 | 0 | 3.7 | 0 | nd | 13 | 0 | 6.5 | 0 | nd | 8.6 | 0 | 4.3 | 0
| 1,2,3,4,6,7,8-HpCDF | 0.01 | nd | 1.4 | 0.014 | 0.7 | 0.007 | nd | 14 | 0.14 | 7 | 0.07 | nd | 11 | 0.11 | 5.5 | 0.055
| 1,2,3,4,7,8,9-HpCDF | 0.01 | nd | 0.4 | 0.004 | 0.2 | 0.002 | nd | 6.6 | 0.066 | 3.3 | 0.033 | nd | 25 | 0.25 | 12.5 | 0.125
| HpCDF Total | 0 | nd | 1.6 | 0 | 0.8 | 0 | nd | 16 | 0 | 8 | 0 | nd | 25 | 0 | 12.5 | 0
| OCDF | 0.001 | nd | 15 | 0.015 | 7.5 | 0.0075 | nd | 25 | 0.025 | 12.5 | 0.0125 | nd | 32 | 0.032 | 16 | 0.016
| Gas sample volume (dscf) |  |  | 78.6 | 78.6 | 78.6 | 78.6 |  | 71.6 | 71.6 | 71.6 | 71.6 |  | 73.1 | 73.1 | 73.1 | 73.1
| O2 (%) |  |  | 4.5 | 4.5 | 4.5 | 4.5 |  | 4.8 | 4.8 | 4.8 | 4.8 |  | 4.2 | 4.2 | 4.2 | 4.2
| PCDD/PCDF (pg in sample) |  |  | 1013 | 23.318 | 843.5 | 12.239 |  | 2846 | 24.701 | 2808 | 13.5405 |  | 1655.6 | 45.182 | 1616.8 | 23.096
| PCDD/PCDF (ng/dscm @ 7% O2) |  | 95.0253 | 0.38641 | 0.0088946 | 0.32175 | 0.0046685 | 90.3648 | 1.2138 | 0.010535 | 1.1976 | 0.005775 | 97.7646 | 0.66691 | 0.0182 | 0.65129 | 0.0093036
| TEQ Cond Avg | 0.0065824
| Total Cond Avg | 0.72354

## df c2
PCDD/PCDF
N
Facility Name and ID: |  | Kalama Chemical, Inc.
Condition ID: |  | 771C2
Condition/Test Date: |  | June 25-27 1996
|  | I-TEF |  | Run 1 |  |  |  |  | Run 2 |  |  |  |  | Run 3
|  | Wght Fact |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ
|  |  |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND
Detected in sample volume (pg)
| 2,3,7,8-TCDD | 1 | nd | 5.3 | 5.3 | 2.65 | 2.65 | nd | 7.2 | 7.2 | 3.6 | 3.6 | nd | 5.9 | 5.9 | 2.95 | 2.95
| TCDD Total | 0 | nd | 15 | 0 | 7.5 | 0 |  | 98 | 0 | 98 | 0 |  | 29 | 0 | 29 | 0
| 1,2,3,7,8-PCDD | 0.5 | nd | 3.4 | 1.7 | 1.7 | 0.85 | nd | 3.1 | 1.55 | 1.55 | 0.775 | nd | 1.7 | 0.85 | 0.85 | 0.425
| PCDD Total | 0 | nd | 24 | 0 | 12 | 0 | nd | 49 | 0 | 24.5 | 0 | nd | 25 | 0 | 12.5 | 0
| 1,2,3,4,7,8-HxCDD | 0.1 | nd | 3.3 | 0.33 | 1.65 | 0.165 | nd | 3.5 | 0.35 | 1.75 | 0.175 | nd | 2 | 0.2 | 1 | 0.1
| 1,2,3,6,7,8-HxCDD | 0.1 | nd | 6.9 | 0.69 | 3.45 | 0.345 | nd | 11 | 1.1 | 5.5 | 0.55 | nd | 8.5 | 0.85 | 4.25 | 0.425
| 1,2,3,7,8,9-HxCDD | 0.1 | nd | 7 | 0.7 | 3.5 | 0.35 | nd | 8.8 | 0.88 | 4.4 | 0.44 | nd | 5.6 | 0.56 | 2.8 | 0.28
| HxCDD Total | 0 |  | 180 | 0 | 180 | 0 |  | 870 | 0 | 870 | 0 |  | 340 | 0 | 340 | 0
| 1,2,3,4,6,7,8-HpCDD | 0.01 | nd | 34 | 0.34 | 17 | 0.17 |  | 170 | 1.7 | 170 | 1.7 |  | 82 | 0.82 | 82 | 0.82
| HpCDD Total | 0 | nd | 35 | 0 | 34 | 0 |  | 350 | 0 | 350 | 0 |  | 170 | 0 | 170 | 0
| OCDD | 0.001 |  | 110 | 0.11 | 110 | 0.11 |  | 680 | 0.68 | 680 | 0.68 |  | 330 | 0.33 | 330 | 0.33
| 2,3,7,8-TCDF | 0.1 |  | 11 | 1.1 | 11 | 1.1 |  | 11 | 1.1 | 11 | 1.1 | nd | 7.9 | 0.79 | 3.95 | 0.395
| TCDF Total | 0 |  | 67 | 0 | 67 | 0 |  | 120 | 0 | 120 | 0 |  | 44 | 0 | 44 | 0
| 1,2,3,7,8-PCDF | 0.05 | nd | 4.3 | 0.215 | 2.15 | 0.1075 | nd | 4.3 | 0.215 | 2.15 | 0.1075 | nd | 2.6 | 0.13 | 1.3 | 0.065
| 2,3,4,7,8-PCDF | 0.5 | nd | 5.2 | 2.6 | 2.6 | 1.3 | nd | 7.5 | 3.75 | 3.75 | 1.875 | nd | 5.2 | 2.6 | 2.6 | 1.3
| PCDF Total | 0 | nd | 14 | 0 | 7 | 0 | nd | 20 | 0 | 10 | 0 | nd | 13 | 0 | 6.5 | 0
| 1,2,3,4,7,8-HxCDF | 0.1 | nd | 7 | 0.7 | 3.5 | 0.35 | nd | 6.6 | 0.66 | 3.3 | 0.33 | nd | 5.3 | 0.53 | 2.65 | 0.265
| 1,2,3,6,7,8-HxCDF | 0.1 | nd | 4.4 | 0.44 | 2.2 | 0.22 | nd | 4.4 | 0.44 | 2.2 | 0.22 | nd | 3.8 | 0.38 | 1.9 | 0.19
| 2,3,4,6,7,8-HxCDF | 0.1 | nd | 6.4 | 0.64 | 3.2 | 0.32 | nd | 6.4 | 0.64 | 3.2 | 0.32 | nd | 4.1 | 0.41 | 2.05 | 0.205
| 1,2,3,7,8,9-HxCDF | 0.1 | nd | 5.2 | 0.52 | 2.6 | 0.26 | nd | 1.8 | 0.18 | 0.9 | 0.09 | nd | 0.9 | 0.09 | 0.45 | 0.045
| HxCDF Total | 0 | nd | 11 | 0 | 5.5 | 0 | nd | 12 | 0 | 6 | 0 | nd | 7.2 | 0 | 3.6 | 0
| 1,2,3,4,6,7,8-HpCDF | 0.01 | nd | 18 | 0.18 | 9 | 0.09 | nd | 14 | 0.14 | 7 | 0.07 | nd | 9 | 0.09 | 4.5 | 0.045
| 1,2,3,4,7,8,9-HpCDF | 0.01 | nd | 7.5 | 0.075 | 3.75 | 0.0375 | nd | 4.3 | 0.043 | 2.15 | 0.0215 | nd | 3.9 | 0.039 | 1.95 | 0.0195
| HpCDF Total | 0 | nd | 18 | 0 | 9 | 0 | nd | 14 | 0 | 7 | 0 | nd | 9 | 0 | 4.5 | 0
| OCDF | 0.001 | nd | 38 | 0.038 | 19 | 0.019 | nd | 21 | 0.021 | 10.5 | 0.0105 | nd | 17 | 0.017 | 8.5 | 0.0085
| Gas sample volume (dscf) |  |  | 93.4 | 93.4 | 93.4 | 93.4 |  | 80.5 | 80.5 | 80.5 | 80.5 |  | 86 | 86 | 86 | 86
| O2 (%) |  |  | 8 | 8 | 8 | 8 |  | 7.4 | 7.4 | 7.4 | 7.4 |  | 10.1 | 10.1 | 10.1 | 10.1
| PCDD/PCDF (pg in sample) |  |  | 512 | 15.678 | 451 | 8.444 |  | 2234 | 20.649 | 2176 | 12.0645 |  | 984.2 | 14.586 | 948.6 | 7.868
| PCDD/PCDF (ng/dscm @ 7% O2) |  | 92.2822 | 0.2086 | 0.0063877 | 0.18375 | 0.0034403 | 83.1469 | 1.0095 | 0.0093305 | 0.98325 | 0.0054515 | 92.1157 | 0.5194 | 0.0076976 | 0.50061 | 0.0041522
| TEQ Cond Avg | 0.004348
| Total Cond Avg | 0.55587