SPECIAL SPECIFICATION

SECTION 16461-S

SMALL POWER PADMOUNT TRANSFORMERS

PART 1 - General	2

1.01	DESCRIPTION	2

1.02	QUALITY ASSURANCE	2

1.03	SUBMITTALS	2

PART 2 - products	4

2.01	KVA RATINGS	4

2.02	VOLTAGE RATINGS AND TAP RATINGS	4

2.03	CORE DESIGN	4

2.04	HIGH VOLTAGE TAPS	4

2.05	TRANSFORMER IMPEDANCES	4

2.06	SHORT-CIRCUIT CAPABILITY	5

2.07	OVERCURRENT PROTECTION	5

2.08	CONSTRUCTION	5

2.09	MANUFACTURERS	7

2.010	LOW VOLTAGE BUSHINGS AND TERMINALS	7

2.011	HIGH-VOLTAGE BUSHINGS AND TERMINALS	7

2.012	ACCESSORIES	8

2.013	JACKING, ROLLING, LIFTING AND MOUNTING FACILITIES	8

2.014	TERMINAL MARKINGS	8

2.015	INSTRUCTION NAMEPLATE	9

2.016	OIL PRESERVATION	9

2.017	TANKS	9

PART 3 - Execution	9

3.01	INSTALLATION	9

3.02	IDENTIFICATION TAGS	10

PART 4 - EVALUATION	10

4.01	LOSS EVALUATION	10

SPECIAL SPECIFICATION

SECTION 16461-S

SMALL POWER PADMOUNT TRANSFORMERS

- General

  - DESCRIPTION

    - This specification is written for three-phase, 60 hertz, 65oC temperature rise, liquid filled, self-cooled, pad mounted, live-front, compartmentalized distribution transformers, rated 1,500 KVA and below, radial feed.

    - Pad mounted transformers shall be provided and installed in accordance with the details and ratings on the working drawings, and in accordance with this specification.

  - QUALITY ASSURANCE

    - All characteristics, definitions, terminology, and voltage designations, except as otherwise specified herein, shall be in accordance with applicable provisions of the latest edition of ANSI C57.12.22, or its successors, and applicable ANSI C57 series specifications including C57.12.00-1987 (or the latest editions).

    - Manufacturer will state the edition and date of ANSI C57.12.22 on submittals.

  - SUBMITTALS

    - The following shall be submitted in accordance with Sandia Specification 01300.

      - Outline drawings including overall height, overall width, overall depth, base dimensions, clearances required for opening doors, arrangement of bushings, and other appurtenances, and compartment dimensions.

      - Weights of tank, oil, transformer total, and shipping weight.

      - Volume of oil, gallons.

      - Material Safety Data Sheet for transformer oil.

      - Test and Performance Data.

        - The manufacturer shall perform all routine tests as defined in ANSI C57.12.00-1987 (or the latest edition).

        - The manufacturer shall provide Sandia with the following certified data by transformer serial number for each transformer shipped.

          - Excitation loss, watts.

          - Impedance, % Z.

          - Total loss, watts.

          - No load loss, watts.

          - Full load loss, watts.

          - Exciting current at 100% and 110% of rated voltage.

          - Average excitation loss in accordance with ANSI C57.12.00-1987 (or the latest edition), Section 9, paragraph 9.3, and Table 16, line 3.

          - Average total loss in accordance with ANSI C57.12.00-1987 (or the latest edition), Section 9, paragraph 9.3, and Table 16, line 3.

          - Percent impedance volts, of the low voltage winding with respect to the high voltage winding at rated self cooled KVA.

          - Steady state transformer top oil temperature rise above ambient, degree Celsius.

          - Transformer oil time constant, time for top oil to obtain 63% of steady state rise above ambient.

          - Certified statement of compliance with short circuit  capability requirements of Paragraph 3.06.

          - Certification of tamper resistant design with complete test data.

      - Manufacturer shall certify that all transformers supplied under this specification contain less than 1 ppm PCB.

      - All required information and laboratory test performance data per Section 3.1.2 of "EEI Finishing Guidelines for Padmounted Equipment," Draft 6.

      - No individual transformer shall be shipped with losses that exceed quoted losses by more than the tolerances in ANSI C57.12.00-1987 (or the latest edition), Table 16, line 2, without written approval of SNL, SCR.

- products

  - KVA RATINGS

    - Kilovolt-ampere ratings shall be 500, 750, 1000, and 1500.

  - VOLTAGE RATINGS AND TAP RATINGS

    - Voltage ratings, minimum BIL rating, and tap ratings shall be in accordance with Table I, below.

TABLE I

| High Voltage Ratings (Volts) Delta | BIL Rating (KV) Delta | Low Voltage Rating (Volts) WYE | BIL Rating (KV) | KVA Rating | High Voltage Taps Required |
| --- | --- | --- | --- | --- | --- |
| 12470 | 95 | 4160 | 60 | 500-1500 | 2-2 ½ % Abv & Bel |

  - CORE DESIGN

    - Transformers shall be of five-legged core design and connected delta-wye.

  - HIGH VOLTAGE TAPS

    - High voltage taps shall be provided in accordance with Table I.  Taps shall be suitable for de-energized operation only.  The tap changer switch shall be ganged and shall be externally operable.  The operating handle shall be located either in the high voltage compartment above the primary bushings or in the secondary compartment above the low voltage bushings.  The tap changer shall be set on the 100% tap at the factory and shall be secured to prevent inadvertent change from this position.

  - TRANSFORMER IMPEDANCES

    - Minimum impedances shall be in accordance with Table II, below:

TABLE II

Secondary Voltage

*Minimum AC Impedance %

| KVA | 2400 Delta |
| --- | --- |
| 500 | 5.75 |
| 750 | 5.75 |
| 1000 | 5.75 |
| 1500 | 5.75 |

*ANSI Standard Tolerance

  - SHORT-CIRCUIT CAPABILITY

    - Mechanical short-circuit capability shall be demonstrated by design compliance with ANSI C57.12.90-1987 (or the latest edition).

    - Thermal short-circuit capability shall be demonstrated by design compliance with ANSI C57-12.00-1987 (or the latest edition).

  - OVERCURRENT PROTECTION

    - Overcurrent protection devices shall not be supplied in radial feed transformers.

  - CONSTRUCTION

    - Description

      - Transformers shall be designed to protect people against accidental contact of energized parts, discourage unauthorized access to or climbing upon the unit by the public and protect against weather.

      - The padmounted transformer shall consist of the transformer tank, high voltage cable terminating compartment, and the low voltage cable terminating compartment.  The transformer tank and compartment shall be assembled as a raintight compartment, outdoor, and tamper resistant integral unit suitable for mounting on a flat surface.

      - There shall be no exposed screws, bolts, or other fastening or hinging devices (other than the pentahead bolt specified in 2.08 D.5) which are externally removable.  There shall be no opening through which foreign objects such as sticks or wires might be inserted to contact energized parts.  Suitable means for padlocking the compartment door(s) shall be provided.  Normal entry shall be possible only with the use of proper access tools.

      - The high- and low-voltage compartments shall be located side by side on one side of the transformer tank.  When facing the compartment, the low voltage compartment shall be on the right.

      - Construction of the unit shall be such that it can be lifted, skidded, and slid into place on the mounting pad without disturbing the entrance cables.

      - All external surfaces shall be constructed of steel, 13 USS gauge or thicker.

      - The transformer and compartment hoods shall be crowned to insure water run off.

    - Bottom Protection

      - The transformer tank base shall be raised above the pad to protect the bottom finish during installation and to minimize corrosion due to moisture accumulation.  The base shall be cross braced to permit rolling in two directs.

      - All external surfaces of ferrous material used in the construction of the assembly shall have undercoating over the regular finish, applied to the bottoms of the components and extending up the side to a point one inch above the bottom of their bases.

    - Protective Coating

      - All coated surfaces both exterior and interior shall be painted using a system which conforms to the requirements of "EEI Proposed Finishing Guidelines for Padmounted Equipment," Draft 6.  The finish coat shall be light gray (ANSI Color No. 70).

    - High and Low-Voltage Compartments

      - Terminal compartments shall be full height, air filled compartments with separate hinged doors.  The compartments shall be completely isolated from each other by a steel barrier without opening or discontinuity of any kind.

      - The edges of the access doors and hoods shall be formed to provide a close fitting mating surface, with internal insertion-prevention lip that will be shaped to resist entry or prying by screwdrivers, wrecking bars, tire irons, single-socket lug wrenches or other readily accessible tools.

      - Hinges and hinge pins shall be passivated AISI Type 304 stainless steel or equivalent corrosion-resistant metal.

      - There shall be a threaded fastening device for the high voltage door, accessible only through the low voltage compartment.  Screen door latches with wing nuts, gravity hooks, etc., are acceptable.  The low voltage compartment door shall have a minimum of three point latching and the handle shall have provisions for pad locking.  The padlocking provision shall be so designed and located as to resist prying or breaking off by screwdrivers, wrecking bars, tire irons, single-socket lug wrenches or other readily accessible tools and to inhibit removal of the padlock with a bolt cutting device or hacksaw.

      - In addition to the regular locking provision above, the access doors shall be secured by a captive, recessed pentahead bolt as depicted in Figure 11, ANSI C57-12.26-1987 (or the latest edition).  Bolts and associated hardware must be rust and corrosion resistant and the design shall minimize the possibility of misalignment and cross-threading.  The design must be such that wire entry through the bolt hole into the compartment(s) is prohibited when the bolt is removed.  The non-rotating cup shall be permanently attached.

        - The captive pentahead bolt shall be coordinated with the latch and padlock to prevent unlatching and insertion of the padlock into the hasp when and until the bolt is completely threaded, respectively.

        - The captive pentahead shall also function as an interlock device to pin the latch closed.

      - Both compartment doors shall be equipped with stops for holding each door in a 90o open position.  The stops shall be captive to prevent loss of the device.

      - Doors on the high- and low-voltage compartments shall be of sufficient size to provide adequate working space when open.

      - The bottom edge of the transformer shall provide for flush mounting on a flat rigid surface to prevent wire entry into the high- or low-voltage compartments.

  - MANUFACTURERS

    - Padmount transformers manufactured by ABB Company, General Electric, Cooper Industries or Howard Industries are acceptable to Sandia.

  - LOW VOLTAGE BUSHINGS AND TERMINALS

    - Bushings arrangement for live front, radial feed transformers shall comply with the latest revision of ANSI C57.12.22 1987.

    - Low-voltage bushings are to be made of wet-process porcelain and clamped externally to the wall of the transformer.  Reusable nitrite rubber gaskets shall seal the bushing to the tank wall in the terminals to the porcelain.

    - Low-voltage terminals shall be 2-hole blade spades with NEMA hole spacing to provide six holes.

    - Low-voltage cable terminals shall be oriented for vertical take-off of secondary cables entering the compartment from below.

  - HIGH-VOLTAGE BUSHINGS AND TERMINALS

    - Bushings arrangement for live front, radial feed transformers shall comply with the latest revision of ANSI C57.12.22.19.87.

    - High-voltage bushings are to be made of wet-process porcelain and clamped externally to the wall of the transformer.  Reusable  nitrite rubber gaskets shall seal the bushing to the tank wall in the terminals to the porcelain.

    - Transformer sizes of 500-1500 KVA, shall have 2-hole blade terminals with 9/16-inch diameter holes.

    - High-voltage cable terminals shall be oriented for vertical take-off of primary cables entering the compartment from below in accordance with Figure 4, ANSI C57.12.22-1989.

    - Transformer design shall allow field replacement of high voltage bushing wells and low voltage bushings by means of common hand tools and oil handling equipment, without totally untanking the transformer.

  - ACCESSORIES

    - The following accessories are required on all transformers and located in the low voltage compartment in such a manner as to not interfere with low voltage terminals:

      - Pressure relief device.

      - Upper filter valve or plug.

      - One inch combination drain, lower filter valve, and sampling device.  Combination drain plug and sampling device may be substituted.

      - Liquid level gauge.

      - Top oil thermometer.

  - JACKING, ROLLING, LIFTING AND MOUNTING FACILITIES

    - Suitable jack bosses or equivalent jacking facilities shall be provided on the tank.  Vertical clearance for jack shall be 1 1/2 inches minimum, 3 1/2 inches maximum.

    - Transformer base shall be arranged for rolling in two directions:  parallel to and at right angles to the center line of the high-voltage bushings.

    - Lifting lugs shall be adequately strengthened, sized, and arranged on the tank to provide a suitable lift for the completely assembled unit.

    - A 3/4 inch minimum and a 1 1/2 inch maximum integral flange shall be provided at the base of the high-voltage and low-voltage compartments, to provide means of anchoring the unit to the pad.

  - TERMINAL MARKINGS

    - External terminals on radial feed transformers shall be marked H1, H2, H3, and X1, X2, and X3 by stenciled white lettering on the tank.

    - A winding diagram with high- and low-voltage connections shall be shown on the instruction nameplate.

  - INSTRUCTION NAMEPLATE

    - Instruction nameplate shall be located on the inside of the low-voltage compartment door.

    - Instruction nameplate shall contain the information specified in paragraph 5.12 of ANSI C57.12.00-1987 (or latest edition), nameplate B.

    - Nameplate shall indicate that the transformer oil contained less than 1 ppm PCB at time of manufacture.

  - OIL PRESERVATION

    - Transformers shall be of sealed tank construction, so designed that the interior is sealed from the atmosphere and the gas plus oil volume remains constant.  The transformer shall remain effectively sealed for all temperatures to plus 105oC top oil.

  - TANKS

    - The tank shall be of sufficient strength to withstand a pressure of 7 psi gage, without permanent distortion.

      - Welded main cover construction shall be provided.  Access to internal connection for test purposes shall be provided by means of a handhole, accessible only from the padlocked compartments.

      - Tank grounding provision shall consist of:

        - Two unpainted copper-faced steel or stainless steel pads.  2 inches x 3 1/2 inches each with two holes spaced on 1-3/4 inch centers and tapped for 1/2 inch - 13 NC thread.  The minimum thickness of the copper facing shall be 0.015 inch.  Minimum threaded depth of holes shall be 1/2 inch.

      - These ground pads shall be welded on the transformer base or on the tank wall near the base, one in the high-voltage compartment and one in the low-voltage compartment.

- Execution

  - INSTALLATION

    - Transformer shall be installed on a concrete pad as shown on contract drawings.  Handling of the transformer shall be in accordance with manufacturer's instructions.

    - Touch up scratched or marred surface to match original finish.

    - Check for damage and tighten connections prior to energizing transformer.

    - Energization of primary circuits and transformer shall be in accordance with Sandia specification 16475, "Primary System Safety Requirements" and contract drawings.

    - Upon energization of the transformer, the phase rotation shall be verified and secondary voltages measured, line-to-line and line-ground, on all phases.

  - IDENTIFICATION TAGS

    - All transformers shall have 3-1/4" identification tags identifying transformer number per contract documents.  Tags shall be black letters on yellow background, 3-1/4" high, reflective pressure sensitive, Almetek brand.

- EVALUATION

## 4.01	LOSS EVALUATION

- Transformers bid under this specification will be evaluated for no load losses and load losses using the present worth method.  Each type of loss is associated with a demand charge and an energy charge.  The present value of carrying charges associated with each of the charges are multiplied by the appropriate loss figure supplied by the manufacturer for each unit then added to the each unit bid transformer price to obtain the total evaluated cost (TEC) per unit:

              - TEC 	=  T$ + PVDC x NLL + PVEC x LL; where:

              - TEC	=  Total Evaluated Cost

              - T$	=  Unit bid transformer price, $

              - PVDC	=  Present worth value of demand charges per kilowatt of no load losses, 		    $/KW.

              - PVEC	=  Present worth value of energy charges per kilowatt of load losses, $/KW.

              - NLL	=  Transformer no load losses, KW.

              - LL	=  Transformer load losses, KW.

Current Values:

PVDC	=  $8134.00

PVEC	=  $3326.00

- In the event actual losses exceed the losses guaranteed, SNL shall have the right to either reject the equipment or to accept the equipment for a reduced price.  The amount due SNL shall be calculated as follows:

              - Price Reduction = (NLLA - NLLQ) x PVDC +(LLA - LLQ) x PVEC; where:

              - NLLA 	=  Actual transformer no load losses, KW.

              - NLLQ 	=  Quoted transformer no load losses, KW.

              - LLA   	=  Actual transformer load losses, KW.

              - LLQ  	=  Quoted transformer load losses, KW.

- END OF SECTION -